## South Australia Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer at
http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information
Data presented is current as at 22 December 2017
South Australia Summary
Changes since last update
Hornsdale Wind Farm Stage 2: HWF2 Pty Ltd advises that Hornsdale Wind Farm Stage 2 (102 MW) is operational.
Hornsdale Wind Farm Stage 3: HWF3 Pty Ltd advises that Hornsdale Wind Farm Stage 3 (109 MW) is operational.
Hornsdale Power Reserve: Hornsdale Power Reserve Pty Ltd advises that Hornsdale Power Reserve Unit 1 (100 MW / 129 MWh) battery storage is operational.
Lincoln Gap Wind Farm Stage 1: Lincoln Gap Wind Farm Pty Ltd advises that Lincoln Gap Wind Farm Stage 1 (126 MW) is now a committed project.
Willogoleche Wind Farm: Willogoleche Power Pty Ltd advises that Willogoleche Wind Farm (119 MW) is now a committed project.
Generation withdrawals
Withdrawn
AEMO has not been advised of any plant that are currently withdrawn from this region.
Announced withdrawals (i.e. Mothballed, Seasonal Shut down etc.)
AEMO has not been advised of any announcements of plant that are to be withdrawn from this region.
Committed projects
Coal, CCGT, OCGT, Gas other, Water, Biomass, Geo-thermal, Other : None to report.
Solar: Bungala Solar Power Project (220 MW)
Wind: Lincoln Gap Wind Farm Stage 1 (126 MW), Willogoleche Wind Farm (119 MW)
Proposed projects
Please refer to information presented in the worksheet titled 'New Developments'.
Plant limitations
AEMO has not been advised of any plant limitations for this region.
South Australia existing and potential new developments by generation type (MW)
Status | Coal | CCGT | OCGT | Gas other | Solar | Wind | Water | Biomass | Storage | Other | Total
Existing | 0 | 658 | 914.8 | 1280 | 4.7228 | 1806.05 | 2.5 | 18.2 | 100 | 131.698 | 4915.9708
Announced Withdrawal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Existing less Announced Withdrawal | 0 | 658 | 914.8 | 1280 | 4.7228 | 1806.05 | 2.5 | 18.2 | 100 | 131.698 | 4915.9708
Committed | 0 | 0 | 4 | 0 | 220 | 245 | 0 | 0 | 0 | 0 | 469
Proposed | 0 | 500 | 350 | 0 | 911.7 | 3393.8 | 200 | 15 | 30 | 805.8 | 6206.3
Withdrawn | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note: Existing includes Announced Withdrawal
* Excludes rooftop PV installations

## Change Log
South Australia Change Log
Lists all key updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication date: | 2012-12-20
Snowtown S2: TrustPower advises that the Snowtown 2 project is now in a Committed status. Snowtown Stage 2 project will consist of two separately
metered wind farms, Snowtown 2 North (144 MW) and Snowtown 2 South (126 MW), sharing a single transmission line owned by TrustPower.
Publication date: | 2013-06-30
Playford B Power Station: Alinta energy advises that Playford B power station will be available with a recall time of around 90 days.
Alinta Energy have also revised the output from last year's in summer and winter from 200 MW to 180 MW (-20 MW) due to Turbine 2 being out of service.
However should AEMO require it, Turbine 2 can be brought back into service, taking the longer-term availability of Playford B Power Station up to 200 MW.
Hallett 4 North Brown Hill: AGL advises that Hallett 4 North Brown Hill's available capacity has been revised from 81.9 MW to 99.2 MW (+17.3 MW) in summer,
due to de-rating applied to all Suzlon S88/S97 machines.
Hallett Stage 1 Brown Hill: AGL advises that Hallett Stage 1 Brown Hill's available capacity has been revised from 58.5 MW to 70.9 MW (+12.4 MW) in summer,
due to de-rating applied to all Suzlon S88/S97 machines.
Publication date: | 2013-11-15
Palmer Wind Farm: TrustPower Australia advises that Palmer Wind Farm (up to 390 MW) has been newly announced. At this stage there has been no advice on construction and commissioning dates.
Port Macdonnell: Oceanlinx Limited advises that the status of the Port Macdonnell (1 MW) wave energy project is now Committed, with full commissioning in December 2013.
Publication date: | 2014-02-28
Port Macdonnell: Oceanlinx Limited advises that the Port Macdonnell (1 MW) wave energy project commissioning date was revised to March 2014.
Publication date: | 2014-05-30
Port Macdonnell: Oceanlinx Limited advises that the future of the Port Macdonnell (1 MW) wave energy project is uncertain and rests with company receivers. This project remains as a committed project with a commissioning date to be advised.
Publication date: | 2014-08-07
Paralana Project: Pertatherm Limited advises that Paralana project capacity has been revised to 3.5 MW.
Paralana Stage 2: Pertatherm Limited advises that Paralana Stage 2 capacity has been revised to 3.5 MW.
Publication date: | 2014-12-10
Northern Power Station: Alinta Energy advises that Northern Power Station Returned back to normal service in October 2014.
Snowtown S2: TrustPower advises that the Snowtown 2 wind farm (270 MW) project is now completed and in full commercial operation since November 2014.
Publication date: | 2015-04-15
Pelican Point Power Station: Pelican Point Power Limited advises that Pelican Point Power Station is to reduce the stations capacity to half from 1 April 2015 with unit 2 only being available on a 48 hour recall.
Torrens Island Power Station A: AGL Energy advises that Torrens Island Power Station is to be taken out of service in 2017.
Hornsdale Wind Farm (Stage 1): Hornsdale Wind Farm Pty Ltd advises construction to start in October 2015 and full commercial operation expected in November 2017.
Publication date: | 2015-08-13
Northern Power Station: Alinta Energy advised in June 2015 that Northern Power Station would retire by March 2018 at the latest, but not before March 2016. In late July Alinta Energy advised that Northern Power Station will retire by March 2017.
Playford B Power Station: Alinta energy advises that Playford B power station (240 MW) will retire by April 2017.
Publication date: | 2015-10-23
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) is planned to cease generation around 31 March 2016.
Playford B Power Station: Alinta Energy advises that Playford B Power Station (240 MW) is planned to cease generation around 31 March 2016.
Pelican Point Power Station: Pelican Point Power Limited advises Pelican Point Power Station’s available capacity has been reduced to 0 MW (-239 MW) in winter 2016 given the current dynamics and outlook in the electricity and gas markets.
Hornsdale Wind Farm (Stage 1): Hornsdale Wind Farm Pty Ltd advises that Stage 1 of Hornsdale Wind Farm (102.4 MW) is a committed project. Full commercial operation is expected in November 2016.
Port Augusta Renewable Energy Park: DP Energy advises of the Port Augusta Renewable Energy Park wind and solar project totalling 375 MW.
Point Paterson Project: Acquasol Infrastructure Pty Ltd advises that the proposed Point Paterson Projects has been put on hold.
Publication date: | 2016-03-03
Hornsdale Wind Farm (Stage 1): HWF 1 Pty Ltd advises that Stage 1 of Hornsdale Wind Farm (102.4 MW) is a committed project. Full commercial operation is expected in November 2016.
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) is planned to cease generation around March – May 2016.
New Development: Leigh Creek Energy Project, Lincoln Gap Wind Farm, Mount Hill, Palmer Wind Farm, Pelican Point S2, Port Augusta Renewable Energy Park, Stony Gap, Waterloo, Willogoleche, Woakwine Wind Farm, Kingfisher solar storage project, Roxby Downs Solar Farm, Yorke Penninsula Biomass Energy, Infratech’s floating PV plant, Epuron Uluru PV plant are added to the list.
Publication date: | 2016-04-15
Hornsdale Wind Farm (Stage 1): HWF 1 Pty Ltd advises that Stage 1 of Hornsdale Wind Farm (102.4 MW) is a committed project. Full commercial operation is expected in November 2016.
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) is planned to cease generation around March – May 2016.
Playford B Power Station: Alinta Energy advises that Playford B Power Station (240 MW) is planned to will retire around March - May 2016.
New Development: Leigh Creek Energy Project, Lincoln Gap Wind Farm, Mount Hill, Palmer Wind Farm, Pelican Point S2, Port Augusta Renewable Energy Park, Stony Gap, Waterloo, Willogoleche, Woakwine Wind Farm, Kingfisher solar storage project, Roxby Downs Solar Farm, Yorke Penninsula Biomass Energy, Infratech’s floating PV plant, are added to the list.
Publication date: | 2016-08-11
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) has closed operations in May 2016.
Playford B Power Station: Alinta Energy advises that Playford B Power Station (240 MW) has closed operations in May 2016.
Torrens Island Power Station A: AGL Energy advises that it will defer the previously planned mothballing of four generating units from its Torrens Island A Power Station (480 MW) in June 2016.
Hornsdale Wind Farm (Stage 2): HWF 2 advises that Stage 2 of Hornsdale Wind Farm (102.4 MW) is a committed project.
Waterloo Expansion: Waterloo Windfarm Ptd Ltd. advises that Waterloo Expansion Wind Farm (19.8 MW) is a committed project.
Angaston: Lumo Generation SA Pty Ltd. advises that Angaston Power Station (50 MW) has changed registration status from Non-Scheduled to Scheduled.
New Development: Aurora Solar Energy Project, Bungala Solar Power Project, Port Augusta Solar, Yorke Peninsula Biomass.
Publication date: | 2016-11-18
Hornsdale Wind Farm Stage 1: HWF1 Pty Ltd advises that Hornsdale Wind Farm Stage 1 (102.4 MW) is now completed and undergoing commissioning tests.
Waterloo: Waterloo Windfarm Pty Ltd advises that the Waterloo Wind Farm expansion (+19.8 MW) is now completed and undergoing commissioning tests.
Publication date: | 2017-02-27
Hornsdale Wind Farm Stage 2: HWF2 Pty Ltd advises that Hornsdale Wind Farm Stage 2 is undergoing construction and first/early generation happened on the 21st of February of 2017. Practical Completion under the EPC Contract is expected on 08/06/17 and Full Commercial Operation (FiT ACT Government) will commence on 01/12/18.
Publication date: | 2017-06-05
Bungala Solar Power Project: Reach Solar Management Co advises that Bungala Solar Power Project (220 MW) is now a committed project.
Hornsdale Wind Farm Stage 3: HWF 3 Pty Ltd advises that Hornsdale Wind Farm Stage 3 (109 MW) is now a committed project.
Pelican Point: Pelican Point Power Limited advises that Pelican Point (478 MW) is currently operating at half capacity (239 MW), but will make the full capacity available to market as of July 1 2017.
Publication date: | 2017-12-22
Hornsdale Wind Farm Stage 2: HWF2 Pty Ltd advises that Hornsdale Wind Farm Stage 2 (102 MW) is operational.
Hornsdale Wind Farm Stage 3: HWF3 Pty Ltd advises that Hornsdale Wind Farm Stage 3 (109 MW) is operational.
Hornsdale Power Reserve: Hornsdale Power Reserve Pty Ltd advises that Hornsdale Power Reserve Unit 1 (100 MW / 129 MWh) battery storage is operational.
Lincoln Gap Wind Farm Stage 1: Lincoln Gap Wind Farm Pty Ltd advises that Lincoln Gap Wind Farm Stage 1 (126 MW) is now a committed project.
Willogoleche Wind Farm: Willogoleche Power Pty Ltd advises that Willogoleche Wind Farm (119 MW) is now a committed project.

## Existing S & SS Generation
Existing scheduled and semi-scheduled generation
Power Station | Owner | Unit Number and Nameplate Capacity (MW) | Installed Capacity (MW) | Technology Type | Fuel Type | Dispatch Type | Service Status
Angaston | Lumo Generation SA Pty Ltd | 12 x 1.66 18 x 1.66 | 50 | Compression Reciprocating Engine | Diesel | S | In Service
Clements Gap | Pacific Hydro Clements Gap Pty Ltd | 27 x 2.1 | 56.7 | Wind - Onshore | Wind | SS | In Service
Dry Creek GT | Synergen Power Pty Ltd | 3 x 52 | 156 | OCGT | Natural Gas Pipeline | S | In Service
Hallett 4 North Brown Hill | Brown Hill North Pty Ltd | 63 x 2.1 | 132.3 | Wind - Onshore | Wind | SS | In Service
Hallett 5 The Bluff WF | Eurus Energy | 25 x 2.1 | 52.5 | Wind - Onshore | Wind | SS | In Service
Hallett GT | EnergyAustralia | 4 x 16.4 3 x 17 2 x 17.3 2 x 24.8 1 x 27.5 | 228.3 | OCGT | Natural Gas Pipeline | S | In Service
Hallett Stage 1 Brown Hill | Palisade Investment Partner Limited | 45 x 2.1 | 94.5 | Wind - Onshore | Wind | SS | In Service
Hallett Stage 2 Hallett Hill | Infrastructure Capital Group Limited | 34 x 2.1 | 71.4 | Wind - Onshore | Wind | SS | In Service
Hornsdale Power Reserve Unit 1 | Hornsdale Power Reserve Pty Ltd | 100 MW 129 MWh | 100 | Battery Storage | Storage | S | In Service
Hornsdale Wind Farm Stage 1 | HWF 1 Pty Ltd | 32 x 3.2 | 102.4 | Wind - Onshore | Wind | SS | In Service
Hornsdale Wind Farm Stage 2 | HWF 2 Pty Ltd | 32 x 3.2 | 102.4 | Wind - Onshore | Wind | SS | In Service
Hornsdale Wind Farm Stage 3 | HWF 3 Pty Ltd | 35 x 3.2 | 109 | Wind - Onshore | Wind | SS | In Service
Ladbroke Grove | Origin Energy Power Limited | 2 x 40 | 80 | OCGT | Natural Gas Pipeline | S | In Service
Lake Bonney 2 Wind Farm | Lake Bonney Wind Power Pty Ltd | 53 x 3 | 159 | Wind - Onshore | Wind | SS | In Service
Lake Bonney 3 Wind Farm | Lake Bonney Wind Power Pty Ltd | 13 x 3 | 39 | Wind - Onshore | Wind | SS | In Service
Lonsdale | Lumo Generation SA Pty Ltd | 18 x 1.15 | 20.7 | Compression Reciprocating Engine | Diesel | S | In Service
Mintaro GT | Synergen Power Pty Ltd | 1 x 90 | 90 | OCGT | Natural Gas Pipeline | S | In Service
Osborne | Osborne Cogeneration Pty Ltd | 1 x 118 1 x 62 | 180 | CCGT | Natural Gas Pipeline | S | In Service
Pelican Point | Pelican Point Power Limited | 2 x 239 | 478 | CCGT | Natural Gas Pipeline | S | In Service (Half capacity)
Port Lincoln GT | Synergen Power Pty Ltd | 2 x 25 1 x 23.5 | 73.5 | OCGT | Diesel | S | In Service
Port Stanvac 1 | Lumo Generation SA Pty Ltd | 36 x 1.6 | 57.6 | Compression Reciprocating Engine | Diesel | S | In Service
Quarantine | Origin Energy Power Limited | 4 x 24 1 x 128 | 224 | OCGT | Natural Gas Pipeline | S | In Service
Snowtown | Snowtown Wind Farm Pty Ltd | 47 x 2.1 | 98.7 | Wind - Onshore | Wind | SS | In Service
Snowtown S2 | Snowtown Wind Farm Stage 2 Pty Ltd | 90 x 3 | 270 | Wind - Onshore | Wind | SS | In Service
Snuggery | Synergen Power Pty Ltd | 3 x 21 | 63 | OCGT | Diesel | S | In Service
Torrens Island A | AGL Energy | 4 x 120 | 480 | Steam Sub Critical | Natural Gas Pipeline | S | In Service
Torrens Island B | AGL Energy | 4 x 200 | 800 | Steam Sub Critical | Natural Gas Pipeline | S | In Service
Waterloo | Waterloo Windfarm Pty Ltd | 6 x 3.3 37 x 3 | 130.8 | Wind - Onshore | Wind | SS | In Service
Total |  |  | 4499.8

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation
Power Station | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | Dispatch Type
Angaston | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | S
Bungala Solar Power Project | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | SS
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Dry Creek GT | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | S
Hallett 4 North Brown Hill | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | SS
Hallett 5 The Bluff WF | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | SS
Hallett GT | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | S
Hallett Stage 1 Brown Hill | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | SS
Hallett Stage 2 Hallett Hill | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | SS
Hornsdale Power Reserve Unit 1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | S
Hornsdale Wind Farm Stage 1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Hornsdale Wind Farm Stage 2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Hornsdale Wind Farm Stage 3 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | SS
Ladbroke Grove | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Lake Bonney 2 Wind Farm | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | SS
Lake Bonney 3 Wind Farm | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | SS
Lincoln Gap Wind Farm Stage 1 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Lonsdale | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | S
Mintaro GT | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Osborne | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | S
Pelican Point | 458 | 458 | 458 | 458 | 458 | 458 | 458 | 458 | 458 | 458 | S
Port Lincoln GT | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | S
Port Stanvac 1 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | S
Quarantine | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | S
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snowtown S2 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | SS
Snuggery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | S
Torrens Island A | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | S
Torrens Island B | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | S
Waterloo | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | SS
Willogoleche Wind Farm | 0 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | SS
Total | 4214.61 | 4679.61 | 4679.61 | 4679.61 | 4679.61 | 4679.61 | 4679.61 | 4679.61 | 4679.61 | 4679.61
The table above lists the latest Summer capacities for South Australian generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. These figures are 9.4% of the installed capacity during summer, and 7.0% during winter, based on AEMO's analysis of historical wind output over summer 2011-12 to 2015-16, and winter 2011 - 2015.
Due to the intermittent nature of sunlight, solar generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. However, AEMO has not yet calculated contribution factors for solar, due to there being insufficient historical data to analyse for semi-scheduled solar generation in South Australia. Thus the Firm Solar Capacity values in the table below are shown as NA, and do not contribute to the total capacity in that table.
The two tables below have been included to better represent the supply availability in South Australia, by taking into account the firm contribution by semi-scheduled generation. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm semi-scheduled generation. The Summer aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled generation for the Summer period. The total refers to the maximum amount that can be generated from the semi-scheduled generation at the Summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation
Power Station | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | Dispatch Type
Angaston | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | S
Dry Creek GT | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | S
Hallett GT | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | S
Hornsdale Power Reserve Unit 1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | S
Ladbroke Grove | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Lonsdale | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | S
Mintaro GT | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Osborne | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | S
Pelican Point | 458 | 458 | 458 | 458 | 458 | 458 | 458 | 458 | 458 | 458 | S
Port Lincoln GT | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | S
Port Stanvac 1 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | S
Quarantine | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | S
Snuggery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | S
Torrens Island A | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | S
Torrens Island B | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | S
Firm Wind Capacity | 127.7751 | 150.8051 | 150.8051 | 150.8051 | 150.8051 | 150.8051 | 150.8051 | 150.8051 | 150.8051 | 150.8051 | SS
Firm Solar Capacity | [10 empty] | SS | bar: 2017-18 to 2026-27
Total | 2983.0751 | 3006.1051 | 3006.1051 | 3006.1051 | 3006.1051 | 3006.1051 | 3006.1051 | 3006.1051 | 3006.1051 | 3006.1051
Summer aggregate available semi-scheduled generation
Power Station | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | Dispatch Type
Bungala Solar Power Project | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | SS
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Hallett 4 North Brown Hill | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | SS
Hallett 5 The Bluff WF | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | 39.38 | SS
Hallett Stage 1 Brown Hill | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | 70.88 | SS
Hallett Stage 2 Hallett Hill | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | 53.55 | SS
Hornsdale Wind Farm Stage 1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Hornsdale Wind Farm Stage 2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Hornsdale Wind Farm Stage 3 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | SS
Lake Bonney 2 Wind Farm | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | SS
Lake Bonney 3 Wind Farm | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | SS
Lincoln Gap Wind Farm Stage 1 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snowtown S2 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | SS
Waterloo | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | SS
Willogoleche Wind Farm | 0 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | SS
Total (Wind) | 1359.31 | 1604.31 | 1604.31 | 1604.31 | 1604.31 | 1604.31 | 1604.31 | 1604.31 | 1604.31 | 1604.31
Total (Solar) | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220

## Winter Scheduled Capacities
Winter aggregate available scheduled and semi-scheduled generation
Power Station | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | Dispatch Type
Angaston | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | S
Bungala Solar Power Project | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | SS
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Dry Creek GT | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | S
Hallett 4 North Brown Hill | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | SS
Hallett 5 The Bluff WF | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | SS
Hallett GT | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | S
Hallett Stage 1 Brown Hill | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | SS
Hallett Stage 2 Hallett Hill | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | SS
Hornsdale Power Reserve Unit 1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | S
Hornsdale Wind Farm Stage 1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Hornsdale Wind Farm Stage 2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Hornsdale Wind Farm Stage 3 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | SS
Ladbroke Grove | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Lake Bonney 2 Wind Farm | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | SS
Lake Bonney 3 Wind Farm | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | SS
Lincoln Gap Wind Farm Stage 1 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Lonsdale | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | S
Mintaro GT | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Osborne | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | S
Pelican Point | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | S
Port Lincoln GT | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | S
Port Stanvac 1 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | S
Quarantine | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | S
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snowtown S2 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | SS
Snuggery | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Torrens Island A | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | S
Torrens Island B | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | S
Waterloo | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | SS
Willogoleche Wind Farm | 0 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | SS
Total | 4476.7 | 4941.7 | 4941.7 | 4941.7 | 4941.7 | 4941.7 | 4941.7 | 4941.7 | 4941.7 | 4941.7
The table above lists the latest Winter capacities for South Australian generation. Winter conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. These figures are 9.4% of the installed capacity during summer, and 7.0% during winter, based on AEMO's analysis of historical wind output over summer 2011-12 to 2015-16, and winter 2011 - 2015.
Due to the intermittent nature of sunlight, solar generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. However, AEMO has not yet calculated contribution factors for solar, due to there being insufficient historical data to analyse for semi-scheduled solar generation in South Australia. Thus the Firm Solar Capacity values in the table below are shown as NA, and do not contribute to the total capacity in that table.
The two tables below have been included to better represent the supply availability in South Australia, by taking into account the firm contribution by semi-scheduled generation. The Winter aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm semi-scheduled generation. The Winter aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled generation for the Winter period. The total refers to the maximum amount that can be generated from the semi-scheduled generation at the Winter reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation
Power Station | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | Dispatch Type
Angaston | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | S
Dry Creek GT | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | S
Hallett GT | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | S
Hornsdale Power Reserve Unit 1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | S
Ladbroke Grove | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Lonsdale | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | S
Mintaro GT | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Osborne | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | S
Pelican Point | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | S
Port Lincoln GT | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | S
Port Stanvac 1 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | S
Quarantine | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | S
Snuggery | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Torrens Island A | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | S
Torrens Island B | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | S
Firm Wind Capacity | 107.513 | 116.333 | 116.333 | 116.333 | 116.333 | 116.333 | 116.333 | 116.333 | 116.333 | 116.333 | SS
Firm Solar Capacity | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | SS
Total | 3167.313 | 3176.133 | 3176.133 | 3176.133 | 3176.133 | 3176.133 | 3176.133 | 3176.133 | 3176.133 | 3176.133
Winter aggregate available semi-scheduled generation
Power Station | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | Dispatch Type
Bungala Solar Power Project | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | SS
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Hallett 4 North Brown Hill | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | SS
Hallett 5 The Bluff WF | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | SS
Hallett Stage 1 Brown Hill | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | SS
Hallett Stage 2 Hallett Hill | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4 | SS
Hornsdale Wind Farm Stage 1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Hornsdale Wind Farm Stage 2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Hornsdale Wind Farm Stage 3 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | SS
Lake Bonney 2 Wind Farm | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | SS
Lake Bonney 3 Wind Farm | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | SS
Lincoln Gap Wind Farm Stage 1 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snowtown S2 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | SS
Waterloo | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | 130.8 | SS
Willogoleche Wind Farm | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | SS
Total (Wind) | 1535.9 | 1661.9 | 1661.9 | 1661.9 | 1661.9 | 1661.9 | 1661.9 | 1661.9 | 1661.9 | 1661.9
Total (Solar) | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220

## Existing NS Generation
Existing non-scheduled generation
Power Station | Owner | Nameplate Capacity (MW) | Technology Type | Fuel Type | Service Status
Blue Lake Milling Power Plant | Vibe Energy Pty Ltd | 0.505 | Compression Reciprocating Engine | Diesel | In service
Bolivar Waste Water Treatment | South Australian Water Corporation | 10 | Spark Ignition Reciprocating Engine | Sewerage / Waste Water | In service
Canunda | Canunda Power Pty Ltd | 46 | Wind - Onshore | Wind | In service
Cathedral Rocks | JV Cathedral Rock Investments Pty Ltd and Acciona Energy Oceania Pty Ltd | 66 | Wind - Onshore | Wind | In service
Lake Bonney 1 Wind Farm | Lake Bonney Wind Power Pty Ltd | 80.5 | Wind - Onshore | Wind | In service
Mt Millar | Mount Millar Wind Farm Pty Ltd | 70 | Wind - Onshore | Wind | In service
Starfish Hill | Ratch Australia | 34.5 | Wind - Onshore | Wind | In service
Tatiara Meats | Vibe Energy Pty Ltd | 0.5 | Compression Reciprocating Engine | Diesel | In service
Terminal Storage Mini Hydro | Lofty Ranges Power Pty Ltd | 2.5 | Hydro - Gravity | Water | In service
Wattle Point | Infrastructure Capital Group | 90.75 | Wind - Onshore | Wind | In service
Wingfield 1 | EDL LFG SA Pty Ltd | 4.1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Wingfield 2 | EDL LFG SA Pty Ltd | 4.1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Adelaide Zoo Solar System | TBA | 0.1508 | PV Panels | Solar | In service
NAWMA - LFG - SOLAR | Northern Adelaide Waste Management Authority | 2.393 | Solar + methane | Other | In service
Redmud Green Energy 10 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 11 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 12 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 13 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 14 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 4 | TBA | 0.6 | PV Panels | Solar | In service
Redmud Green Energy 5 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 6 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 7 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 8 | TBA | 0.212 | PV Panels | Solar | In service
Redmud Green Energy 9 | TBA | 0.212 | PV Panels | Solar | In service
SA Aquatic & Leasure Centre | TBA | 0.512 | PV Panels | Solar | In service
Yalumba Winery Solar system (Angaston) | TBA | 1.14 | PV Panels | Solar | In service
Yalumba Winery Solar system (Oxford Landing) | TBA | 0.2 | PV Panels | Solar | In service
Total |  | 416.5708

## New Developments
Projects under development
Project | Owner | Unit ID | Technology Type | Fuel Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Full Commercial Use Date | Source
Aurora Solar Energy Project | SolarReserve |  | Solar Thermal + Storage | Solar | [5 empty] | Pub An | 150 | S | TBA | http://www.solarreserve.com/en/global-projects/csp/aurora
Barker Inlet Power Station | AGL Energy Limited | 12 | Reciprocating engines (gas/diesel) | Other | ü |  |  | ü | ü | Adv | 210 | S | Sep-2019 | https://www.agl.com.au/about-agl/media-centre/asx-and-media-releases/2017/june/agl-announces-development-of-$295m-power-station-in-sa
Barn Hill | AGL Energy Limited | 1-62 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 220 | SS | TBA
BHP Olympic Dam Backup Generation | TBA |  | Reciprocating engines (gas/diesel) | Diesel | [5 empty] | Pub An | 30 | TBA | TBA
Bungala Solar Power Project | Reach Solar Management Co |  | PV - single axis tracking | Solar | ü | ü | ü | ü | ü | Com | 220 | SS | Aug-2018 | www.power-technology.com/projects/bungala-solar-pv-plant-port-augusta/
Carmodys Hill | Energy Pacific Vic Pty Ltd | 1-70 | Wind - Onshore | Wind | [5 empty] | Pub An | 140 | SS | TBA
Ceres Project | Senvion Australia |  | Wind - Onshore | Wind | [5 empty] | Pub An | 636 | SS | TBA | http://www.theceresproject.com.au/the_ceres_project
Dalrymple Battery storage | ElectraNet |  | Battery Storage | Storage | [5 empty] | Pub An | 30 | TBA | TBA
Exmoor | Acciona Energy Oceania Pty Ltd | 1-48 | Wind - Onshore | Wind | [5 empty] | Pub An | 144 | SS | TBA
Hallett RePower | Energy Australia | 1 | OCGT | Natural Gas | [5 empty] | Pub An | 30 | S | TBA
Keyneton | Energy Pacific Vic Pty Ltd | 1-42 | Wind - Onshore | Wind | [5 empty] | Pub An | 105 | SS | TBA
Kingfisher Solar Storage | Lyon Solar |  | PV - single axis tracking | Solar | ü |  |  |  | ü | Pub An | 120 | SS | TBA
Kongorong | Ratch Australia Corporation | 1-57 | Wind - Onshore | Wind | [5 empty] | Pub An | 240 | SS | Jun-2021
Kulpara | Ratch Australia Corporation | 30 | Wind - Onshore | Wind | [5 empty] | Pub An | 103 | SS | TBA
Leigh Creek Energy project | Leigh Creek Energy Limited | 5 | CCGT | Syngas | [5 empty] | Pub An | 500 | S | TBA
Lincoln Gap Wind Farm Stage 1 | Lincoln Gap Wind Farm Pty Ltd | 1-59 | Wind - Onshore | Wind | ü | ü | ü | ü | ü | Com | 126 | SS | Oct-2018 | http://lincolngapwindfarm.com.au/about-the-project/
Lincoln Gap Wind Farm Stage 2 | Lincoln Gap Wind Farm Pty Ltd |  | Wind - Onshore | Wind | [5 empty] | Pub An | 86 | SS | TBA
Palmer Wind Farm | Tilt Renewables Australia | 1-103 | Wind - Onshore | Wind | [5 empty] | Pub An | 309 | SS | Dec-2018 | https://www.mid-murray.sa.gov.au/webdata/resources/files/Palmer%20Wind%20Farm%20Fact%20Sheet%20-%203%20March%202017.pdf , https://www.tiltrenewables.com/assets-and-projects/Palmer-Wind-Farm/
Pelican Point S2 | Pelican Point Power Limited | 12 | OCGT | Natural Gas | [5 empty] | Pub An | 320 | S | TBA
Planet Ark Power and Schneider Electric - PV and Battery Microgrid | Planet Ark Power and Schneider Electric |  | PV + storage | Solar | [5 empty] | Pub An | 5.7 | TBA | TBA | https://planetarkpower.com/papower2/wp-content/uploads/2017/11/29-November-Next-wave-of-energy-storage-projects-announced.pdf
Port Augusta Graphite Energy | Solastor Pty Ltd | 2 | Solar Thermal + Storage | Solar | ü |  |  |  |  | Pub An | 110 | SS | TBA
Port Augusta Renewable Energy Park (Stage 1) | PAREP 1 PTY LIMITED |  | Wind - Onshore | Wind | [5 empty] | Pub An | 375 | SS | TBA
Port Augusta Renewable Energy Park (Stage 2) | DP Energy Australia Pty Ltd |  | PV - single axis tracking | Solar | [5 empty] | Pub An |  | TBA | TBA
Quarantine Expansion | Origin Energy |  | OCGT | Natural Gas | [5 empty] | Pub An |  | TBA | TBA
Quarantine Repower | Origin Energy | 1 | OCGT | Natural Gas |  |  |  |  | ü | Com | 4 | NS | Summer 2018/19
Riverland Solar Storage | Lyon Solar |  | PV - single axis tracking | Other | ü |  |  |  | ü | Pub An | 330 | SS | TBA | http://lyonbatterystorage.com.au/projects/
SA Diesels | TBA |  | TBA | Diesel | [5 empty] | Pub An | 277 | TBA | TBA
Spencer Gulf Pumped Storage Hydro | Energy Australia |  | Pump Storage | Water | [5 empty] | Pub An | 200 | S | Dec-2020
Stony Gap | Energy Australia | 1-35 | Wind - Onshore | Wind | [5 empty] | Pub An |  | SS | TBA
Tailem Bend | Equis | 1 | PV – no tracking (fixed flat plate) | Solar | ü |  |  |  |  | Pub An | 108 | SS | TBA | http://equisenergy.com/wp-content/uploads/2017/05/EQUIS-ENERGY-Equis-Expands-into-Australia-with-Two-Large-Scale-Solar-Projects-1-Feb-2017.pdf
Tailem Bend - Diesel | Snowy Hydro Ltd | 1 | Compression Reciprocating Engine | Diesel | ü | ü |  | ü |  | Adv | 28.8 | S | TBA
Tailem Bend Solar Project | Equis |  | PV – no tracking (fixed flat plate) | Solar | ü |  |  |  |  | Pub An | 108 | SS | TBA
Whyalla Solar Farm | Energy Pacific Vic Pty Ltd |  | PV - single axis tracking | Solar | [5 empty] | Pub An | 100 | SS | TBA
Whyalla Solar Farm | Adani Rugby Run Pty Ltd |  | PV Panels | Solar | ü |  |  |  | ü | Pub An | 140 | SS | Apr-2019
Willogoleche Wind Farm | Willogoleche Power Pty Ltd |  | Wind - Onshore | Wind | ü | ü | ü | ü | ü | Com | 119 | SS | Winter 2018 | http://www.gdfsuezau.com/about-us/asset/Willogoleche-Wind-Farm
Woakwine Wind Farm | Infigen Energy | Turbines 1-124 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 400 | SS | TBA
Yorke Peninsula Biomass | Kallis Family Trust | 1 | Steam Sub Critical | Straw based fuel | ü |  |  |  | ü | Pub An | 15 | NS | TBA
Yorke Peninsula Wind Farm | Senvion Australia | 187 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 635.8 | SS | Jun-2020 | http://www.theceresproject.com.au/
Com* - Identifies projects that are under construction, but AEMO has not been informed that the project meets all 5 commitment criteria

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as semi-scheduled or non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as scheduled or non-scheduled. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW, unless AEMO approves its classification as scheduled or semi-scheduled.
Generating systems greater than 30 MW must be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating of less than 5 MW may be exempted by AEMO if its generation is purchased entirely by the local retail or a customer at the generator's connection point or the generator is classified as a market generating unit by a market small generation aggregator. A generating unit with a nameplate rating between 5 MW and 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of reliability assessments and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedance (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation and storage for which formal commitment has been made for construction or installation.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects are either under construction or meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction and connection approvals/EIS | The proponent has obtained all required planning consents, construction approvals, connection contracts (including Generator Performance Standard agreement from AEMO in the form of the 534A letter), and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.