## Queensland Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer on the 'Disclaimer' tab of this workbook.
Queensland Summary
Committed project developments
Kogan Creek Solar Boost: CS Energy advises that the Kogan Creek Solar Boost project (44 MW) is now a committed project and due to be completed in 2014. Note that the 44 MW capacity is not additional to the 730/744 MW summer/winter capacities of Kogan Creek, rather it is a contribution towards the total generation.
Plant retirements
AEMO has not been advised of any plant retirements in Queensland within the 10-year planning outlook.
Changes since the 2012 ESOO (existing generation)
Tarong Power Station: Stanwell Corporation advises that the Tarong plant has revised its available capacity from 1,400 MW to 700 MW (-700 MW) in summer and winter, due to the withdrawal of service of Unit 2 (DUID TARONG#2) in October 2012 and Unit 4 (DUID TARONG#4) in December 2012, both for a period of at least two years or until wholesale electricity demand improves.
Collinsville Power Station: Ratch Australia advises that the Collinsville plant has revised its available capacity from 190 MW to 0 MW (-190 MW) in summer and winter, due to the withdrawal of service of all generation units from 31 December 2012, until wholesale electricity demand improves. The Collinsville plant was de-registered on 1 Jan 2013.
Braemar Power Station: Alinta Energy advised in February 2013 that Braemar's available capacity had been revised from 435 MW to 480 MW (+45 MW) in summer, due to the regular use of Evaporative Cooling and Peak Firing of the units. These modes of operation result in the units achieving higher levels of output than would be typically expected during periods of high temperature. Alinta's latest advice is that the revised available capacity has changed from 480 MW to 465 MW (-15 MW) in summer.
Darling Downs Power Station: Alinta Energy advises that Darling Downs available capacity has been revised from 605 MW to 580 MW (-25 MW) in summer, reflecting capability at higher temperatures.
Millmerran Power Station: Millmerran Power Partners advises that the Millmerran plant has revised its available capacity from 856 MW to 760 MW (-96 MW) in summer, based on operating experience on higher temperature days.
Plant limitations
Tarong Power Station: Stanwell Corporation advises that Tarong will undergo the following outages:
· Unit 1 will be unavailable during:
- summer 2016–17 (until 12 November 2016).
· Unit 2 will be unavailable during:
- winter 2013 (from 4 August 2013), and
- winter 2015 (from 1 August 2015 to 11 August 2015).
· Unit 4 will be unavailable during:
- winter 2014 (from 2 August 2014), and
- winter 2016 (from 6 August 2016 to 16 August 2016).
Tarong North Power Station: Stanwell Corporation advises that Tarong North Power Station will undergo the following outages:
· Unit 1 will be unavailable during:
- summer 2013–14 (until 15 November 2013), and
- summer 2015–16 (until 14 November 2015).

## Change Log
Queensland Change Log
Lists all updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication Date: | 2012-12-20
Solar Dawn Project: Areva and the Solar Dawn Consortium advised it would no longer develop the proposed 250 MW solar thermal power facility in South-West Queensland.
Tarong Power Station: Stanwell Corporation advises that the Tarong plant has revised its available capacity from 1,400 MW to 700 MW (-700 MW) in summer and winter,
due to the withdrawal of service of Unit 2 (DUID TARONG#2) in October 2012 and Unit 4 (DUID TARONG#4) in December 2012, both for a period of at least two years
or until wholesale electricity demand improves.
Collinsville Power Station: Ratch Australia advises that the Collinsville plant has revised its available capacity from 190 MW to 0 MW (-190 MW) in summer and winter, due to the withdrawal of service of all generation units from 31 December 2012, until wholesale electricity demand improves.
Publication Date: | 2013-02-22
Millmerran Power Station: Millmerran Power Partners advises that the Millmerran plant has revised its available capacity from 856 MW to 760 MW (-96 MW) in summer, based on operating experience on higher temperature days.
Braemar Power Station: Alinta Energy advises that Braemar's available capacity has been revised from 435 MW to 480 MW (+45 MW) in summer, due to use of Evaporative Cooling and Peak Firing of the units.
Publication Date: | 2013-06-30
Braemar Power Station: Alinta Energy advises that Braemar's available capacity has been revised from 435 MW to 465 MW (+30 MW) in summer (an increase from last years ESOO), due to the regular use of Evaporative Cooling and Peak Firing of the units. These modes of operation result in the units achieving higher levels of output than would be typically expected during periods of high temperature.
Darling Downs Power Station: Alinta Energy advises that Darling Downs available capacity has been revised from 605 MW to 580 MW (-25 MW) in summer, reflecting capability at higher temperatures.
Kogan Creek Solar Boost: CS Energy advises that the Kogan Creek Solar Boost project is now a committed project and due to be completed in Jan 2014.

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless classified as semi-scheduled, or AEMO is permitted to classify it as non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW and equal to or greater than 5 MW.
Generating systems greater than 30 MW may be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating less than 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Installed | Plant Type | Fuel | Dispatch Type
Capacity (MW)
Barcaldine Power Station | Ergon Energy Queensland Pty Ltd | 1 x 37 1 x 18 | 55 | CCGT | Natural Gas Pipeline | S
Barron Gorge | Stanwell Corporation Limited | 2 x 33 | 66 | Run of River | Water | S
Braemar | Braemar Power Project Pty Ltd | 3 x 168 | 504 | OCGT | Coal Seam Methane | S
Braemar 2 | NewGen Braemar 2 Partnership | 3 x 173 | 519 | OCGT | Coal Seam Methane | S
Callide B | CS Energy | 2 x 350 | 700 | Steam Sub Critical | Black Coal | S
Callide C | Callide Power Management | 2 x 450 | 900 | Steam Super Critical | Black Coal | S
Collinsville | Ratch Australia | 2 x 31.5 2 x 30.5 1 x 66 | 190 | Steam Sub Critical | Black Coal | S
Condamine A | QGC | 1 x 144 | 144 | CCGT | Coal Seam Methane | S
Darling Downs | Origin Energy Power Limited | 1 x 280 3 x 121.5 | 644.5 | CCGT | Coal Seam Methane | S
Gladstone | Gladstone Power Station Participants | 6 x 280 | 1680 | Steam Sub Critical | Black Coal | S
Kareeya | Stanwell Corporation Limited | 4 x 21.6 | 86.4 | Run of River | Water | S
Kogan Creek | CS Energy | 1 x 744 | 744 | Steam Super Critical | Black Coal | S
Mackay GT | Stanwell Corporation Limited | 1 x 34 | 34 | OCGT | Diesel | S
Millmerran | Millmerran Power Partners | 2 x 426 | 852 | Steam Super Critical | Black Coal | S
Mt Stuart | Origin Energy Mt Stuart | 2 x 146 1 x 131.5 | 423.5 | OCGT | Kerosene Aviation fuel used for stationary energy | S
Oakey | Oakey Power Holdings | 2 x 140.9 | 281.8 | OCGT | Diesel | S
Roma | Origin Energy Power Limited | 2 x 40 | 80 | OCGT | Natural Gas Pipeline | S
Stanwell | Stanwell Corporation Limited | 4 x 365 | 1460 | Steam Sub Critical | Black Coal | S
Swanbank E GT | Stanwell Corporation Limited | 1 x 385 | 385 | CCGT | Coal Seam Methane | S
Tarong | Stanwell Corporation Limited | 4 x 350 | 1400 | Steam Sub Critical | Black Coal | S
Tarong North | Stanwell Corporation Limited | 1 x 450 | 450 | Steam Super Critical | Black Coal | S
Wivenhoe | CS Energy | 2 x 250 | 500 | Pump Storage | Water | S
Yabulua | Ratch Australia | 1 x 160 1 x 84 | 244 | CCGT | Coal Seam Methane | S
Total |  |  | 12343.2
a. Formerly known as Townsville GT.

## Existing Wind Generation
Existing & committed wind generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Installed | Plant Type | Fuel | Dispatch Type
Capacity (MW)
Windy Hill | Ratch Australia | 20 x 0.6 | 12 | Wind - Onshore | Wind | NS
Total |  |  | 12

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation – Queensland (MW)
Power Station | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | Dispatch Type
Barcaldine | –14 | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | S
Barcaldine Power Station | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | S
Barron Gorge | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | S
Braemar | 465 | 465 | 465 | 465 | 465 | 465 | 465 | 465 | 465 | 465 | S
Braemar 2 | 495 | 495 | 495 | 495 | 495 | 495 | 495 | 495 | 495 | 495 | S
Callide B | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | S
Callide C | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | S
Collinsville | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Condamine A | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | S
Darling Downs | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | S
Gladstone | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | S
Kareeya | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | S
Kogan Creek | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | S
Mackay GT | 34 | 34 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | S
Millmerran | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760 | S
Mt Stuart | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | S
Oakey | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | S
Roma | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | S
Stanwell | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | S
Swanbank E GT | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | S
Tarong | 700 | 700 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Tarong North | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | S
Wivenhoe | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | S
Yabulua | 235 | 235 | 234 | 234 | 233 | 233 | 233 | 232 | 232 | 232 | S
Total | 11077.4 | 11077.4 | 11776.4 | 11776.4 | 11741.4 | 11741.4 | 11741.4 | 11740.4 | 11740.4 | 11740.4
a. Formerly known as Townsville GT.

## Winter Scheduled Capacities
Winter aggregate available scheduled and semi-scheduled generation – Queensland (MW)
Project Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Barcaldine Power Station | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | S
Barron Gorge | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | S
Braemar | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | S
Braemar 2 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | S
Callide B | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | S
Callide C | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | S
Collinsville | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Condamine A | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | S
Darling Downs | 630 | 630 | 630 | 630 | 630 | 630 | 630 | 630 | 630 | 630 | S
Gladstone | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | S
Kareeya | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | S
Kogan Creek | 744 | 744 | 744 | 744 | 744 | 744 | 744 | 744 | 744 | 744 | S
Mackay GT | 34 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Millmerran | 852 | 852 | 852 | 852 | 852 | 852 | 852 | 852 | 852 | 852 | S
Mt Stuart | 419 | 419 | 419 | 419 | 419 | 419 | 419 | 419 | 419 | 419 | S
Oakey | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | S
Roma | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Stanwell | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | S
Swanbank E GT | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | S
Tarong | 700 | 700 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Tarong North | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | S
Wivenhoe | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | S
Yabulua | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 242 | 242 | 242 | S
Total | 11439.4 | 11439.4 | 12139.4 | 12105.4 | 12105.4 | 12105.4 | 12105.4 | 12104.4 | 12104.4 | 12104.4
a. Formerly known as Townsville GT.

## New Developments
Projects under development – Queensland
Project | Owner | Unit ID | Fuel Type | Generation Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW)a | Dispatch Type | Commissioning Start Date
Aldoga Power Station | EnergyAustralia | 1-6 | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 1500 | S | TBA
Archer Point | Wind Power Queensland Pty Ltd | 1-60 | Wind | Wind - Onshore | [5 empty] | Pub An | 120 | SS | 2015-12-31
Blackstone Power Station | EnergyAustralia | One | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 1500 | S | TBA
Bowen | Ratch Australia | 1-60/80 | Wind | Wind - Onshore | [5 empty] | Pub An | 120-240 | SS | TBA
Braemar 3 | ERM Power Limited | 1-2 | Coal Seam Methane | OCGT | ü |  |  |  |  | Pub An | 550 | S | TBA
Braemar 4 | ERM Power Limited | 1-3 | Coal Seam Methane | OCGT | ü |  |  |  |  | Pub An | 495 | S | TBA
Coopers Gap | Coopers Gap Wind Farm Pty Ltd | 115 | Wind | Wind - Onshore | [5 empty] | Pub An | 350 | SS | TBA
Crediton | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 40-90 | SS | TBA
Crows Nest | AGL Energy | 1-67 | Wind | Wind - Onshore | [5 empty] | Pub An | 200 | SS | TBA
Darling Downs 2 | Origin Energy | 1-4 | Natural Gas Pipeline | OCGT | ü |  |  |  |  | Pub An | 500 | S | TBA
Forsayth Wind Farm | Infigen Energy | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | TBA | SS | TBA
High Road | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 34 | SS | 2016-04-01
Kennedy Wind Farm | Windlab Developments | 1-250 | Wind | Wind - Onshore | [5 empty] | Pub An | 600 | SS | TBA
Kogan Creek Solar Boost | CS Energy | 1 | Solar | Solar Thermal | ü | ü | ü | ü | ü | Com | 44 | S | 2014-01-01
Mt Cotton Biomass Cogeneration Power Station | Darwalla Milling Co Pty Ltd | 1 | Wood Waste | Steam Sub Critical | ü |  |  |  |  | Pub An | 7.6 | S | TBA
Mt Emerald | Ratch Australia | Units 1-75 | Wind | Wind - Onshore | [5 empty] | Pub An | 225 | SS | 2017-03-31
Mungi Generation project | Harcourt Generation | 1 | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 60 | S | TBA
North Qld Bio-Energy Plant | Nth. Qld. Bio-Energy Corporation Ltd | 1-3 | Bagasse | Steam Sub Critical | ü |  |  |  |  | Pub An | 100 | S | 2016-07-01
Westlink Power Project | Westlink Pty Ltd as trustee for Westlink Industrial Trust | 1-2 | Natural Gas Pipeline | OCGT | ü |  |  |  |  | Pub An | Up to 1000 developed over three stages | S | 2016-06-30
|  | 3-4 | Natural Gas Pipeline | OCGT | ü |  |  |  |  | Pub An | Up to 1000 developed over three stages | S | 2018-06-30
|  | 5-6 | Natural Gas Pipeline | OCGT | ü |  |  |  |  | Pub An | Up to 1000 developed over three stages | S | 2020-06-30
Windy Hill II | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 30 | NS | 2018-09-01
a. Where the proponent has provided a range of nameplate capacities, the upper bound has been used in any total calculations

## Existing NS Generation
Existing non-scheduled generation – Queensland
Power Station | Owner | Fuel Type | Technology Type | Nameplate Capacity (MW)
Browns Plains | EDL LFG Qld Pty Ltd | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 2.18
Callide A | Oxyfuel Technologies Pty Ltd | Black Coal | Steam Sub Critical | 30
Daandine | Energy infrastructure Investments Pty Ltd | Coal Seam Methane | Compression Reciprocating Engine | 30
FPC Green Energya | FPC 30 Limited as Trustee for FPC Green Fund Trust | Green and air dried wood | Steam Sub Critical | 30
Fraser Coast Community Solar Farm | Ingenero | Solar | PV panels | 0.401
German Creek | EDL CSM Qld Pty Ltd | Waste Coal Mine Gas | Spark Ignition Reciprocating Engine | 45
Inkerman Mill | Pioneer Sugar Mills P/L | Bagasse | Steam Sub Critical | 10.5
Invicta Mill | The Haughton Sugar Company P/L | Bagasse | Steam Sub Critical | 50.3
ISIS Central Sugar Mill Co-generation Plant | AGL Energy | Bagasse | Steam Sub Critical | 25
Kalamia Mill | Sucrogen Kalamia P/L | Bagasse | Steam Sub Critical | 9
Kareeya 5 | Stanwell Corporation Limited | Water | Hydro - Gravity | 7
KRC Cogeneration Plant | AGL | Natural Gas Pipeline | Steam Sub Critical | 5
Macknade Mill | Sucrogen Herbert P/L | Bagasse | Steam Sub Critical | 8
Maryborough | MSF Sugar | Bagasse | Steam Super Critical | 7.5
Moranbah Generation Project | AGL | Waste Coal Mine Gas | Compression Reciprocating Engine | 12.56
Moranbah North | EDL Projects Australia Pty Ltd | Waste Coal Mine Gas | Spark Ignition Reciprocating Engine | 45.6
Mulgrave | MSF Sugar | Bagasse | Steam Super Critical | 13
Oaky Creek | Envirogen Oaky Pty Ltd | Waste Coal Mine Gas | Compression Reciprocating Engine | 20.518
Pioneer Sugar Mill | Pioneer Sugar Mills P/L | Bagasse | Steam Sub Critical | 67.8
Plane Creek Mill | Sucrogen Plane Creek Mill P/L | Bagasse | Steam Sub Critical | 14
Proserpine | Sucrogen Proserpine Pty Ltd | Bagasse | Steam Sub Critical | 17
Racecourse Mill | Mackay Sugar Ltd | Bagasse | Steam Sub Critical | 48
Rochedale Renewable Energy Facility | LMS Generation | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 4.158
Roghan Road | EDL LFG Qld Pty Ltd | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 1.2
South Johnstone | MSF Sugar | Bagasse | Steam Sub Critical | 19.3
Southbank Institute of Technology Unit 1 Plant | Southbank Institute of Technology | Diesel | Compression Reciprocating Engine | 1
Stapylton Green Energy | Stapylton Green Energy | Biomass recycled municipal and industrial material | Steam Sub Critical | 4.8
Suncoast Gold Macadamias | AGL | Macadamia Nut Shells | Steam Sub Critical | 0
Tableland | MSF Sugar | Bagasse | Steam Super Critical | 7
Tarong GT | Stanwell Corporation Limited | Fuel Oil | OCGT | 15
Ti Tree Bioenergy | Ti Tree Bioenergy | Landfill Methane / Landfill Gas | Compression Reciprocating Engine | 3.3
Victoria Mill | Sucrogen Herbert P/L | Bagasse | Steam Sub Critical | 24
Whitwood Road | LMS Generation | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 1.123
Windy Hill | Ratch Australia | Wind | Wind - Onshore | 12
Wivenhoe Small Hydro | Stanwell Corporation Limited | Water | Hydro - Gravity | 4.5
Yarwun | RTA Yarwun Pty Ltd | Natural Gas Pipeline | CCGT | 154
Total |  |  |  | 749.74
a. Formerly known as Rocky Point.

## Disclaimer
Important Notice
Purpose
The purpose of this publication is to provide technical, market data and information regarding opportunities in the National Electricity Market.
AEMO publishes the Electricity Statement of Opportunities in accordance with clause 3.13.3(q) of the National Electricity Rules (Rules). This publication has been prepared by AEMO using information available at 31 July 2013, unless otherwise specified. Information made available after 31 July 2013 may have been included in this publication where practical.
Disclaimer
AEMO has made every effort to ensure the quality of the information in this publication but cannot guarantee that information, forecasts and assumptions are accurate, complete or appropriate for your circumstances. This publication does not include all of the information that an investor, participant or potential participant in the National Electricity Market might require, and does not amount to a recommendation of any investment.
Anyone proposing to use the information in this publication (including information and reports from third parties) should independently verify and check its accuracy, completeness and suitability for purpose, and obtain independent and specific advice from appropriate experts.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this publication:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this publication; and
· are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information or other matters contained in or derived from this publication, or any omissions from it, or in respect of a person’s use of the information in this publication.
Acknowledgement
AEMO acknowledges the support, co-operation and contribution of all participants in providing data and information used in this publication.
Copyright
© 2013 Australian Energy Market Operator Limited. The material in this publication may be used in accordance with the copyright permissions on AEMO’s website.