## Introduction
Victorian Declared Shared Network rating and loading information
This workbook presents declared shared network (DSN) rating1 and loading information at the time of the snapshots presented in Chapter 2 of the 2020 Victorian Annual Planning Report (VAPR).
The "Maximum demand 1" worksheet presents the continuous and short-term line and transformer ratings, as well as (N) and (N-1) loadings at the time of the maximum demand snapshot.
The "Maximum demand 2" worksheet presents a summary of the reactive power adequacy, as well as Interconnector power flows and limits at the time of the maximum demand snapshot.
The "High export to NSW 1" worksheet presents the continuous and short-term line and transformer ratings, as well as (N) and (N-1) loadings at the time of the high power flow from Victoria to NSW snapshot. Only Northern Corridor elements are shown for this snapshot as this is the only region where DSN elements tend to be more heavily loaded during high export from Victoria, rather than during high Victorian demand.
The "High export to NSW 2" worksheet presents a summary of the reactive power adequacy, as well as Interconnector power flows and limits at the time of the high power flow from Victoria to NSW snapshot.
The (N) loading for an asset presents its % loading under system normal condition, based on the asset’s continuous rating.
The (N-1) loading of an asset presents its % loading following the worst single credible contingency, based on the asset’s short term rating. The reported short-term ratings for transmission lines represent the 15 minute ratings.
Rating types are shown in the tables as “D” (dynamic rating), “D/W” (dynamic rating with wind monitoring), and “S” (static rating).
Dynamic ratings (D) are used in real time by AEMO system operators, calculated by taking into account the ambient temperature and a solar heating factor calculation based on the date and time. For lines equipped with wind monitoring facilities (D/W), the calculation of dynamic ratings also takes into account the actual wind speed, otherwise a standard wind speed of 0.6 m/s is assumed.
The rating for equipment with static ratings (S) is based on ambient temperatures that assume a wind speed of 0.6 m/s. Short-term ratings are not available for some lines with static ratings, in which case, the short-term rating is equal to the continuous rating.
[1] AEMO. AEMO transmission equipment ratings. Available at https://www.aemo.com.au/energy-systems/electricity/national-electricity-market-nem/data-nem/network-data/transmission-equipment-ratings

## Maximum demand 1
Table 1 — Maximum demand snapshot: DSN continuous and short-term ratings and loadings
Region | Voltage | Lines/transformers | Continuous rating (N) (MVA) | Continuous loading (N) (MVA) | Short–term rating (N–1) (MVA) | Short-term loading (N-1) (MVA) | Rating type | (N) loading | (N–1) loading
Eastern Corridor | 500 kV | Hazelwood 500kV - Loy Yang 500kV 1 | 3182.4089 | 1167.5612 | 3693.928 | 1750.5081 | D | 36.69% | 47.39%
|  | Hazelwood 500kV - Loy Yang 500kV 2 | 3195.3569 | 1151.8602 | 3370.0759 | 1738.8086 | D | 36.05% | 51.6%
|  | Hazelwood 500kV - Loy Yang 500kV 3 | 3201.4641 | 1136.5731 | 3318.1809 | 1715.7285 | D | 35.5% | 51.71%
|  | Hazelwood 500kV - South Morang 500kV 1 | 2529 | 886.8617 | 2529 | 1228.4294 | S | 35.07% | 48.57%
|  | Hazelwood 500kV - South Morang 500kV 2 | 2529 | 887.4134 | 2529 | 1228.897 | S | 35.09% | 48.59%
|  | Hazelwood 500kV - Rowville 500kV 1 | 3097 | 1007.7909 | 3097 | 1496.092 | S | 32.54% | 48.31%
|  | Cranbourne 500kV - Hazelwood 500kV 1 | 3097 | 1111.3926 | 3097 | 1558.8931 | S | 35.89% | 50.34%
| 220 kV | Rowville 220kV - Yallourn 220kV 1 | 292.18 | 148.9005 | 355.516 | 221.3498 | D/W | 50.96% | 62.26%
|  | Rowville 220kV - Yallourn 220kV 2 | 291.806 | 183.8834 | 343.577 | 233.5038 | D/W | 63.02% | 67.96%
|  | Rowville 220kV - Yallourn 220kV 3 | 291.828 | 187.5957 | 341.737 | 238.2071 | D/W | 64.28% | 69.7%
|  | Rowville 220kV - Yallourn 220kV 4 | 291.762 | 187.5957 | 341.367 | 238.2071 | D/W | 64.3% | 69.78%
|  | Hazelwood 220kV - Yallourn 220kV 1 | 398.783 | 230.9655 | 398.783 | 291.9225 | D | 57.92% | 73.2%
|  | Hazelwood 220kV - Yallourn 220kV 2 | 413.355 | 342.7041 | 450.179 | 344.5138 | D | 82.91% | 76.53%
|  | Hazelwood 220kV - Rowville 220kV 1 | 297.907 | 115.4225 | 368.733 | 149.6972 | D | 38.74% | 40.6%
|  | Hazelwood 220kV - Rowville 220kV 2 | 297.05 | 115.5431 | 368.883 | 149.8081 | D | 38.9% | 40.61%
|  | Morwell 220kV 1 - Hazelwood PS 220kV 1 | 234 | 104.2933 | 294 | 163.8501 | S | 44.57% | 55.73%
|  | Jeeralang 220kV - Morwell 220kV 1 | 349 | 108.4121 | 349 | 154.3924 | S | 31.06% | 44.24%
|  | Jeeralang 220kV - Morwell 220kV 2 | 349 | 99.1326 | 349 | 160.9346 | S | 28.4% | 46.11%
|  | Hazelwood 220kV - Jeeralang 220kV 1 | 745.222 | 76.5537 | 745.222 | 148.0518 | D | 10.27% | 19.87%
|  | Hazelwood 220kV - Jeeralang 220kV 2 | 746.513 | 74.8656 | 746.513 | 147.9038 | D | 10.03% | 19.81%
|  | Hazelwood 220kV - Jeeralang 220kV 3 | 412.549 | 27.0294 | 549.225 | 97.818 | D | 6.552% | 17.81%
|  | Hazelwood 220kV - Jeeralang 220kV 4 | 404.156 | 27.0294 | 404.156 | 97.818 | D | 6.688% | 24.2%
| 500/220 kV | Rowville 500/220kV A1 Transformer | 1000 | 810.998 | 1500 | 952.13 | S | 81.1% | 63.48%
|  | Rowville 500/220kV A2 Transformer | 1000 | 648.4836 | 1500 | 976.8751 | S | 64.85% | 65.13%
|  | Hazelwood 500/220kV A1 Transformer1 | 600 | 0 | 638 | 0 | S | N/A | N/A
|  | Hazelwood 500/220kV A2 Transformer | 600 | 153.1659 | 638 | 225.6993 | S | 25.53% | 35.38%
|  | Hazelwood 500/220kV A3 Transformer | 600 | 157.0966 | 638 | 234.9605 | S | 26.18% | 36.83%
|  | Hazelwood 500/220kV A4 Transformer | 600 | 156.535 | 638 | 234.5396 | S | 26.09% | 36.76%
South–West Corridor | 500 kV | Heywood 500kV - Tarrone 500kV 1 | 2771 | 76.9211 | 2771 | 79.5511 | S | 2.776% | 2.871%
|  | Moorabool 500kV - Tarrone 500kV 12 | 3248 | 0 | 3248 | 0 | S | N/A | N/A
|  | Moorabool 500kV - Mortlake 500kV 13 | 2598 | 0 | 2598 | 0 | S | N/A | N/A
|  | Mortlake 500kV - Heywood 500kV 1 | 2771 | 268.4038 | 2771 | 275.903 | S | 9.686% | 9.957%
|  | Heywood 500kV - Portland Al 500kV 1 | 1386 | 228.184 | 1386 | 377.2033 | S | 16.46% | 27.22%
|  | Heywood 500kV - Portland Al 500kV 2 | 1386 | 226.849 | 1386 | 377.1931 | S | 16.37% | 27.21%
| 275 kV | Heywood 275kV - South East 275kV 1 | 597 | 58.7653 | 701 | 119.0256 | D | 9.843% | 16.98%
|  | Heywood 275kV - South East 275kV 2 | 597 | 58.7653 | 701 | 119.0256 | D | 9.843% | 16.98%
| 500/275 kV | Heywood 500/275 kV M3 Transformer | 370 | 37.4158 | 525 | 77.8662 | S | 10.11% | 14.83%
Northern Corridor | 330 kV | Dederang 330kV - Wodonga 330kV 1 | 918.802 | 236.8367 | 918.802 | 396.7727 | S | 25.78% | 43.18%
|  | Dederang 330kV - Murray 330kV 1 | 1088.528 | 617.013 | 1241.8051 | 1061.9777 | D | 56.68% | 85.52%
|  | Dederang 330kV - Murray 330kV 2 | 1087.277 | 610.692 | 1245.629 | 1060.5265 | D | 56.17% | 85.14%
|  | Dederang 330kV - South Morang 330kV 1 | 873.175 | 487.6053 | 994.048 | 870.247 | D | 55.84% | 87.55%
|  | Dederang 330kV - South Morang 330kV 2 | 873.427 | 486.2473 | 992.033 | 869.511 | D | 55.67% | 87.65%
| 220 kV | Dederang 220kV - Mount Beauty 220kV 1 | 257.133 | 58.3371 | 313.484 | 221.1995 | D | 22.69% | 70.56%
|  | Dederang 220kV - Mount Beauty 220kV 2 | 257.511 | 58.3371 | 314.379 | 221.1995 | D | 22.65% | 70.36%
|  | Dartmouth 220kV - Mount Beauty 220kV 1 | 230 | 118.4037 | 230 | 119.4684 | D | 51.48% | 51.94%
|  | Bogong 220kV - Mount Beauty 220kV 1 | 318.285 | 238.4387 | 348.145 | 238.9454 | D | 74.91% | 68.63%
|  | Mount Beauty 220kV - West Kiewa 220kV 1 | 97 | 45.0128 | 97 | 45.1668 | S | 46.4% | 46.56%
|  | Eildon 220kV - Thomastown 220kV 1 | 487.268 | 339.3963 | 547.088 | 428.8425 | D | 69.65% | 78.39%
|  | Eildon 220kV - Mount Beauty 220kV 1 | 252.226 | 134.6598 | 295.004 | 195.2768 | D | 53.39% | 66.19%
|  | Eildon 220kV - Mount Beauty 220kV 2 | 251.397 | 134.6598 | 293.531 | 195.2768 | D | 53.56% | 66.53%
| 330/220 kV | Dederang 330/220kV H1 Transformer | 340 | 146.3493 | 400 | 215.5276 | S | 43.04% | 53.88%
|  | Dederang 330/220kV H2 Transformer | 340 | 130.1149 | 400 | 194.5582 | S | 38.27% | 48.64%
|  | Dederang 330/220kV H3 Transformer | 240 | 123.7331 | 400 | 185.0156 | S | 51.56% | 46.25%
Greater Melbourne and Geelong | 500 kV | Moorabool 500kV - Sydenham 500kV 1 | 2445 | 317.7331 | 2445 | 565.5737 | S | 13% | 23.13%
|  | Moorabool 500kV - Sydenham 500kV 2 | 2445 | 317.7397 | 2445 | 565.5831 | S | 13% | 23.13%
|  | Keilor 500kV - Sydenham 500kV 1 | 1949 | 354.1924 | 1949 | 1022.8732 | S | 18.17% | 52.48%
|  | Keilor 500kV - South Morang 500kV 1 | 2598 | 793.3611 | 2598 | 1057.2703 | S | 30.54% | 40.7%
|  | South Morang 500kV - Sydenham 500kV 1 | 2598 | 460.3593 | 2598 | 814.2349 | S | 17.72% | 31.34%
|  | South Morang 500kV - Sydenham 500kV 2 | 2651 | 453.3049 | 2651 | 801.5609 | S | 17.1% | 30.24%
|  | Rowville 500kV - South Morang 500kV 1 | 3097 | 88.2367 | 3097 | 530.3175 | S | 2.849% | 17.12%
|  | Cranbourne 500kV - Rowville 500kV 1 | 2771 | 420.8715 | 2771 | 1005.1574 | S | 15.19% | 36.27%
| 220 kV | Geelong 220kV - Moorabool 220kV 1 | 845.556 | 286.4826 | 845.556 | 546.06 | D | 33.88% | 64.58%
|  | Geelong 220kV - Moorabool 220kV 2 | 874.383 | 286.4826 | 874.383 | 546.06 | D | 32.76% | 62.45%
|  | Geelong 220kV - Keilor 220kV 1 | 261.916 | 39.9845 | 321.888 | 78.6799 | D/W | 15.27% | 24.44%
|  | Geelong 220kV - Deer Park 220kV 2 | 262.693 | 93.9912 | 318.998 | 234.0184 | D/W | 35.78% | 73.36%
|  | Deer Park 220kV - Keilor 220kV 2 | 262.801 | 133.2759 | 305.382 | 226.7536 | D/W | 50.71% | 74.25%
|  | Geelong 220kV - Keilor 220kV 3 | 263.571 | 40.0113 | 323.948 | 78.7374 | D/W | 15.18% | 24.31%
|  | Altona 220kV - Keilor 220kV 1 | 720 | 95.8927 | 876 | 172.4539 | D | 13.32% | 19.69%
|  | Brooklyn 220kV - Keilor 220kV 1 | 818.489 | 106.4992 | 818.489 | 190.5661 | D | 13.01% | 23.28%
|  | Altona 220kV - Brooklyn 220kV 1 | 720 | 151.6505 | 792 | 201.6497 | D | 21.06% | 25.46%
|  | Brooklyn 220kV - Newport 220kV 1 | 815.601 | 35.2178 | 815.601 | 439.7865 | D | 4.318% | 53.92%
|  | Brooklyn 220kV - Fishermans Bend 220kV 1 | 813.466 | 5.0982 | 813.466 | 174.9679 | D | 0.6267% | 21.51%
|  | Fishermans Bend 220kV - Newport 220kV 1 | 815.372 | 405.13 | 815.372 | 458.4126 | D | 49.69% | 56.22%
|  | Fishermans Bend 220kV - West Melbourne 220kV 1 | 349 | 91.6352 | 420 | 178.7352 | D | 26.26% | 42.56%
|  | Fishermans Bend 220kV - West Melbourne 220kV 2 | 349 | 91.6352 | 420 | 178.7352 | D | 26.26% | 42.56%
|  | Keilor 220kV - West Melbourne 220kV 1 | 799.292 | 80.9302 | 813.257 | 253.0158 | D | 10.13% | 31.11%
|  | Keilor 220kV - West Melbourne 220kV 2 | 776.297 | 80.6538 | 776.297 | 252.1514 | D | 10.39% | 32.48%
|  | Keilor 220kV - Thomastown 220kV 1 | 462 | 144.1802 | 478 | 378.9716 | S | 31.21% | 79.28%
|  | Keilor 220kV - Thomastown 220kV 2 | 925 | 98.293 | 1143 | 238.1997 | S | 10.63% | 20.84%
|  | South Morang 220kV - Thomastown 220kV 1 | 549 | 376.8149 | 604 | 532.6288 | S | 68.64% | 88.18%
|  | South Morang 220kV - Thomastown 220kV 2 | 549 | 400.2633 | 604 | 508.5154 | S | 72.91% | 84.19%
|  | Brunswick 220kV - Thomastown 220kV 1 | 619.666 | 171.4995 | 741.409 | 312.3853 | D | 27.68% | 42.13%
|  | Brunswick 220kV - Thomastown 220kV 2 | 795.005 | 360.5237 | 808.895 | 509.5853 | D | 45.35% | 63%
|  | Ringwood 220kV - Thomastown 220kV 1 | 728.402 | 307.8547 | 883.355 | 639.0319 | D | 42.26% | 72.34%
|  | Templestowe 220kV - Thomastown 220kV 1 | 703.764 | 228.6531 | 815.287 | 554.2437 | D | 32.49% | 67.98%
|  | Rowville 220kV - Templestowe 220kV 1 | 836.378 | 150.601 | 836.378 | 356.6132 | D | 18.01% | 42.64%
|  | Rowville 220kV - Thomastown 220kV 1 | 550 | 53.2583 | 605 | 102.6634 | D | 9.683% | 16.97%
|  | Rowville 220kV - Ringwood 220kV 1 | 851.107 | 291.1885 | 877.05 | 580.1305 | D | 34.21% | 66.15%
|  | Malvern 220kV - Rowville 220kV 1 | 403.718 | 122.1612 | 435.036 | 247.2841 | D | 30.26% | 56.84%
|  | Malvern 220kV - Rowville 220kV 2 | 403.397 | 122.1688 | 434.691 | 247.281 | D | 30.29% | 56.89%
|  | Rowville 220kV - Springvale 220kV 1 | 751 | 365.6642 | 898 | 733.9529 | D/W | 48.69% | 81.73%
|  | Rowville 220kV - Springvale 220kV 2 | 751 | 365.6642 | 898 | 733.8458 | D/W | 48.69% | 81.72%
|  | Rowville 220kV - Richmond 220kV 1 | 641.968 | 232.9294 | 666.059 | 359.2639 | D | 36.28% | 53.94%
|  | Rowville 220kV - Richmond 220kV 2 | 638.05 | 231.4424 | 661.994 | 358.2521 | D | 36.27% | 54.12%
|  | Heatherton 220kV - Springvale 220kV 1 | 405.649 | 170.9821 | 431.96 | 342.2769 | D | 42.15% | 79.24%
|  | Heatherton 220kV - Springvale 220kV 2 | 409.508 | 170.9821 | 436.069 | 342.2769 | D | 41.75% | 78.49%
|  | East Rowville 220kV - Rowville 220kV 1 | 820.113 | 252.2279 | 873.306 | 591.6964 | D | 30.76% | 67.75%
|  | East Rowville 220kV - Rowville 220kV 2 | 818.915 | 252.2279 | 872.031 | 591.6964 | D | 30.8% | 67.85%
|  | Cranbourne 220kV - East Rowville 220kV 1 | 799.725 | 121.4038 | 799.725 | 385.9172 | D | 15.18% | 48.26%
|  | Cranbourne 220kV - East Rowville 220kV 2 | 800.387 | 121.4038 | 800.387 | 385.9172 | D | 15.17% | 48.22%
|  | Cranbourne 220kV - Tyabb 220kV 1 | 538.018 | 128.0349 | 538.018 | 257.5931 | D | 23.8% | 47.88%
|  | Cranbourne 220kV - Tyabb 220kV 2 | 537.549 | 128.0349 | 537.549 | 257.5931 | D | 23.82% | 47.92%
|  | John Lysaght 220kV - Tyabb 220kV 1 | 183 | 7.8543 | 183 | 15.7195 | S | 4.292% | 8.59%
|  | John Lysaght 220kV - Tyabb 220kV 2 | 183 | 7.8543 | 183 | 15.7195 | S | 4.292% | 8.59%
|  | Brunswick 220kV - Richmond 220kV 1 | 450 | 173.2926 | 650 | 318.1441 | S | 38.51% | 48.95%
| 500/220 kV | Keilor 500/220kV A2 Transformer | 750 | 364.353 | 810 | 508.3896 | S | 48.58% | 62.76%
|  | Keilor 500/220kV A3 Transformer | 750 | 380.5051 | 810 | 509.3964 | S | 50.73% | 62.89%
|  | Keilor 500/220kV A4 Transformer | 750 | 366.1761 | 810 | 509.9297 | S | 48.82% | 62.95%
|  | Cranbourne 500/220kV A1 Transformer | 1000 | 694.6034 | 1500 | 948.9334 | S | 69.46% | 63.26%
| 500/330 kV | South Morang 500/330kV F2 Transformer | 1000 | 283.1656 | 1200 | 495.6749 | S | 28.32% | 41.31%
| 330/220 kV | South Morang 330/220kV H1 Transformer | 700 | 519.6984 | 850 | 707.2711 | S | 74.24% | 83.21%
|  | South Morang 330/220kV H2 Transformer4 | 700 | N/A | 850 | N/A | S | N/A | N/A
|  | South Morang 330/220kV H3 Transformer | 700 | 505.6348 | 1000 | 689.4276 | S | 72.23% | 68.94%
Regional Victoria | 220 kV | Buronga 220kV - Red Cliffs 220kV 1 | 292 | 114.9716 | 292 | 164.136 | S | 39.37% | 56.21%
|  | Horsham 220kV - Murra Warra 220kV 1 | 534.989 | 55.3115 | 669.229 | 97.0176 | D | 10.34% | 14.5%
|  | Kiamal 220kV - Murra Warra 220kV 1 | 450 | 28.6884 | 499 | 74.1878 | D | 6.375% | 14.87%
|  | Kiamal 220kV - Red Cliffs 220kV 1 | 444 | 42.8507 | 444 | 73.3587 | D | 9.651% | 16.52%
|  | Red Cliffs 220kV - Wemen 220kV 1 | 225.024 | 94.8777 | 244.087 | 116.5196 | D | 42.16% | 47.74%
|  | Kerang 220kV - Wemen 220kV 1 | 228.097 | 75.4733 | 249.2 | 98.4565 | D | 33.09% | 39.51%
|  | Ballarat 220kV - Waubra 220kV 1 | 484.793 | 174.9235 | 484.793 | 214.1924 | D | 36.08% | 44.18%
|  | Ararat 220kV - Waubra 220kV 1 | 621.574 | 165.2863 | 783.177 | 204.3839 | D | 26.59% | 26.1%
|  | Ararat 220kV - Crowlands 220kV 1 | 623.912 | 51.2785 | 798.947 | 85.3376 | D | 8.219% | 10.68%
|  | Bulgana 220kV - Horsham 220kV 1 | 625.228 | 14.1231 | 708.074 | 78.5396 | D | 2.259% | 11.09%
|  | Bulgana 220kV - Crowlands 220kV 1 | 624.82 | 20.5019 | 715.562 | 77.617 | D | 3.281% | 10.85%
|  | Bendigo 220kV - Kerang 220kV 1 | 305.112 | 28.3657 | 305.112 | 53.665 | D | 9.297% | 17.59%
|  | Ballarat 220kV - Bendigo 220kV 1 | 398.177 | 76.5071 | 434.842 | 178.7414 | D | 19.21% | 41.1%
|  | Ballarat 220kV - Terang 220kV 1 | 373.394 | 34.873 | 434.183 | 60.0572 | D | 9.339% | 13.83%
|  | Ballarat 220kV - Moorabool 220kV 1 | 294.791 | 14.4607 | 364.112 | 45.9089 | D/W | 4.905% | 12.61%
|  | Ballarat 220kV - Moorabool 220kV 2 | 497.783 | 19.008 | 559.835 | 60.5456 | D/W | 3.819% | 10.81%
|  | Ballarat 220kV - Elaine 220kV 1 | 469.176 | 51.6003 | 524.652 | 99.2601 | D/W | 11% | 18.92%
|  | Elaine 220kV - Moorabool 220kV 1 | 468.149 | 34.6582 | 524.098 | 47.2544 | D/W | 7.403% | 9.016%
|  | Moorabool 220kV - Terang 220kV | 358.134 | 26.7276 | 429.631 | 52.4409 | D | 7.463% | 12.21%
|  | Bendigo 220kV - Fosterville 220kV 1 | 354.385 | 129.5623 | 428.659 | 180.3567 | D/W | 36.56% | 42.07%
|  | Fosterville 220kV - Shepparton 220kV 1 | 354.385 | 147.062 | 428.659 | 199.0032 | D/W | 41.5% | 46.42%
|  | Glenrowan 220kV - Shepparton 220kV 1 | 453.253 | 133.3449 | 486.92 | 226.4963 | D | 29.42% | 46.52%
|  | Glenrowan 220kV - Shepparton 220kV 2 | 452.765 | 133.3449 | 486.396 | 226.4963 | D | 29.45% | 46.57%
|  | Dederang 220kV - Shepparton 220kV 1 | 273.569 | 123.2603 | 325.31 | 162.3302 | D | 45.06% | 49.9%
|  | Dederang 220kV - Glenrowan 220kV 1 | 460.679 | 185.3824 | 481.994 | 307.7317 | D | 40.24% | 63.85%
|  | Dederang 220kV - Glenrowan 220kV 2 | 393 | 185.3824 | 422 | 307.7317 | D | 47.17% | 72.92%
| 500/220 kV | Moorabool 500/220kV A1 Transformer | 1000 | 297.1027 | 1310 | 487.5948 | S | 29.71% | 37.22%
|  | Moorabool 500/220kV A2 Transformer | 1000 | 302.2524 | 1500 | 490.7047 | S | 30.23% | 32.71%
* This is 5 minute short-term rating (N-1) available to the operator.
1 Hazelwood 500/220kV A1 Transformer was out of service at the time of the maximum demand snapshot as its CB has been removed for use elsewhere.
2 Moorabool 500kV - Tarrone 500kV 1 was out of service at the time of the maximum demand snapshot due to a VIC-SA separation event.
3 Moorabool 500kV - Mortlake 500kV 1 was out of service at the time of the maximum demand snapshot due to a VIC-SA separation event.
4 South Morang 330/220kV H2 Transformer is normally out of service under system normal conditions as it is used as a hot spare transformer.

## Maximum demand 2
Table 2 — Maximum demand snapshot: Interconnector power flow and limits
Interconnector | Actual power flow (MW)1 | Limit2 | Limiting constraint equation | Constraint description
Vic–NSW | -314 | 480 MW import limit | V>>V_NIL_3 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback
Vic–SA (Heywood) | -90 | 0 MW import limit | SA_HYSE23 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW
Vic–SA (Murraylink) | -108 | 110 MW import limit | S>NIL_NIL_NWMH2 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback
Tas–Vic (Basslink) | 424 | 424 MW export limit | F_QNV++MG_R60 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS
1 Note that actual interconnector power flows during a five-minute interval might be slightly outside the limits shown in this period of rapidly transitioning interconnection flow and limits. Unless stated otherwise, the 5 minute dispatch targets remained within the limits hence the constraint limit was not deemed to be violated.
2 This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. The actual interconnector power flows during a five-minute interval might be outside the limits shown; these limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.
3 SA and part of the VIC network was separated following the loss of the Moorabool 500kV - Tarrone 500kV 1 and Moorabool 500kV - Mortlake 500kV 1 transmission lines. The VIC-SA interconnector lines between Heywood terminal station and South East terminal station remained online.
Table 3 — Maximum demand snapshot: reactive power adequacy
Reactive supply | MVAr | Reactive absorption | MVAr
From generation | 42.7 | Loads | 2165.7
Static VAr compensators | -42.5 | Shunt reactors | 428.7
Synchronous condensers | 0 | Line Losses | 4091.83
Shunt capacitors | 4063.9 | To Inter-regional Transfers | 96
Line charging | 2675.9 | Line Shunt | 0
Total | 6782.5 | Total | 6782.23

## High export to NSW 1
Table 4 — High export to NSW snapshot: DSN continuous and short-term ratings and loadings
Region | Voltage | Lines/transformers | Continuous rating (N) | Continuous loading (N) | Short–term rating (N–1) | Short-term loading (N-1) | Rating type | (N) loading | (N–1) loading
Northern Corridor |  | Dederang 330kV - Wodonga 330kV 1 | 1224.822 | 408.1138 | 1224.822 | 511.5464 | S | 33.32% | 41.76%
|  | Dederang 330kV - Murray 330kV 1 | 1376.0601 | 261.341 | 1378.297 | 443.9114 | D | 18.99% | 32.21%
|  | Dederang 330kV - Murray 330kV 2 | 1373.397 | 259.0725 | 1375.941 | 442.5984 | D | 18.86% | 32.17%
|  | Dederang 330kV - South Morang 330kV 1 | 1155.139 | 443.8852 | 1155.139 | 751.1382 | D | 38.43% | 65.03%
|  | Dederang 330kV - South Morang 330kV 2 | 1156.109 | 442.712 | 1156.109 | 750.5329 | D | 38.29% | 64.92%
| 220 kV | Dederang 220kV - Mount Beauty 220kV 1 | 425.01 | 77.6853 | 522.5 | 141.035 | D | 18.28% | 26.99%
|  | Dederang 220kV - Mount Beauty 220kV 2 | 425.562 | 77.6853 | 470.351 | 141.035 | D | 18.25% | 29.99%
|  | Dartmouth 220kV - Mount Beauty 220kV 1 | 230 | 6.2455 | 230 | 6.622 | D | 2.715% | 2.879%
|  | Bogong 220kV - Mount Beauty 220kV 1 | 457.156 | 2.3821 | 567.163 | 2.5245 | D | 0.5211% | 0.4451%
|  | Mount Beauty 220kV - West Kiewa 220kV 1 | 97 | 40.3832 | 97 | 44.3178 | S | 41.63% | 45.69%
|  | Eildon 220kV - Thomastown 220kV 1 | 808.412 | 162.8095 | 808.412 | 232.0623 | D | 20.14% | 28.71%
|  | Eildon 220kV - Mount Beauty 220kV 1 | 370.587 | 73.0842 | 370.587 | 111.3983 | D | 19.72% | 30.06%
|  | Eildon 220kV - Mount Beauty 220kV 2 | 370.428 | 73.0842 | 370.428 | 111.3983 | D | 19.73% | 30.07%
| 330/220 kV | Dederang 330/220kV H1 Transformer | 340 | 41.6851 | 400 | 75.3235 | S | 12.26% | 18.83%
|  | Dederang 330/220kV H2 Transformer | 340 | 37.0611 | 400 | 66.9679 | S | 10.9% | 16.74%
|  | Dederang 330/220kV H3 Transformer | 250 | 35.2432 | 400 | 63.6833 | S | 14.1% | 15.92%

## High export to NSW 2
Table 5 — High Victorian export snapshot: Interconnector power flow and limits
Interconnector | Actual power flow (MW)1 | Limit2 | Limiting constraint equation | Constraint description
Vic–NSW | 1373 | 1359 MW export limit | V^^N_NIL_1 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines
Vic–SA (Heywood) | -19 | -19 MW import limit | V>>V_NIL_2A_R | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 500kV, feedback
Vic–SA (Murraylink) | -21 | 101 MW import limit | SVML_ROC_80 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink
Tas–Vic (Basslink) | 388 | 383 MW export limit | F_MAIN++NIL_MG_R60 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS
1 Note that actual interconnector power flows during a five-minute interval might be slightly outside the limits shown due to errors in calculating the limits; these limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.
2 This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. The actual interconnector power flows during a five-minute interval might be outside the limits shown; these limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.
Table 6 — High Victorian export snapshot: reactive power adequacy
Reactive supply | MVAr | Reactive absorption | MVAr
From generation | 120.4 | Loads | 523.9
Static VAr compensators | -18 | Shunt reactors | 671.2
Synchronous condensers | 0 | Line Losses | 2521.17
Shunt capacitors | 84.9 | To Inter-regional Transfers | -466
Line charging | 3045 | Line Shunt | 0
Total | 3250.3 | Total | 3250.27