## Introduction
In December 2018, AER made a final determination on a new Transmission Annual Planning Report (TAPR) Guideline, requiring TNSPs to publish specified information on emerging transmission line and terminal station limitations.
The "Summary of Transmission (T) line segment data" spreadsheet provides information on a selected set of transmission lines associated with DSN emerging limitations, based on AEMO’s VAPR and RIT-T reports. As the relevant RIT-Ts are still works in progress, the information provided is subject to changes.
The general criteria for selecting the existing assets to be included in the data reporting for emerging limitations are:
• The assets which are associated with both load and generation driven emerging limitations.
• The preferred option to address the associated emerging limitations have not yet been finalised by AEMO or other relevant TNSPs
In addition to the information on emerging limitations specified in the TAPR guideline, the "Summary of T. Line Segment data" sheet also includes information related to priority, developing and monitored limitations. More information is provided for the priority limitations than for developing and monitored limitations.
The information on priority, developing and monitored limitations includes:
• Line ID
• Constraint Primary Driver
• From location
• To location
• Reference to Asset Rating
• Voltage level
• Preferred investment-Description (if available)
• Preferred investment- Capital cost (if available)
• Preferred investment -cost accuracy

## Summary of T. Line Segment data
VAPR Section Reference | Limitation Type | Victorian Region | Transmission Line ID | Constraint Primary Driver | Location of constraint (start) | Location of constraint (end) | Asset Rating (Load Shed @35°C) | Forecast Demand (note 1) | Voltage Level | Maximum load at risk per year | Energy at risk | Preferred investment - Description (note 4) | Preferred investment - Capital cost (note 4) | Preferred investment - Annual operating cost | Preferred investment — Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MW) | Annual deferral value ($million) | Historic line load trace | Historic line rating | Annual economic cost of constraint | VCR ($/MWh) | Annual constraint duration (note 2) | Constraint duration on peak demand day (note 3)
Sections 3.4.3 and 4.5 and Appendix A2.1 | Monitored | Central North REZ | Dederang - Glenrowan 220 kV | New generation, increased demand and interconnector transfer | 36.454⁰ S 146.992⁰ E | 36.494⁰ S 146.075⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic load shedding and generation runback control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Sections 3.4.3 and 4.5 and Appendix A2.1 | Monitored | Central North REZ | Glenrowan - Shepparton 220 kV | New generation, increased demand and interconnector transfer | 36.494⁰ S 146.075⁰ E | 36.353⁰ S 145.365⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 3.4.3 and 4.5 and Appendix A2.1 | Monitored | Central North REZ | Shepparton - Bendigo 220 kV | New generation, increased demand and interconnector transfer | 36.353⁰ S 145.365⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Section 4.4 and Appendix A2.2 | Developing | Eastern Corridor | Hazelwood – Yallourn 220 kV | High generation output and high temperature | 38.273⁰ S 146.392⁰ E | 38.177⁰ S 146.344⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Construct a new single or double circuit line with one or two circuits strung, or rebuild existing double circuit line at a higher rating. Installation of BESS on the 220 kV network east of this constraint. | Not available. | Not available. |  | Not available.
Appendix A2.2 | Monitored | Eastern Corridor | Hazelwood – Rowville 220 kV | High generation output and high temperature | 38.273⁰ S 146.392⁰ E | 37.928⁰ S 145.226⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Construct a new single or double circuit Hazelwood – Rowville 220 kV line with one or two circuits strung post Yallourn power station retirement. | Not available. | Not available. |  | Not available.
Appendix A2.2 | Monitored | Eastern Corridor | Rowville - Yallourn 220 kV | High generation output and high temperature | 37.928⁰ S 145.226⁰ E | 38.177⁰ S 146.344⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Construct a new single or double circuit Rowville-Yallourn 220 kV line with one or two circuits strung post Yallourn power station retirement.
Section 4.4, 4.5.6, and Appendix A2.2 | Developing (Line outage), Monitored (no line outage) | Eastern Corridor | Hazelwood – Loy Yang 500 kV | Lack of outage window period due to constricted generation secure support across demand range post Yallourn Power Station retirement. | 38.273⁰ S 146.392⁰ E | 38.256⁰ S 146.573⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Construct a new single or double circuit Hazelwood-Loy Yang 500kV line with one or two circuits strung. | Not available. | Not available. |  | Not available.
Appendix A2.3 | Monitored | Ovens Murray REZ | Dederang - Mount Beauty 220 kV | Increased metro Melbourne demand, new generation and increased interconnector transfer | 36.454⁰ S 146.992⁰ E | 36.743⁰ S 147.165⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme and up-rate the conductor temperature of both 220 kV circuits between Dederang and Mount Beauty to 82ºC. | Not available. | Not available. |  | Not available.
Appendix A2.3 | Monitored | Ovens Murray REZ | Mount Beauty - Eildon 220 kV | New generation and increased interconnector transfer | 36.743⁰ S 147.165⁰ E | 37.224⁰ S 145.921⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Mount Beauty and Eildon to 75ºC. Up-rate terminations to match line. | Not available. | Not available. |  | Not available.
Appendix A2.3 | Monitored | Ovens Murray REZ | Eildon - Thomastown 220 kV | Increased interconnector transfer | 37.224⁰ S 145.921⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Eildon and Thomstown to 75ºC. Up-rate terminations to match line. | Not available. | Not available. |  | Not available.
Appendix A2.3 | Monitored | Northern Corridor | Murray - Dederang 330 kV | High generation output or increased interconnector transfer | 36.226⁰ S 148.144⁰ E | 36.454⁰ S 146.992⁰ E | Note 5 | Same as Asset Rating | 330 kV |  |  | Install a new 1,060 MVA 330 kV line to Dederang (or a newly established station nearby)- a third line from Murray, or a second line from Jindera. | Not available. | Not available. |  | Not available.
Section 4.5 and Appendix A2.4 | Monitored | Murray River REZ | Red Cliffs - Wemen 220 kV | New and retired generation, and high temperature | 34.275⁰ S 142.2⁰ E | 34.791⁰ S 142.522⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Replace the existing Bendigo – Kerang – Wemen – Red Cliffs 220 kV line with a new double circuit 220 kV line and provide associated terminal station aumentation. | Not available. | Not available.
Section 4.5 and Appendix A2.4 | Monitored | Murray River REZ | Wemen - Kerang 220 kV | New and retired generation, and high temperature | 34.791⁰ S 142.522⁰ E | 35.782⁰ S 143.945⁰ E | Note 5 | Same as Asset Rating | 220 kV
Section 4.5 and Appendix A2.4 | Monitored | Murray River REZ | Kerang - Bendigo 220 kV | New and retired generation | 35.782⁰ S 143.945⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.4 | Monitored | Murray River REZ | Red Cliffs - Wemen 220 kV | Increased demand | 34.275⁰ S 142.2⁰ E | 34.791⁰ S 142.522⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic load shedding control scheme to enable the use of five minute line rating. Replace the existing Bendigo – Kerang – Wemen – Red Cliffs 220 kV line with a new double circuit 220 kV line and provide associated terminal station aumentation. | Not available. | Not available. |  | Not available.
Appendix A2.4 | Monitored | Murray River REZ | Wemen - Kerang 220 kV | Increased demand | 34.791⁰ S 142.522⁰ E | 35.782⁰ S 143.945⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.4 | Monitored | Murray River REZ | Kerang - Bendigo 220 kV | Increased demand | 35.782⁰ S 143.945⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Heywood 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 |  | 500 kV |  |  | A switched capacitor with individual phase switching at Heywood or near Alcoa Portland. Install phase switched power flow controllers at Heywood or near Alcoa Portland. An SVC or a STATCOM. Additional transposition towers along the Moorabool – Heywood – Alcoa Portland 500 kV line. | Not available. | Not available. |  | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Heywood - Portland 500 kV | New generation | 38.182⁰ S 141.638⁰ E | 38.387⁰ S 141.626⁰ E | Note 5 |  | 500 kV
Section 3.4.3 and Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Mortlake 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.062⁰ S 142.67⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | A new Moorabool – Mortlake/Tarrone – Heywood 500 kV line. Line limiting plant upgrades. Install wind monitoring dynamic line rating scheme. | Not available. | Not available. |  | Not available.
Section 3.4.3 and Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Haunted Gully 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.007⁰ S 143.315⁰ E | Note 5 | Same as Asset Rating | 500 kV
Section 3.4.3 and Appendix A2.5 | Monitored | South West Victoria REZ | Haunted Gully - Tarrone 500 kV | New generation | 38.007⁰ S 143.315⁰ E | 38.179⁰ S 142.181⁰ E | Note 5 | Same as Asset Rating | 500 kV
Section 3.4.3 and Appendix A2.5 | Monitored | South West Victoria REZ | Mortlake - Heywood 500 kV | New generation | 38.062⁰ S 142.67⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 | Same as Asset Rating | 500 kV
Section 3.4.3 and Appendix A2.5 | Monitored | South West Victoria REZ | Tarrone - Heywood 500 kV | New generation | 38.179⁰ S 142.181⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 | Same as Asset Rating | 500 kV
Sections 3.4.3, 4.5, and Appendix A2.5 | Monitored | South West Victoria REZ | Ballarat - Berrybank 220 kV | New generation | 37.567⁰ S 143.921⁰ E | 37.900⁰ S 143.438⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. Replace the existing Ballarat – Berrybank – Terang – Moorabool 220 kV line with a new double circuit 220 kV line. | Not available. | Not available. |  | Not available.
Sections 3.4.3, 4.5, and Appendix A2.5 | Monitored | South West Victoria REZ | Berrybank - Terang 220 kV | New generation | Vic | 38.256⁰ S 142.925⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 3.4.3, 4.5, and Appendix A2.5 | Monitored | South West Victoria REZ | Terang - Moorabool 220 kV | New generation | 38.256⁰ S 142.925⁰ E | 38.037⁰ S 144.296⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Ringwood - Thomastown 220 kV | Increased demand in Eastern Metropolitan Melbourne and/or Latrobe Valley operated in radial configuration after Yallourn Power Station retirement. | 37.821⁰ S 145.216⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut in Rowville – Ringwood – Thomastown 220 kV at Templestowe and Rowville – Templestowe – Thomastown 220 kV at Ringwood to form the Rowville – Ringwood – Templestowe – Thomastown No. 1 and No. 2 circuits plus any fault level mitigation work. New (third) 500/220 kV transformer at Rowville, plus any fault level mitigation works. | Not available. | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Templestowe - Thomastown 220 kV |  | 37.749⁰ S 145.171⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Rowville - Malvern 220 kV | Increased demand or additional loads connected to Malvern Terminal Station. | 37.928⁰ S 145.226⁰ E | 37.878⁰ S 145.084⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut-in Rowville–Richmond 220 kV No.1 and No.4 circuits at Malvern Terminal Station to form the Rowville–Malvern–Richmond No.3 and No.4 circuits. | Not available. | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Rowville - Springvale 220 kV | Increased demand or additional loads connected to Springvale and Heatherton Terminal Station. | 37.928⁰ S 145.226⁰ E | 37.928⁰ S 145.146⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a third Rowville –Springvale circuit (underground cable). Connect a Cranbourne – Heatherton 220 kV double circuit overhead line. | Not available. | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Springvale - Heatherton 220 kV | Increased demand or additional loads connected to Heatherton Terminal Station. | 37.928⁰ S 145.146⁰ E | 37.941⁰ S 145.078⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | South Morang - Thomastown 220 kV | Increased demand around the Melbourne Metropolitan area and/or increased export to New South Wales and/or Latrobe Valley operated in a radial configuration after Yallourn Power Station retirement. Generation planting and retirements as per the 2022 ISP Step Change scenario. | 37.644⁰ S 145.078⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Increase the transfer capability by installing wind monitoring facilities on the South Morang to Thomastown line. Install an automatic load shedding control scheme to enable the use of five-minute line rating. Install a third 500/220 kV transformer at Rowville, plus any fault level mitigation works. | Not available. | Not available. |  | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Moorabool - Geelong 220 kV | High generation in South West Victoria and Western Victoria as well as high demand in Greater Melbourne. | 38.037⁰ S 144.296⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a new double circuit Moorabool – Geelong 220kV line with a rating of approximately 800 MVA per circuit at 35ºC. | Not available. | Not available. |  | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Geelong - Keilor 220 kV |  | 38.083⁰ S 144.339⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Replace the existing Geelong-Keilor 220 kV double circuit line (circuits 1 and 3) with a new double circuit line, each circuit rated at 800 MVA at 35ºC.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Keilor - Deer Park 220 kV | Increased Deer Park demand. | 37.738⁰ S 144.846⁰ E | 37.778⁰ S 144.735⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a load shedding control scheme. Replace the existing Geelong – Keilor No. 1 and No. 3 220 kV lines with a new double circuit line rated at 800 MVA at 35ºC. Parallel the existing three Geelong – Deer Park – Keilor 220 kV circuits to form a Geelong – Deer Park and Deer Park – Keilor circuit, each rated 810 MVA at 35º C. | Not available. | Not available. |  | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Deer Park - Geelong 220 kV |  | 37.778⁰ S 144.735⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Keilor - Thomastown No. 1 220 kV | Latrobe Valley operated in a radial configuration after Yallourn Power Station retirement. | 37.738⁰ S 144.846⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Install an automatic load shedding control scheme to enable the use of five-minute line rating Install a third 500/220 kV transformer at Rowville, plus any fault level mitigation works. | Not available. | Not available. |  | Not available.
Section 3.4.3 and Appendix A2.6 | Monitored | Greater Mel & Geelong | Sydenham - Keilor 500 kV | Increased generation in west and southwest Victoria supplying Keilor Terminal Station. | 37.676⁰ S 144.747⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Line limiting plant upgrades at Sydenham and Keilor terminal stations. Install a new single circuit Sydenham – Keilor 500 kV line with a rating of approximately 2,900 MVA at 35ºC. Uprate line rating of the existing Sydenham – Keilor 500 kV line. | Not available. | Not available. |  | Not available.
Section 3.4.3 and Appendix A2.7 | Monitored | Western Victoria REZ | Red Cliffs - Kiamal 220 kV | Increased generation in Western Victoria and Murray River REZ. | 34.275⁰ S 142.2⁰ E | 35.031⁰ S 142.293⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. Install a new double circuit Bulgana to Murra Warra 220kV line via a new terminal station at Horsham. | Not available. | Not available. |  | Not available.
Section 3.4.3 and Appendix A2.7 | Monitored | Western Victoria REZ | Kiamal - Murra Warra 220 kV | Increased generation in Western Victoria and Murray River REZ. | 35.031⁰ S 142.293⁰ E | 36.433⁰ S 142.318⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 3.4.3 and 4.5 and Appendix A2.7 | Monitored | Western Victoria REZ | Murra Warra - Horsham 220 kV | Increased generation in Western Victoria and Murray River REZ. | 36.433⁰ S 142.318⁰ E | 36.731⁰ S 142.246⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 3.4.3 and 4.5 and Appendix A2.7 | Monitored | Western Victoria REZ | Horsham - Bulgana 220 kV | Increased generation in Western Victoria and Murray River REZ. | 36.731⁰ S 142.246⁰ E | 37.037⁰ S 142.984⁰ E | Note 5 | Same as Asset Rating | 220 kV
Note 1: As those lines are associated with existing constraints, their maximum line loads are expected to be their ratings.
Note 2: The annual constraint duration values are the estimated next available year forecasts based on information from the corresponding RIT-Ts.
Note 3: The constraint duration on peak demand day is based on available estimated forecasts from the corresponding RIT-Ts or historical data if forecasts are unavailable.
Note 4: The investment option with possibly the lowest cost has been provided, as per Appendix A2 of the 2022 VAPR. All DSN augmentation costs are under review, given the recent significant changes in material and labour costs.
Note 5: See asset ratings available on AEMO's website at http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Network-Data/Transmission-Equipment-Ratings

## Summary Sgmt data-2021 unsorted (hidden)
VAPR Section Reference | Limitation Type | Victorian Region | Transmission Line ID | Constraint Primary Driver | Location of constraint (start) | Location of constraint (end) | Asset Rating (Load Shed @35°C) | Forecast Demand (note 1) | Voltage Level | Maximum load at risk per year | Energy at risk | Preferred investment - Description (note 4) | Preferred investment - Capital cost | Preferred investment - Annual operating cost | Preferred investment — Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MW) | Annual deferral value ($million) | Historic line load trace | Historic line rating | Annual economic cost of constraint | VCR ($/MWh) | Annual constraint duration (note 2) | Constraint duration on peak demand day (note 3)
Section 4.4 and Appendix A2.2 | Developing | Eastern Corridor | Hazelwood – Yallourn 220 kV | High generation output and high temperature | 38.273⁰ S 146.392⁰ E | 38.177⁰ S 146.344⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Construct a new single or double circuit line with one or two circuits strung, or rebuild existing double circuit line at a higher rating. | $31,500,000-$37,100,000 | Not available. |  | Not available.
Appendix A2.2 | Monitored | Eastern Corridor | Hazelwood – Rowville 220 kV | High generation output and high temperature | 38.273⁰ S 146.392⁰ E | 37.928⁰ S 145.226⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Upgrade Hazelwood – Rowville 220 kV line prior to Yallourn power station retirement, or construct a new single or double circuit Hazelwood – Rowville 220 kV line with one or two circuits strung post Yallourn power station retirement. | Not available. | Not available. |  | Not available.
Appendix A2.2 | Monitored | Eastern Corridor | Rowville - Yallourn 220 kV | High generation output and high temperature | 37.928⁰ S 145.226⁰ E | 38.177⁰ S 146.344⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Upgrade Rowville-Yallourn 220 kV line prior to Yallourn power station retirement, or construct a new single or double circuit Rowville-Yallourn 220 kV line with one or two circuits strung post Yallourn power station retirement.
Section 4.4 and Appendix A2.2 | Developing (Line outage), Monitored (no line outage) | Eastern Corridor | Hazelwood – Loy Yang 500 kV | Lack of outage window period due to constricted generation secure support across demand range post Yallourn Power Station retirement. | 38.273⁰ S 146.392⁰ E | 38.256⁰ S 146.573⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Construct a new single or double circuit Hazelwood-Loy Yang 500kV line with one or two circuits strung. | Not available. | Not available. |  | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Heywood 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 |  | 500 kV |  |  | A switched capacitor with individual phase switching at Heywood or near Alcoa Portland. | 15300000 | Not available. | ±50% | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Heywood - Portland 500 kV | New generation | 38.182⁰ S 141.638⁰ E | 38.387⁰ S 141.626⁰ E | Note 5 |  | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Mortlake 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.062⁰ S 142.67⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Install a wind monitoring scheme. | Not available. | Not available. |  | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Haunted Gully 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.007⁰ S 143.315⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Haunted Gully - Tarrone 500 kV | New generation | 38.007⁰ S 143.315⁰ E | 38.179⁰ S 142.181⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Mortlake - Heywood 500 kV | New generation | 38.062⁰ S 142.67⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Tarrone - Heywood 500 kV | New generation | 38.179⁰ S 142.181⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 | Same as Asset Rating | 500 kV
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Dederang - Mount Beauty 220 kV | Increased metro Melbourne demand, new generation and increased interconnector transfer | 36.454⁰ S 146.992⁰ E | 36.743⁰ S 147.165⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme and up-rate the conductor temperature of both 220 kV circuits between Dederang and Mount Beauty to 82ºC. | 13300000 | Not available. | ±50% | Not available.
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Mount Beauty - Eildon 220 kV | New generation and increased interconnector transfer | 36.743⁰ S 147.165⁰ E | 37.224⁰ S 145.921⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Mount Beauty and Eildon to 75ºC. Up-rate terminations to match line. | 114900000 | Not available. | ±50% | Not available.
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Eildon - Thomastown 220 kV | Increased interconnector transfer | 37.224⁰ S 145.921⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Eildon and Thomstown to 75ºC. Up-rate terminations to match line. |  | Not available. | ±50% | Not available.
Appendix A2.3 | Monitored | Northern Corridor | Murray - Dederang 330 kV | High generation output or increased interconnector transfer | 36.226⁰ S 148.144⁰ E | 36.454⁰ S 146.992⁰ E | Note 5 | Same as Asset Rating | 330 kV |  |  | Install a new 1,060 MVA 330 kV line to Dederang (or a newly established station nearby)- a third line from Murray, or a second line from Jindera. | Not available. | Not available. |  | Not available.
Section 4.6.2 and Appendix A2.6 | Monitored | Greater Mel & Geelong | Ringwood - Thomastown 220 kV | Increased demand in Eastern Metropolitan Melbourne and/or Latrobe Valley operated in radial configuration after Yallourn Power Station retirement. | 37.821⁰ S 145.216⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut in Rowville – Ringwood – Thomastown 220 kV at Templestowe and Rowville – Templestowe – Thomastown 220 kV at Ringwood to form the Rowville – Ringwood – Templestowe – Thomastown No. 1 and No. 2 circuits. | $15,100,000 plus any fault mitigation costs. | Not available. | ±50% | Not available.
Section 4.6.2 and Appendix A2.6 | Monitored | Greater Mel & Geelong | Templestowe - Thomastown 220 kV |  | 37.749⁰ S 145.171⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Rowville - Malvern 220 kV | Increased demand | 37.928⁰ S 145.226⁰ E | 37.878⁰ S 145.084⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut-in Rowville–Richmond 220 kV No.1 and No.4 circuits at Malvern Terminal Station to form the Rowville–Malvern–Richmond No.3 and No.4 circuits. | 11800000 | Not available. | ±50% | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Rowville - Springvale 220 kV | Increased demand | 37.928⁰ S 145.226⁰ E | 37.928⁰ S 145.146⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a Cranbourne – Heatherton 220 kV double circuit overhead line. | 38000000 | Not available. | ±50% | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Springvale - Heatherton 220 kV | Increased demand | 37.928⁰ S 145.146⁰ E | 37.941⁰ S 145.078⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | South Morang - Thomastown 220 kV | Increased demand around the Melbourne Metropolitan area and/or increased export to New South Wales and/or Latrobe Valley operated in a radial configuration after Yallourn Power Station retirement. | 37.644⁰ S 145.078⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Increase the transfer capability by installing wind monitoring facilities on the South Morang to Thomastown line. | Not available. | Not available. |  | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Moorabool - Geelong 220 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a new double circuit Moorabool – Geelong 220kV line with a rating of approximately 800 MVA per circuit at 35ºC. | $42,700,00 | Not available. | ±50% | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Geelong - Keilor 220 kV | New generation | 38.083⁰ S 144.339⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Replace the existing Geelong-Keilor 220 kV double circuit line (circuits 1 and 3) with a new double circuit line, each circuit rated at 800 MVA at 35ºC. | $190,500,00
Appendix A2.6 | Monitored | Greater Mel & Geelong | Keilor - Deer Park 220 kV | Increased demand | 37.738⁰ S 144.846⁰ E | 37.778⁰ S 144.735⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a load shedding control scheme. | Not available. | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Deer Park - Geelong 220 kV | Increased demand | 37.778⁰ S 144.735⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Keilor - Thomastown No. 1 220 kV | Latrobe Valley operated in a radial configuration after Yallourn Power Station retirement. | 37.738⁰ S 144.846⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. |  | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Sydenham - Keilor 500 kV | New generation | 37.676⁰ S 144.747⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Increase station plant ratings to remove station thermal constraints on line. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Red Cliffs - Kiamal 220 kV | New and retired generation | 34.275⁰ S 142.2⁰ E | 35.031⁰ S 142.293⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not Available | Not available. |  | Not available.
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Kiamal - Murra Warra 220 kV | New and retired generation | 35.031⁰ S 142.293⁰ E | 36.433⁰ S 142.318⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Murra Warra - Horsham 220 kV | New and retired generation | 36.433⁰ S 142.318⁰ E | 36.731⁰ S 142.246⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Horsham - Bulgana 220 kV | New and retired generation | 36.731⁰ S 142.246⁰ E | 37.037⁰ S 142.984⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Red Cliffs - Wemen 220 kV | New and retired generation, and high temperature | 34.275⁰ S 142.2⁰ E | 34.791⁰ S 142.522⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Wemen - Kerang 220 kV | New and retired generation, and high temperature | 34.791⁰ S 142.522⁰ E | 35.782⁰ S 143.945⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Kerang - Bendigo 220 kV | New and retired generation | 35.782⁰ S 143.945⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.4 | Monitored | Murray River REZ | Red Cliffs - Wemen 220 kV | Increased demand | 34.275⁰ S 142.2⁰ E | 34.791⁰ S 142.522⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic load shedding control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Appendix A2.4 | Monitored | Murray River REZ | Wemen - Kerang 220 kV | Increased demand | 34.791⁰ S 142.522⁰ E | 35.782⁰ S 143.945⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.4 | Monitored | Murray River REZ | Kerang - Bendigo 220 kV | Increased demand | 35.782⁰ S 143.945⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.5 | Priority | South West Victoria REZ | Ballarat - Terang 220 kV | New generation | 37.567⁰ S 143.921⁰ E | 38.256⁰ S 142.925⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.3.3 and Appendix A2.5 | Priority | South West Victoria REZ | Terang - Moorabool 220 kV | New generation | 38.256⁰ S 142.925⁰ E | 38.037⁰ S 144.296⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Dederang - Glenrowan 220 kV | New generation, increased demand and interconnector transfer | 36.454⁰ S 146.992⁰ E | 36.494⁰ S 146.075⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic load shedding and generation runback control scheme to enable the use of five minute line rating. | 1500000 | Not available. | ±50% | Not available.
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Glenrowan - Shepparton 220 kV | New generation, increased demand and interconnector transfer | 36.494⁰ S 146.075⁰ E | 36.353⁰ S 145.365⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Shepparton - Bendigo 220 kV | New generation, increased demand and interconnector transfer | 36.353⁰ S 145.365⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Note 1: As those lines are associated with existing constraints, their maximum line loads are expected to be their ratings.
Note 2: The annual constraint duration values are the estimated next available year forecasts based on information from the corresponding RIT-Ts. For West VIC RIT-T constraints, annual constraint duration is based on 2021 forecasts.
Note 3: The constraint duration on peak demand day is based on available estimated forecasts from the corresponding RIT-Ts or historical data if forecasts are unavailable.
Note 4: The investment option with the lowest cost has been provided, as per Appendix A1 of the 2021 VAPR. This investment is indicative only, and the preferred option will be determined as per the required RIT-T assessment.
Note 5: See asset ratings available on AEMO's website at http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Network-Data/Transmission-Equipment-Ratings

## Asset Rating
Transmission line ratings are only provided for lines that VAPR identifies in emerging or priority limitations. The 2022 VAPR identifies no lines in emerging or priority limitations.

## Annual Cost of Constraint
Annunal cost of constraints are only provided for lines that VAPR identifies in emerging or priority limitations. The 2022 VAPR identifies no lines in emerging or priority limitations.

## Historic Line Loadings
Historic line loadings are only provided for lines that VAPR identifies in emerging or priority limitations. The 2022 VAPR identifies no lines in emerging or priority limitations.

## Historic Line Ratings
Historic line ratings are only provided for lines that VAPR identifies in emerging or priority limitations. The 2022 VAPR identifies no lines in emerging or priority limitations.