## Inputs
Base Assumptions
Discount rate | 5.9%
Asset life (years) | 30
O&M | 2%
Sensitivities | Low | High
Cost | 70% | 130%
Discount rate | 3.2% | 8.6%
Reasonable scenarios
Scenario | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change
Central | 50% | 33% | 20% | 50%
Step Change | 25% | 33% | 20% | 0%
Slow Change | 25% | 33% | 20% | 25%
Fast Change | 0% | 0% | 20% | 25%
High DER | 0% | 0% | 20% | 0%
Solution | Name | Year | MVAr | Capital Cost ($M)
Option 1.0 | KTS 220 kV | 2022 | 100 | 6.5
Option 1A | KTS 220 kV | 2022 | 100 | 6.5
| MTS 220 kV | 2023 | 100 | 6.8
Option 1B | KTS 220 kV | 2022 | 100 | 6.5
| MTS 220 kV | 2023 | 100 | 6.8
| MTS 220 kV | 2025 | 100 | 7.5
Option 1C | KTS 220 kV | 2022 | 100 | 6.5
| MTS 220 kV | 2023 | 100 | 6.8
| MTS 220 kV | 2025 | 100 | 7.5
| MTS 220 kV | 2025 | 100 | 7.5
Option 1D | KTS 220 kV | 2022 | 100 | 6.5
| MTS 220 kV | 2023 | 100 | 6.8
| MTS 220 kV | 2025 | 100 | 7.5
| MTS 220 kV | 2025 | 100 | 7.5
| MTS 220 kV | 2025 | 100 | 7.5
Option 2 | KTS 220 kV | 2022 | 100 | 6.5
| MTS 220 kV | 2023 | 100 | 6.8
| MTS 220 kV | 2025 | 100 | 7.5
| SMTS 330 kV SynCon | 2025 | 100 | 69.9
Reactor | Cost | Description | Assumptions | Explanation
MLTS No. 2 220 kV 100 MVAr Reactor - Non-Contestable | $6.8M | Utilise Bay F, existing racks, existing two towers, and existing oil treatment.
MLTS No. 2 220 kV 100 MVAr Reactor - Contestable | $8.6 M | Utilise Bay K, new rack, new tower and new oil treatment, move fence and road way, extend cable trench, bench and dress new areas. |  | Compared to Item 1: Avoids utilising existing AusNet Infrastructure (racks, towers and oil containment/treatment system) by utilising Vacant Bay K, establishing dedicated support structures & oil treatment. Necessitates additional switchyard preparation, road and fence movement.
MLTS No. 3 220 kV 100 MVAr Reactor – Non-Contestable | $7.5M | Utilise Bay K, new rack, use existing A2 Tx tower, existing oil treatment, move fence and road way, extend cable trench, bench and dress new areas | No. 2 Reactor was non contestable and switched in Bay F leaving Bay K for 3rd Reactor
MLTS No. 3 220 kV 100 MVAr Reactor - Contestable | $9.7M | Utilise Bay L, new racks, new tower and new oil treatment, move fence and road way, extend cable trench, bench and dress new areas. | No. 2 Reactor was contestable and switched in Bay K, requiring use of bay L for No. 3 Reactor. | Compared to Item 3: Avoids utilising existing AusNet or Alternative Owner Infrastructure (tower and oil containment/treatment system) by utilising Vacant Bay L, establishing dedicated support structures & oil treatment. Necessitates additional switchyard preparation, road and fence movement.
MLTS No. 2 & 3 220 kV 100 MVAr Reactors – Non Contestable (single project) | $13.9M | Utilise Bays F & K, one new rack, reuse existing racks and towers, reuse existing oil treatment, move fence and roadway. |  | Compared to Items 1 & 3: Savings in reactor specification and design costs, station design, site management and project management costs
MLTS No. 2 & 3 220 kV 100 MVAr Reactors – Contestable (Single Project) | $16.2M | Utilise Bays K & L, new racks, 1 new tower, 1 new oil treatment sys, move roadway & fence once. |  | Compared to Items 2 & 3: Single Movement of road way and fence way, shared use of civil infrastructure (tower and oil treatment).
Compared to Item 5: Additional structures and oil treatment required, larger changes to roadways and fences.
KTS No. 3 220 kV 100 MVAr Reactor – Non Contestable | $6.7M | Utilise Bay M | No tower required. i.e. single span from switchyard rack to reactor rack.
KTS No. 3 220 kV 100 MVAr Reactor - Contestable | $7.2M | Utilise Bay M, add separate oil treatment sys. | No viable alternative to avoid utilising AusNet support structures due to switchyard expansion limitations. | Compared to Item 7: Separate oil treatment facility established. Must use AusNet Rack due to no space to expand switchyard.
Equipment | Cost (P50 Direct)
KTS No. 2 220 kV 100 MVAr Reactor | $6.5 M
MLTS No. 2 220 kV 100 MVAr Reactor | $6.8 M
MLTS No. 3 220 kV 100 MVAr Reactor (double switched) | $9.6 M

## Summary
Cost and net market benefits for base case assumptions (weighting, discount rate and cost)
Option | Capital Cost, $M (2019-20) | Capital + O&M Cost, $M (NPV) | Central - Net Market Benefit $M (NPV) | Step Change - Net Market Benefit $M (NPV) | Slow Change - Net Market Benefit $M (NPV) | Base Weighted - Net market benefit $M (NPV)
1 | 6.5 | 5.5825 | 14.0531 | 122.5197 | 54.3653 | 51.2478
1A | 13.3 | 11.0972 | 14.8634 | 211.6049 | 73.1862 | 78.6295
1B | 20.8 | 16.5208 | 9.761 | 276.1596 | 75.6977 | 92.8448
1C | 28.3 | 21.9444 | 4.3375 | 282.189 | 71.0422 | 90.4765
1D | 35.8 | 27.3679 | -1.0861 | 276.8156 | 65.6186 | 85.0655
2 | 90.7 | 67.0685 | -35.8258 | 279.5066 | 34.2114 | 60.5166
Net market benefits NPV ($M) - base weighting
Option | Base | High Discount Rate | Low Discount Rate | High Cost | Low Cost
1 | 51.2478 | 33.6125 | 81.2001 | 49.5731 | 52.9226
1A | 78.6295 | 50.676 | 126.5394 | 75.3003 | 81.9586
1B | 92.8448 | 58.8207 | 151.862 | 87.8886 | 97.8011
1C | 90.4765 | 56.0946 | 150.5766 | 83.8932 | 97.0598
1D | 85.0655 | 51.4393 | 144.2649 | 76.8551 | 93.2759
2 | 60.5166 | 27.5182 | 121.6146 | 40.3961 | 80.6372
Net market benefits NPV ($M) - Central scenario
Option | Base | High Discount Rate | Low Discount Rate | High Cost | Low Cost
1 | 14.0531 | 8.2569 | 24.053 | 12.3784 | 15.7278
1A | 14.8634 | 7.534 | 27.7849 | 11.5342 | 18.1925
1B | 9.761 | 3.0895 | 21.9498 | 4.8048 | 14.7173
1C | 4.3375 | -1.5737 | 15.6172 | -2.2458 | 10.9208
1D | -1.0861 | -6.2369 | 9.2846 | -9.2965 | 7.1243
2 | -35.8258 | -36.8465 | -29.7089 | -55.9463 | -15.7052
Net market benefits NPV ($M) - Alternative scenario weightings
Option | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change
1 | 51.2478 | 63.0096 | 75.9417 | 42.2495
1A | 78.6295 | 98.886 | 121.4097 | 60.492
1B | 92.8448 | 119.334 | 148.282 | 65.7822
1C | 90.4765 | 117.9977 | 151.292 | 62.7072
1D | 85.0655 | 112.6449 | 145.9146 | 57.2838
2 | 60.5166 | 91.7044 | 117.9235 | 21.5403

## Least Worst Regret
Net market benefits for base case assumptions (discount rate and cost)
Option | Central - Net Market Benefit $M (NPV) | Step Change - Net Market Benefit $M (NPV) | Slow Change - Net Market Benefit $M (NPV) | Fast Change - Net Market Benefit $M (NPV) | High DER - Net Market Benefit $M (NPV)
1 | 14.0531 | 122.5197 | 54.3653 | 86.5265 | 102.2436
1A | 14.8634 | 211.6049 | 73.1862 | 139.055 | 168.3392
1B | 9.761 | 276.1596 | 75.6977 | 167.9092 | 211.8824
1C | 4.3375 | 282.189 | 71.0422 | 171.1115 | 227.7798
1D | -1.0861 | 276.8156 | 65.6186 | 165.6888 | 222.5362
2 | -35.8258 | 279.5066 | 34.2114 | 123.6015 | 188.1238
Regret ($M)
Option | Central - Net Market Benefit $M (NPV) | Step Change - Net Market Benefit $M (NPV) | Slow Change - Net Market Benefit $M (NPV) | Fast Change - Net Market Benefit $M (NPV) | High DER - Net Market Benefit $M (NPV) | Worse regret - 3 ESOO scenarios | Worse -all 5 screnarios
0Z | 0.81027 | 159.6693 | 21.3323 | 84.585 | 125.5362 | 159.6693 | 159.6693
1A | 0 | 70.5841 | 2.5115 | 32.0565 | 59.4406 | 70.5841 | 70.5841
1B | 5.1023 | 6.0294 | 0 | 3.2023 | 15.8975 | 6.0294 | 15.8975
1C | 10.5259 | 0 | 4.6555 | 0 | 0 | 10.5259 | 10.5259
1D | 15.9495 | 5.3734 | 10.079 | 5.4227 | 5.2436 | 15.9495 | 15.9495
2 | 50.6891 | 2.6824 | 41.4863 | 47.5101 | 39.656 | 50.6891 | 50.6891

## Option 1.0
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M |  | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change |  | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change
Base | 5.9% | 100% | 6.5 | 5.5825 | 14.0531 | 122.5197 | 54.3653 | 86.5265 | 102.2436 | 51.2478 | 63.0096 | 75.9417 | 42.2495 |  | 19.6356 | 128.1022 | 59.9478 | 92.109 | 107.8261 | 56.8303 | 68.5362 | 81.5241 | 47.832
High Discount rate | 8.6% | 100% | 6.5 | 5.1764 | 8.2569 | 82.2602 | 35.676 | 58.1909 | 66.8991 | 33.6125 | 41.6437 | 50.2566 | 27.5951 |  | 13.4332 | 87.4366 | 40.8523 | 63.3672 | 72.0755 | 38.7888 | 46.7683 | 55.433 | 32.7715
Low Discount rate | 3.2% | 100% | 6.5 | 6.0322 | 24.053 | 190.5349 | 86.1597 | 134.2882 | 162.5509 | 81.2001 | 99.2467 | 119.5173 | 67.1385 |  | 30.0852 | 196.5671 | 92.1919 | 140.3204 | 168.5831 | 87.2323 | 105.2186 | 125.5495 | 73.1707
High Cost | 5.9% | 130% | 6.5 | 7.2572 | 12.3784 | 120.845 | 52.6906 | 84.8518 | 100.5689 | 49.5731 | 61.3516 | 74.2669 | 40.5748 |  | 19.6356 | 128.1022 | 59.9478 | 92.109 | 107.8261 | 56.8303 | 68.5362 | 81.5241 | 47.832
Low Cost | 5.9% | 70% | 6.5 | 3.9077 | 15.7278 | 124.1945 | 56.0401 | 88.2013 | 103.9184 | 52.9226 | 64.6676 | 77.6164 | 43.9243 |  | 19.6356 | 128.1022 | 59.9478 | 92.109 | 107.8261 | 56.8303 | 68.5362 | 81.5241 | 47.832
Base
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Base Weighted
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 5.5825 |  | NPV | [5 empty] | 19.6356 | NPV | [5 empty] | 128.1022 |  | NPV | [5 empty] | 59.9478 | NPV | [5 empty] | 92.109 | NPV | [5 empty] | 107.8261 | NPV | [5 empty] | 56.8303 | 0
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.44115 | 0.008823 | 5.6533 | 0.44997 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 0 | 0 | 0 | 0 | 0 | 0.44997 |  | 2023 | 24.1728 | 4.0153 | 0.53701 | 0.036673 | 0 | 0.57368 | 2023 | 112.515 | 18.65 | 2.5472 | 0.17034 | 0 | 2.7175 |  | 2023 | 74.359 | 12.1069 | 1.4854 | 0.11058 | 0 | 1.596 | 2023 | 90.8476 | 15.0348 | 2.0569 | 0.13732 | 0 | 2.1942 | 2023 | 42.0662 | 6.9708 | 0.94099 | 0.063667 | 0 | 1.0047 | 2023 | 58.8049 | 9.6969 | 1.2766 | 0.088565 | 0 | 1.3652
2024 | 0 | 0 | 0 | 0 | 0 | 0.44997 |  | 2024 | 27.9276 | 4.6401 | 0.63287 | 0.042379 | 0 | 0.67525 | 2024 | 215.6737 | 35.6525 | 5.0161 | 0.32563 | 0 | 5.3418 |  | 2024 | 87.8533 | 14.2891 | 1.8197 | 0.13051 | 0 | 1.9502 | 2024 | 152.7445 | 25.2486 | 3.5461 | 0.2306 | 0 | 3.7767 | 2024 | 73.6928 | 12.1918 | 1.6925 | 0.11135 | 0 | 1.8038 | 2024 | 89.8456 | 14.8054 | 2.0254 | 0.13522 | 0 | 2.1606
2025 | 0 | 0 | 0 | 0 | 0 | 0.44997 |  | 2025 | 34.2015 | 5.683 | 0.7671 | 0.051905 | 0 | 0.819 | 2025 | 242.3649 | 40.0401 | 5.6205 | 0.3657 | 0 | 5.9862 |  | 2025 | 96.0794 | 15.6796 | 2.0626 | 0.14321 | 0 | 2.2058 | 2025 | 206.6095 | 34.1294 | 4.7679 | 0.31172 | 0 | 5.0796 | 2025 | 109.1472 | 18.0898 | 2.4968 | 0.16522 | 0 | 2.662 | 2025 | 101.7118 | 16.7714 | 2.3043 | 0.15318 | 0 | 2.4575
2026 | 0 | 0 | 0 | 0 | 0 | 0.44997 |  | 2026 | 43.3082 | 7.1956 | 1.0364 | 0.06572 | 0 | 1.1021 | 2026 | 326.6711 | 53.7208 | 8.0261 | 0.49065 | 0 | 8.5167 |  | 2026 | 129.2218 | 20.9477 | 2.8027 | 0.19132 | 0 | 2.994 | 2026 | 267.3235 | 43.9588 | 6.5783 | 0.40149 | 0 | 6.9798 | 2026 | 189.6389 | 31.3623 | 4.6483 | 0.28644 | 0 | 4.9347 | 2026 | 135.6274 | 22.2649 | 3.2254 | 0.20335 | 0 | 3.4287
2027 | 0 | 0 | 0 | 0 | 0 | 0.44997 |  | 2027 | 48.4488 | 8.0439 | 1.2335 | 0.073468 | 0 | 1.307 | 2027 | 330.1975 | 54.2226 | 8.5261 | 0.49523 | 0 | 9.0214 |  | 2027 | 152.9223 | 24.8189 | 3.3454 | 0.22668 | 0 | 3.5721 | 2027 | 261.3693 | 42.9844 | 6.7973 | 0.39259 | 0 | 7.1899 | 2027 | 230.3765 | 37.9657 | 5.9857 | 0.34675 | 0 | 6.3325 | 2027 | 145.0044 | 23.7823 | 3.5847 | 0.21721 | 0 | 3.8019
2028 | 0 | 0 | 0 | 0 | 0 | 0.44997 |  | 2028 | 52.1958 | 8.6681 | 1.6562 | 0.079168 | 0 | 1.7354 | 2028 | 366.7742 | 60.0994 | 11.734 | 0.54891 | 0 | 12.2829 |  | 2028 | 203.3549 | 32.8554 | 5.4352 | 0.30008 | 0 | 5.7353 | 2028 | 284.3334 | 46.7208 | 9.1907 | 0.42672 | 0 | 9.6174 | 2028 | 316.2919 | 51.8011 | 10.2323 | 0.47312 | 0 | 10.7054 | 2028 | 168.6302 | 27.5727 | 5.1204 | 0.25183 | 0 | 5.3722
2029 | 0 | 0 | 0 | 0 | 0 | 0.44997 |  | 2029 | 61.6814 | 10.2368 | 2.0495 | 0.093497 | 0 | 2.143 | 2029 | 380.6559 | 62.0812 | 12.6699 | 0.56701 | 0 | 13.2369 |  | 2029 | 218.8927 | 35.3363 | 5.88 | 0.32274 | 0 | 6.2028 | 2029 | 264.493 | 43.4931 | 8.8825 | 0.39724 | 0 | 9.2797 | 2029 | 349.1548 | 57.0445 | 11.7449 | 0.52101 | 0 | 12.2659 | 2029 | 180.7279 | 29.4728 | 5.6622 | 0.26919 | 0 | 5.9314
2030 | 0 | 0 | 0 | 0 | 0 | 0.44997 |  | 2030 | 61.283 | 10.1756 | 2.0979 | 0.092937 | 0 | 2.1909 | 2030 | 398.24 | 64.7322 | 13.5537 | 0.59122 | 0 | 14.1449 |  | 2030 | 242.8681 | 39.095 | 6.5457 | 0.35707 | 0 | 6.9028 | 2030 | 243.8707 | 40.144 | 8.4231 | 0.36665 | 0 | 8.7898 | 2030 | 361.3765 | 58.9275 | 12.5043 | 0.5382 | 0 | 13.0425 | 2030 | 190.9185 | 31.0446 | 6.0738 | 0.28354 | 0 | 6.3574
Total | 100 | 6.5 | 0.44115 | 0.008823 | 5.6533 | 5.6533 |  | Total | 371.3572 | 61.6772 | 10.3894 | 0.56332 | 0 | 25.4171 | Total | 2400.0074 | 394.0404 | 68.2042 | 3.5989 | 0 | 166.1106 |  | Total | 1268.4109 | 205.3954 | 30.6308 | 1.8759 | 0 | 78.9031 | Total | 1812.6483 | 298.5322 | 51.1061 | 2.7266 | 0 | 115.9493 | Total | 1694.763 | 278.2622 | 50.7144 | 2.5415 | 0 | 150.8209 | Total | 1102.7832 | 180.6976 | 29.9035 | 1.6504 | 0 | 73.962
High Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 5.1764 |  | NPV | [5 empty] | 13.4332 | NPV | [5 empty] | 87.4366 |  | NPV | [5 empty] | 40.8523 | NPV | [5 empty] | 63.3672 | NPV | [5 empty] | 72.0755 | NPV | [5 empty] | 38.7888
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.56203 | 0.011241 | 5.9591 | 0.57327 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 0 | 0 | 0 | 0 | 0 | 0.57327 |  | 2023 | 24.1728 | 4.0153 | 0.53701 | 0.036673 | 0 | 0.57368 | 2023 | 112.515 | 18.65 | 2.5472 | 0.17034 | 0 | 2.7175 |  | 2023 | 74.359 | 12.1069 | 1.4854 | 0.11058 | 0 | 1.596 | 2023 | 90.8476 | 15.0348 | 2.0569 | 0.13732 | 0 | 2.1942 | 2023 | 42.0662 | 6.9708 | 0.94099 | 0.063667 | 0 | 1.0047 | 2023 | 58.8049 | 9.6969 | 1.2766 | 0.088565 | 0 | 1.3652
2024 | 0 | 0 | 0 | 0 | 0 | 0.57327 |  | 2024 | 27.9276 | 4.6401 | 0.63287 | 0.042379 | 0 | 0.67525 | 2024 | 215.6737 | 35.6525 | 5.0161 | 0.32563 | 0 | 5.3418 |  | 2024 | 87.8533 | 14.2891 | 1.8197 | 0.13051 | 0 | 1.9502 | 2024 | 152.7445 | 25.2486 | 3.5461 | 0.2306 | 0 | 3.7767 | 2024 | 73.6928 | 12.1918 | 1.6925 | 0.11135 | 0 | 1.8038 | 2024 | 89.8456 | 14.8054 | 2.0254 | 0.13522 | 0 | 2.1606
2025 | 0 | 0 | 0 | 0 | 0 | 0.57327 |  | 2025 | 34.2015 | 5.683 | 0.7671 | 0.051905 | 0 | 0.819 | 2025 | 242.3649 | 40.0401 | 5.6205 | 0.3657 | 0 | 5.9862 |  | 2025 | 96.0794 | 15.6796 | 2.0626 | 0.14321 | 0 | 2.2058 | 2025 | 206.6095 | 34.1294 | 4.7679 | 0.31172 | 0 | 5.0796 | 2025 | 109.1472 | 18.0898 | 2.4968 | 0.16522 | 0 | 2.662 | 2025 | 101.7118 | 16.7714 | 2.3043 | 0.15318 | 0 | 2.4575
2026 | 0 | 0 | 0 | 0 | 0 | 0.57327 |  | 2026 | 43.3082 | 7.1956 | 1.0364 | 0.06572 | 0 | 1.1021 | 2026 | 326.6711 | 53.7208 | 8.0261 | 0.49065 | 0 | 8.5167 |  | 2026 | 129.2218 | 20.9477 | 2.8027 | 0.19132 | 0 | 2.994 | 2026 | 267.3235 | 43.9588 | 6.5783 | 0.40149 | 0 | 6.9798 | 2026 | 189.6389 | 31.3623 | 4.6483 | 0.28644 | 0 | 4.9347 | 2026 | 135.6274 | 22.2649 | 3.2254 | 0.20335 | 0 | 3.4287
2027 | 0 | 0 | 0 | 0 | 0 | 0.57327 |  | 2027 | 48.4488 | 8.0439 | 1.2335 | 0.073468 | 0 | 1.307 | 2027 | 330.1975 | 54.2226 | 8.5261 | 0.49523 | 0 | 9.0214 |  | 2027 | 152.9223 | 24.8189 | 3.3454 | 0.22668 | 0 | 3.5721 | 2027 | 261.3693 | 42.9844 | 6.7973 | 0.39259 | 0 | 7.1899 | 2027 | 230.3765 | 37.9657 | 5.9857 | 0.34675 | 0 | 6.3325 | 2027 | 145.0044 | 23.7823 | 3.5847 | 0.21721 | 0 | 3.8019
2028 | 0 | 0 | 0 | 0 | 0 | 0.57327 |  | 2028 | 52.1958 | 8.6681 | 1.6562 | 0.079168 | 0 | 1.7354 | 2028 | 366.7742 | 60.0994 | 11.734 | 0.54891 | 0 | 12.2829 |  | 2028 | 203.3549 | 32.8554 | 5.4352 | 0.30008 | 0 | 5.7353 | 2028 | 284.3334 | 46.7208 | 9.1907 | 0.42672 | 0 | 9.6174 | 2028 | 316.2919 | 51.8011 | 10.2323 | 0.47312 | 0 | 10.7054 | 2028 | 168.6302 | 27.5727 | 5.1204 | 0.25183 | 0 | 5.3722
2029 | 0 | 0 | 0 | 0 | 0 | 0.57327 |  | 2029 | 61.6814 | 10.2368 | 2.0495 | 0.093497 | 0 | 2.143 | 2029 | 380.6559 | 62.0812 | 12.6699 | 0.56701 | 0 | 13.2369 |  | 2029 | 218.8927 | 35.3363 | 5.88 | 0.32274 | 0 | 6.2028 | 2029 | 264.493 | 43.4931 | 8.8825 | 0.39724 | 0 | 9.2797 | 2029 | 349.1548 | 57.0445 | 11.7449 | 0.52101 | 0 | 12.2659 | 2029 | 180.7279 | 29.4728 | 5.6622 | 0.26919 | 0 | 5.9314
2030 | 0 | 0 | 0 | 0 | 0 | 0.57327 |  | 2030 | 61.283 | 10.1756 | 2.0979 | 0.092937 | 0 | 2.1909 | 2030 | 398.24 | 64.7322 | 13.5537 | 0.59122 | 0 | 14.1449 |  | 2030 | 242.8681 | 39.095 | 6.5457 | 0.35707 | 0 | 6.9028 | 2030 | 243.8707 | 40.144 | 8.4231 | 0.36665 | 0 | 8.7898 | 2030 | 361.3765 | 58.9275 | 12.5043 | 0.5382 | 0 | 13.0425 | 2030 | 190.9185 | 31.0446 | 6.0738 | 0.28354 | 0 | 6.3574
Total | 100 | 6.5 | 0.56203 | 0.011241 | 5.9591 | 5.9591 |  | Total | 371.3572 | 61.6772 | 10.3894 | 0.56332 | 0 | 21.0295 | Total | 2400.0074 | 394.0404 | 68.2042 | 3.5989 | 0 | 137.4358 |  | Total | 1268.4109 | 205.3954 | 30.6308 | 1.8759 | 0 | 65.2824 | Total | 1812.6483 | 298.5322 | 51.1061 | 2.7266 | 0 | 95.9336 | Total | 1694.763 | 278.2622 | 50.7144 | 2.5415 | 0 | 124.7854 | Total | 1102.7832 | 180.6976 | 29.9035 | 1.6504 | 0 | 61.1943
Low Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 6.0322 |  | NPV | [5 empty] | 30.0852 | NPV | [5 empty] | 196.5671 |  | NPV | [5 empty] | 92.1919 | NPV | [5 empty] | 140.3204 | NPV | [5 empty] | 168.5831 | NPV | [5 empty] | 87.2323
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.32971 | 0.0065941 | 5.2483 | 0.3363 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 0 | 0 | 0 | 0 | 0 | 0.3363 |  | 2023 | 24.1728 | 4.0153 | 0.53701 | 0.036673 | 0 | 0.57368 | 2023 | 112.515 | 18.65 | 2.5472 | 0.17034 | 0 | 2.7175 |  | 2023 | 74.359 | 12.1069 | 1.4854 | 0.11058 | 0 | 1.596 | 2023 | 90.8476 | 15.0348 | 2.0569 | 0.13732 | 0 | 2.1942 | 2023 | 42.0662 | 6.9708 | 0.94099 | 0.063667 | 0 | 1.0047 | 2023 | 58.8049 | 9.6969 | 1.2766 | 0.088565 | 0 | 1.3652
2024 | 0 | 0 | 0 | 0 | 0 | 0.3363 |  | 2024 | 27.9276 | 4.6401 | 0.63287 | 0.042379 | 0 | 0.67525 | 2024 | 215.6737 | 35.6525 | 5.0161 | 0.32563 | 0 | 5.3418 |  | 2024 | 87.8533 | 14.2891 | 1.8197 | 0.13051 | 0 | 1.9502 | 2024 | 152.7445 | 25.2486 | 3.5461 | 0.2306 | 0 | 3.7767 | 2024 | 73.6928 | 12.1918 | 1.6925 | 0.11135 | 0 | 1.8038 | 2024 | 89.8456 | 14.8054 | 2.0254 | 0.13522 | 0 | 2.1606
2025 | 0 | 0 | 0 | 0 | 0 | 0.3363 |  | 2025 | 34.2015 | 5.683 | 0.7671 | 0.051905 | 0 | 0.819 | 2025 | 242.3649 | 40.0401 | 5.6205 | 0.3657 | 0 | 5.9862 |  | 2025 | 96.0794 | 15.6796 | 2.0626 | 0.14321 | 0 | 2.2058 | 2025 | 206.6095 | 34.1294 | 4.7679 | 0.31172 | 0 | 5.0796 | 2025 | 109.1472 | 18.0898 | 2.4968 | 0.16522 | 0 | 2.662 | 2025 | 101.7118 | 16.7714 | 2.3043 | 0.15318 | 0 | 2.4575
2026 | 0 | 0 | 0 | 0 | 0 | 0.3363 |  | 2026 | 43.3082 | 7.1956 | 1.0364 | 0.06572 | 0 | 1.1021 | 2026 | 326.6711 | 53.7208 | 8.0261 | 0.49065 | 0 | 8.5167 |  | 2026 | 129.2218 | 20.9477 | 2.8027 | 0.19132 | 0 | 2.994 | 2026 | 267.3235 | 43.9588 | 6.5783 | 0.40149 | 0 | 6.9798 | 2026 | 189.6389 | 31.3623 | 4.6483 | 0.28644 | 0 | 4.9347 | 2026 | 135.6274 | 22.2649 | 3.2254 | 0.20335 | 0 | 3.4287
2027 | 0 | 0 | 0 | 0 | 0 | 0.3363 |  | 2027 | 48.4488 | 8.0439 | 1.2335 | 0.073468 | 0 | 1.307 | 2027 | 330.1975 | 54.2226 | 8.5261 | 0.49523 | 0 | 9.0214 |  | 2027 | 152.9223 | 24.8189 | 3.3454 | 0.22668 | 0 | 3.5721 | 2027 | 261.3693 | 42.9844 | 6.7973 | 0.39259 | 0 | 7.1899 | 2027 | 230.3765 | 37.9657 | 5.9857 | 0.34675 | 0 | 6.3325 | 2027 | 145.0044 | 23.7823 | 3.5847 | 0.21721 | 0 | 3.8019
2028 | 0 | 0 | 0 | 0 | 0 | 0.3363 |  | 2028 | 52.1958 | 8.6681 | 1.6562 | 0.079168 | 0 | 1.7354 | 2028 | 366.7742 | 60.0994 | 11.734 | 0.54891 | 0 | 12.2829 |  | 2028 | 203.3549 | 32.8554 | 5.4352 | 0.30008 | 0 | 5.7353 | 2028 | 284.3334 | 46.7208 | 9.1907 | 0.42672 | 0 | 9.6174 | 2028 | 316.2919 | 51.8011 | 10.2323 | 0.47312 | 0 | 10.7054 | 2028 | 168.6302 | 27.5727 | 5.1204 | 0.25183 | 0 | 5.3722
2029 | 0 | 0 | 0 | 0 | 0 | 0.3363 |  | 2029 | 61.6814 | 10.2368 | 2.0495 | 0.093497 | 0 | 2.143 | 2029 | 380.6559 | 62.0812 | 12.6699 | 0.56701 | 0 | 13.2369 |  | 2029 | 218.8927 | 35.3363 | 5.88 | 0.32274 | 0 | 6.2028 | 2029 | 264.493 | 43.4931 | 8.8825 | 0.39724 | 0 | 9.2797 | 2029 | 349.1548 | 57.0445 | 11.7449 | 0.52101 | 0 | 12.2659 | 2029 | 180.7279 | 29.4728 | 5.6622 | 0.26919 | 0 | 5.9314
2030 | 0 | 0 | 0 | 0 | 0 | 0.3363 |  | 2030 | 61.283 | 10.1756 | 2.0979 | 0.092937 | 0 | 2.1909 | 2030 | 398.24 | 64.7322 | 13.5537 | 0.59122 | 0 | 14.1449 |  | 2030 | 242.8681 | 39.095 | 6.5457 | 0.35707 | 0 | 6.9028 | 2030 | 243.8707 | 40.144 | 8.4231 | 0.36665 | 0 | 8.7898 | 2030 | 361.3765 | 58.9275 | 12.5043 | 0.5382 | 0 | 13.0425 | 2030 | 190.9185 | 31.0446 | 6.0738 | 0.28354 | 0 | 6.3574
Total | 100 | 6.5 | 0.32971 | 0.0065941 | 5.2483 | 5.2483 |  | Total | 371.3572 | 61.6772 | 10.3894 | 0.56332 | 0 | 31.5722 | Total | 2400.0074 | 394.0404 | 68.2042 | 3.5989 | 0 | 206.3365 |  | Total | 1268.4109 | 205.3954 | 30.6308 | 1.8759 | 0 | 98.0105 | Total | 1812.6483 | 298.5322 | 51.1061 | 2.7266 | 0 | 144.028 | Total | 1694.763 | 278.2622 | 50.7144 | 2.5415 | 0 | 187.3441 |  | 1102.7832 | 180.6976 | 29.9035 | 1.6504 | 0 | 91.8729
High Cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 7.2572 |  | NPV | [5 empty] | 19.6356 | NPV | [5 empty] | 128.1022 |  | NPV | [5 empty] | 59.9478 | NPV | [5 empty] | 92.109 | NPV | [5 empty] | 107.8261 | NPV | [5 empty] | 56.8303
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 8.45 | 0.57349 | 0.01147 | 7.3492 | 0.58496 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 0 | 0 | 0 | 0 | 0 | 0.58496 |  | 2023 | 24.1728 | 4.0153 | 0.53701 | 0.036673 | 0 | 0.57368 | 2023 | 112.515 | 18.65 | 2.5472 | 0.17034 | 0 | 2.7175 |  | 2023 | 74.359 | 12.1069 | 1.4854 | 0.11058 | 0 | 1.596 | 2023 | 90.8476 | 15.0348 | 2.0569 | 0.13732 | 0 | 2.1942 | 2023 | 42.0662 | 6.9708 | 0.94099 | 0.063667 | 0 | 1.0047 | 2023 | 58.8049 | 9.6969 | 1.2766 | 0.088565 | 0 | 1.3652
2024 | 0 | 0 | 0 | 0 | 0 | 0.58496 |  | 2024 | 27.9276 | 4.6401 | 0.63287 | 0.042379 | 0 | 0.67525 | 2024 | 215.6737 | 35.6525 | 5.0161 | 0.32563 | 0 | 5.3418 |  | 2024 | 87.8533 | 14.2891 | 1.8197 | 0.13051 | 0 | 1.9502 | 2024 | 152.7445 | 25.2486 | 3.5461 | 0.2306 | 0 | 3.7767 | 2024 | 73.6928 | 12.1918 | 1.6925 | 0.11135 | 0 | 1.8038 | 2024 | 89.8456 | 14.8054 | 2.0254 | 0.13522 | 0 | 2.1606
2025 | 0 | 0 | 0 | 0 | 0 | 0.58496 |  | 2025 | 34.2015 | 5.683 | 0.7671 | 0.051905 | 0 | 0.819 | 2025 | 242.3649 | 40.0401 | 5.6205 | 0.3657 | 0 | 5.9862 |  | 2025 | 96.0794 | 15.6796 | 2.0626 | 0.14321 | 0 | 2.2058 | 2025 | 206.6095 | 34.1294 | 4.7679 | 0.31172 | 0 | 5.0796 | 2025 | 109.1472 | 18.0898 | 2.4968 | 0.16522 | 0 | 2.662 | 2025 | 101.7118 | 16.7714 | 2.3043 | 0.15318 | 0 | 2.4575
2026 | 0 | 0 | 0 | 0 | 0 | 0.58496 |  | 2026 | 43.3082 | 7.1956 | 1.0364 | 0.06572 | 0 | 1.1021 | 2026 | 326.6711 | 53.7208 | 8.0261 | 0.49065 | 0 | 8.5167 |  | 2026 | 129.2218 | 20.9477 | 2.8027 | 0.19132 | 0 | 2.994 | 2026 | 267.3235 | 43.9588 | 6.5783 | 0.40149 | 0 | 6.9798 | 2026 | 189.6389 | 31.3623 | 4.6483 | 0.28644 | 0 | 4.9347 | 2026 | 135.6274 | 22.2649 | 3.2254 | 0.20335 | 0 | 3.4287
2027 | 0 | 0 | 0 | 0 | 0 | 0.58496 |  | 2027 | 48.4488 | 8.0439 | 1.2335 | 0.073468 | 0 | 1.307 | 2027 | 330.1975 | 54.2226 | 8.5261 | 0.49523 | 0 | 9.0214 |  | 2027 | 152.9223 | 24.8189 | 3.3454 | 0.22668 | 0 | 3.5721 | 2027 | 261.3693 | 42.9844 | 6.7973 | 0.39259 | 0 | 7.1899 | 2027 | 230.3765 | 37.9657 | 5.9857 | 0.34675 | 0 | 6.3325 | 2027 | 145.0044 | 23.7823 | 3.5847 | 0.21721 | 0 | 3.8019
2028 | 0 | 0 | 0 | 0 | 0 | 0.58496 |  | 2028 | 52.1958 | 8.6681 | 1.6562 | 0.079168 | 0 | 1.7354 | 2028 | 366.7742 | 60.0994 | 11.734 | 0.54891 | 0 | 12.2829 |  | 2028 | 203.3549 | 32.8554 | 5.4352 | 0.30008 | 0 | 5.7353 | 2028 | 284.3334 | 46.7208 | 9.1907 | 0.42672 | 0 | 9.6174 | 2028 | 316.2919 | 51.8011 | 10.2323 | 0.47312 | 0 | 10.7054 | 2028 | 168.6302 | 27.5727 | 5.1204 | 0.25183 | 0 | 5.3722
2029 | 0 | 0 | 0 | 0 | 0 | 0.58496 |  | 2029 | 61.6814 | 10.2368 | 2.0495 | 0.093497 | 0 | 2.143 | 2029 | 380.6559 | 62.0812 | 12.6699 | 0.56701 | 0 | 13.2369 |  | 2029 | 218.8927 | 35.3363 | 5.88 | 0.32274 | 0 | 6.2028 | 2029 | 264.493 | 43.4931 | 8.8825 | 0.39724 | 0 | 9.2797 | 2029 | 349.1548 | 57.0445 | 11.7449 | 0.52101 | 0 | 12.2659 | 2029 | 180.7279 | 29.4728 | 5.6622 | 0.26919 | 0 | 5.9314
2030 | 0 | 0 | 0 | 0 | 0 | 0.58496 |  | 2030 | 61.283 | 10.1756 | 2.0979 | 0.092937 | 0 | 2.1909 | 2030 | 398.24 | 64.7322 | 13.5537 | 0.59122 | 0 | 14.1449 |  | 2030 | 242.8681 | 39.095 | 6.5457 | 0.35707 | 0 | 6.9028 | 2030 | 243.8707 | 40.144 | 8.4231 | 0.36665 | 0 | 8.7898 | 2030 | 361.3765 | 58.9275 | 12.5043 | 0.5382 | 0 | 13.0425 | 2030 | 190.9185 | 31.0446 | 6.0738 | 0.28354 | 0 | 6.3574
Total | 100 | 8.45 | 0.57349 | 0.01147 | 7.3492 | 7.3492 |  | Total | 371.3572 | 61.6772 | 10.3894 | 0.56332 | 0 | 25.4171 | Total | 2400.0074 | 394.0404 | 68.2042 | 3.5989 | 0 | 166.1106 |  | Total | 1268.4109 | 205.3954 | 30.6308 | 1.8759 | 0 | 78.9031 | Total | 1812.6483 | 298.5322 | 51.1061 | 2.7266 | 0 | 115.9493 | Total | 1694.763 | 278.2622 | 50.7144 | 2.5415 | 0 | 150.8209 | Total | 1102.7832 | 180.6976 | 29.9035 | 1.6504 | 0 | 73.962
Low cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 3.9077 |  | NPV | [5 empty] | 19.6356 | NPV | [5 empty] | 128.1022 |  | NPV | [5 empty] | 59.9478 | NPV | [5 empty] | 92.109 | NPV | [5 empty] | 107.8261 | NPV | [5 empty] | 56.8303
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 4.55 | 0.3088 | 0.0061761 | 3.9573 | 0.31498 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 0 | 0 | 0 | 0 | 0 | 0.31498 |  | 2023 | 24.1728 | 4.0153 | 0.53701 | 0.036673 | 0 | 0.57368 | 2023 | 112.515 | 18.65 | 2.5472 | 0.17034 | 0 | 2.7175 |  | 2023 | 74.359 | 12.1069 | 1.4854 | 0.11058 | 0 | 1.596 | 2023 | 90.8476 | 15.0348 | 2.0569 | 0.13732 | 0 | 2.1942 | 2023 | 42.0662 | 6.9708 | 0.94099 | 0.063667 | 0 | 1.0047 | 2023 | 58.8049 | 9.6969 | 1.2766 | 0.088565 | 0 | 1.3652
2024 | 0 | 0 | 0 | 0 | 0 | 0.31498 |  | 2024 | 27.9276 | 4.6401 | 0.63287 | 0.042379 | 0 | 0.67525 | 2024 | 215.6737 | 35.6525 | 5.0161 | 0.32563 | 0 | 5.3418 |  | 2024 | 87.8533 | 14.2891 | 1.8197 | 0.13051 | 0 | 1.9502 | 2024 | 152.7445 | 25.2486 | 3.5461 | 0.2306 | 0 | 3.7767 | 2024 | 73.6928 | 12.1918 | 1.6925 | 0.11135 | 0 | 1.8038 | 2024 | 89.8456 | 14.8054 | 2.0254 | 0.13522 | 0 | 2.1606
2025 | 0 | 0 | 0 | 0 | 0 | 0.31498 |  | 2025 | 34.2015 | 5.683 | 0.7671 | 0.051905 | 0 | 0.819 | 2025 | 242.3649 | 40.0401 | 5.6205 | 0.3657 | 0 | 5.9862 |  | 2025 | 96.0794 | 15.6796 | 2.0626 | 0.14321 | 0 | 2.2058 | 2025 | 206.6095 | 34.1294 | 4.7679 | 0.31172 | 0 | 5.0796 | 2025 | 109.1472 | 18.0898 | 2.4968 | 0.16522 | 0 | 2.662 | 2025 | 101.7118 | 16.7714 | 2.3043 | 0.15318 | 0 | 2.4575
2026 | 0 | 0 | 0 | 0 | 0 | 0.31498 |  | 2026 | 43.3082 | 7.1956 | 1.0364 | 0.06572 | 0 | 1.1021 | 2026 | 326.6711 | 53.7208 | 8.0261 | 0.49065 | 0 | 8.5167 |  | 2026 | 129.2218 | 20.9477 | 2.8027 | 0.19132 | 0 | 2.994 | 2026 | 267.3235 | 43.9588 | 6.5783 | 0.40149 | 0 | 6.9798 | 2026 | 189.6389 | 31.3623 | 4.6483 | 0.28644 | 0 | 4.9347 | 2026 | 135.6274 | 22.2649 | 3.2254 | 0.20335 | 0 | 3.4287
2027 | 0 | 0 | 0 | 0 | 0 | 0.31498 |  | 2027 | 48.4488 | 8.0439 | 1.2335 | 0.073468 | 0 | 1.307 | 2027 | 330.1975 | 54.2226 | 8.5261 | 0.49523 | 0 | 9.0214 |  | 2027 | 152.9223 | 24.8189 | 3.3454 | 0.22668 | 0 | 3.5721 | 2027 | 261.3693 | 42.9844 | 6.7973 | 0.39259 | 0 | 7.1899 | 2027 | 230.3765 | 37.9657 | 5.9857 | 0.34675 | 0 | 6.3325 | 2027 | 145.0044 | 23.7823 | 3.5847 | 0.21721 | 0 | 3.8019
2028 | 0 | 0 | 0 | 0 | 0 | 0.31498 |  | 2028 | 52.1958 | 8.6681 | 1.6562 | 0.079168 | 0 | 1.7354 | 2028 | 366.7742 | 60.0994 | 11.734 | 0.54891 | 0 | 12.2829 |  | 2028 | 203.3549 | 32.8554 | 5.4352 | 0.30008 | 0 | 5.7353 | 2028 | 284.3334 | 46.7208 | 9.1907 | 0.42672 | 0 | 9.6174 | 2028 | 316.2919 | 51.8011 | 10.2323 | 0.47312 | 0 | 10.7054 | 2028 | 168.6302 | 27.5727 | 5.1204 | 0.25183 | 0 | 5.3722
2029 | 0 | 0 | 0 | 0 | 0 | 0.31498 |  | 2029 | 61.6814 | 10.2368 | 2.0495 | 0.093497 | 0 | 2.143 | 2029 | 380.6559 | 62.0812 | 12.6699 | 0.56701 | 0 | 13.2369 |  | 2029 | 218.8927 | 35.3363 | 5.88 | 0.32274 | 0 | 6.2028 | 2029 | 264.493 | 43.4931 | 8.8825 | 0.39724 | 0 | 9.2797 | 2029 | 349.1548 | 57.0445 | 11.7449 | 0.52101 | 0 | 12.2659 | 2029 | 180.7279 | 29.4728 | 5.6622 | 0.26919 | 0 | 5.9314
2030 | 0 | 0 | 0 | 0 | 0 | 0.31498 |  | 2030 | 61.283 | 10.1756 | 2.0979 | 0.092937 | 0 | 2.1909 | 2030 | 398.24 | 64.7322 | 13.5537 | 0.59122 | 0 | 14.1449 |  | 2030 | 242.8681 | 39.095 | 6.5457 | 0.35707 | 0 | 6.9028 | 2030 | 243.8707 | 40.144 | 8.4231 | 0.36665 | 0 | 8.7898 | 2030 | 361.3765 | 58.9275 | 12.5043 | 0.5382 | 0 | 13.0425 | 2030 | 190.9185 | 31.0446 | 6.0738 | 0.28354 | 0 | 6.3574
Total | 100 | 4.55 | 0.3088 | 0.0061761 | 3.9573 | 3.9573 |  | Total | 371.3572 | 61.6772 | 10.3894 | 0.56332 | 0 | 25.4171 | Total | 2400.0074 | 394.0404 | 68.2042 | 3.5989 | 0 | 166.1106 |  | Total | 1268.4109 | 205.3954 | 30.6308 | 1.8759 | 0 | 78.9031 | Total | 1812.6483 | 298.5322 | 51.1061 | 2.7266 | 0 | 115.9493 | Total | 1694.763 | 278.2622 | 50.7144 | 2.5415 | 0 | 150.8209 | Total | 1102.7832 | 180.6976 | 29.9035 | 1.6504 | 0 | 73.962

## Option 1A
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M |  | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change |  | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change
Base | 5.9% | 100% | 13.3 | 11.0972 | 14.8634 | 211.6049 | 73.1862 | 139.055 | 168.3392 | 78.6295 | 98.886 | 121.4097 | 60.492 |  | 25.9606 | 222.7021 | 84.2834 | 150.1522 | 179.4364 | 89.7267 | 109.8722 | 132.5069 | 71.5892
High Discount rate | 8.6% | 100% | 13.3 | 10.1628 | 7.534 | 140.6494 | 46.9866 | 92.5566 | 109.0722 | 50.676 | 64.4061 | 79.3598 | 38.6528 |  | 17.6968 | 150.8122 | 57.1494 | 102.7194 | 119.235 | 60.8388 | 74.4673 | 89.5226 | 48.8156
Low Discount rate | 3.2% | 100% | 13.3 | 12.1471 | 27.7849 | 332.4323 | 118.1554 | 218.0163 | 270.2035 | 126.5394 | 157.8629 | 193.3185 | 97.9354 |  | 39.932 | 344.5794 | 130.3025 | 230.1634 | 282.3506 | 138.6864 | 169.8886 | 205.4656 | 110.0825
High Cost | 5.9% | 130% | 13.3 | 14.4264 | 11.5342 | 208.2757 | 69.857 | 135.7259 | 165.01 | 75.3003 | 95.5901 | 118.0806 | 57.1628 |  | 25.9606 | 222.7021 | 84.2834 | 150.1522 | 179.4364 | 89.7267 | 109.8722 | 132.5069 | 71.5892
Low Cost | 5.9% | 70% | 13.3 | 7.768 | 18.1925 | 214.934 | 76.5153 | 142.3842 | 171.6684 | 81.9586 | 102.1818 | 124.7389 | 63.8211 |  | 25.9606 | 222.7021 | 84.2834 | 150.1522 | 179.4364 | 89.7267 | 109.8722 | 132.5069 | 71.5892
Base
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Base Weighted
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 11.0972 |  | NPV | [5 empty] | 25.9606 | NPV | [5 empty] | 222.7021 |  | NPV | [5 empty] | 84.2834 | NPV | [5 empty] | 150.1522 | NPV | [5 empty] | 179.4364 | NPV | [5 empty] | 89.7267 | 0
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.44115 | 0.008823 | 5.6533 | 0.44997 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.46151 | 0.0092302 | 6.0554 | 0.92071 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2025 | 44.1055 | 7.3336 | 0.98783 | 0.06698 | 0 | 1.0548 | 2025 | 393.6579 | 65.2042 | 9.1312 | 0.59553 | 0 | 9.7267 |  | 2025 | 131.0436 | 21.4774 | 2.8069 | 0.19616 | 0 | 3.0031 | 2025 | 326.3775 | 54.0477 | 7.5311 | 0.49364 | 0 | 8.0248 | 2025 | 158.6816 | 26.3311 | 3.6266 | 0.24049 | 0 | 3.867 | 2025 | 153.2281 | 25.3372 | 3.4784 | 0.23141 | 0 | 3.7099
2026 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2026 | 56.0708 | 9.3215 | 1.3394 | 0.085137 | 0 | 1.4245 | 2026 | 551.449 | 90.967 | 13.5574 | 0.83083 | 0 | 14.3882 |  | 2026 | 176.7768 | 28.8239 | 3.8288 | 0.26326 | 0 | 4.092 | 2026 | 435.8405 | 71.9285 | 10.7298 | 0.65695 | 0 | 11.3868 | 2026 | 294.7932 | 48.8484 | 7.227 | 0.44615 | 0 | 7.6732 | 2026 | 210.0918 | 34.6085 | 5.0162 | 0.31609 | 0 | 5.3323
2027 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2027 | 63.8547 | 10.6104 | 1.6224 | 0.096908 | 0 | 1.7193 | 2027 | 564.7755 | 93.0603 | 14.5925 | 0.84995 | 0 | 15.4424 |  | 2027 | 211.2452 | 34.4787 | 4.6167 | 0.31491 | 0 | 4.9316 | 2027 | 427.2844 | 70.5278 | 11.1162 | 0.64415 | 0 | 11.7603 | 2027 | 373.0925 | 61.6627 | 9.6975 | 0.56319 | 0 | 10.2607 | 2027 | 225.9325 | 37.1899 | 5.6135 | 0.33967 | 0 | 5.9532
2028 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2028 | 68.7329 | 11.4236 | 2.1773 | 0.10434 | 0 | 2.2816 | 2028 | 633.7705 | 104.2448 | 20.2856 | 0.9521 | 0 | 21.2377 |  | 2028 | 278.7189 | 45.3072 | 7.4454 | 0.41381 | 0 | 7.8592 | 2028 | 471.7976 | 77.8496 | 15.2541 | 0.71103 | 0 | 15.9652 | 2028 | 529.6218 | 87.1645 | 17.1409 | 0.7961 | 0 | 17.937 | 2028 | 262.4888 | 43.0998 | 8.0214 | 0.39364 | 0 | 8.415
2029 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2029 | 82.3425 | 13.6786 | 2.7321 | 0.12493 | 0 | 2.857 | 2029 | 674.8209 | 110.5344 | 22.4688 | 1.0095 | 0 | 23.4784 |  | 2029 | 311.6242 | 50.6473 | 8.3711 | 0.46258 | 0 | 8.8337 | 2029 | 433.4637 | 71.5254 | 14.5645 | 0.65327 | 0 | 15.2177 | 2029 | 583.0173 | 95.6646 | 19.6191 | 0.87374 | 0 | 20.4928 | 2029 | 287.7826 | 47.1347 | 9.076 | 0.4305 | 0 | 9.5065
2030 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2030 | 81.4832 | 13.5413 | 2.7868 | 0.12368 | 0 | 2.9105 | 2030 | 704.7093 | 115.0314 | 23.989 | 1.0506 | 0 | 25.0396 |  | 2030 | 349.7725 | 56.7226 | 9.4296 | 0.51807 | 0 | 9.9477 | 2030 | 393.8378 | 65.0445 | 13.6068 | 0.59407 | 0 | 14.2009 | 2030 | 603.3014 | 98.8395 | 20.8868 | 0.90273 | 0 | 21.7895 | 2030 | 304.3621 | 49.7092 | 9.7481 | 0.45401 | 0 | 10.2021
Total | 200 | 13.3 | 0.90266 | 0.018053 | 11.7087 | 11.7087 |  | Total | 483.217 | 80.3146 | 13.5617 | 0.73354 | 0 | 33.9068 | Total | 4001.0902 | 659.9064 | 114.795 | 6.0271 | 0 | 295.1373 |  | Total | 1743.5818 | 283.9546 | 42.2576 | 2.5935 | 0 | 112.3473 | Total | 2877.8584 | 475.4306 | 81.6659 | 4.3423 | 0 | 191.8314 | Total | 2718.4416 | 448.0235 | 82.1075 | 4.0919 | 0 | 254.6117 | Total | 1677.7765 | 276.1226 | 46.044 | 2.5219 | 0 | 118.8245
High Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 10.1628 |  | NPV | [5 empty] | 17.6968 | NPV | [5 empty] | 150.8122 |  | NPV | [5 empty] | 57.1494 | NPV | [5 empty] | 102.7194 | NPV | [5 empty] | 119.235 | NPV | [5 empty] | 60.8388
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.56203 | 0.011241 | 5.9591 | 0.57327 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.58797 | 0.011759 | 6.3402 | 1.173 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2025 | 44.1055 | 7.3336 | 0.98783 | 0.06698 | 0 | 1.0548 | 2025 | 393.6579 | 65.2042 | 9.1312 | 0.59553 | 0 | 9.7267 |  | 2025 | 131.0436 | 21.4774 | 2.8069 | 0.19616 | 0 | 3.0031 | 2025 | 326.3775 | 54.0477 | 7.5311 | 0.49364 | 0 | 8.0248 | 2025 | 158.6816 | 26.3311 | 3.6266 | 0.24049 | 0 | 3.867 | 2025 | 153.2281 | 25.3372 | 3.4784 | 0.23141 | 0 | 3.7099
2026 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2026 | 56.0708 | 9.3215 | 1.3394 | 0.085137 | 0 | 1.4245 | 2026 | 551.449 | 90.967 | 13.5574 | 0.83083 | 0 | 14.3882 |  | 2026 | 176.7768 | 28.8239 | 3.8288 | 0.26326 | 0 | 4.092 | 2026 | 435.8405 | 71.9285 | 10.7298 | 0.65695 | 0 | 11.3868 | 2026 | 294.7932 | 48.8484 | 7.227 | 0.44615 | 0 | 7.6732 | 2026 | 210.0918 | 34.6085 | 5.0162 | 0.31609 | 0 | 5.3323
2027 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2027 | 63.8547 | 10.6104 | 1.6224 | 0.096908 | 0 | 1.7193 | 2027 | 564.7755 | 93.0603 | 14.5925 | 0.84995 | 0 | 15.4424 |  | 2027 | 211.2452 | 34.4787 | 4.6167 | 0.31491 | 0 | 4.9316 | 2027 | 427.2844 | 70.5278 | 11.1162 | 0.64415 | 0 | 11.7603 | 2027 | 373.0925 | 61.6627 | 9.6975 | 0.56319 | 0 | 10.2607 | 2027 | 225.9325 | 37.1899 | 5.6135 | 0.33967 | 0 | 5.9532
2028 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2028 | 68.7329 | 11.4236 | 2.1773 | 0.10434 | 0 | 2.2816 | 2028 | 633.7705 | 104.2448 | 20.2856 | 0.9521 | 0 | 21.2377 |  | 2028 | 278.7189 | 45.3072 | 7.4454 | 0.41381 | 0 | 7.8592 | 2028 | 471.7976 | 77.8496 | 15.2541 | 0.71103 | 0 | 15.9652 | 2028 | 529.6218 | 87.1645 | 17.1409 | 0.7961 | 0 | 17.937 | 2028 | 262.4888 | 43.0998 | 8.0214 | 0.39364 | 0 | 8.415
2029 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2029 | 82.3425 | 13.6786 | 2.7321 | 0.12493 | 0 | 2.857 | 2029 | 674.8209 | 110.5344 | 22.4688 | 1.0095 | 0 | 23.4784 |  | 2029 | 311.6242 | 50.6473 | 8.3711 | 0.46258 | 0 | 8.8337 | 2029 | 433.4637 | 71.5254 | 14.5645 | 0.65327 | 0 | 15.2177 | 2029 | 583.0173 | 95.6646 | 19.6191 | 0.87374 | 0 | 20.4928 | 2029 | 287.7826 | 47.1347 | 9.076 | 0.4305 | 0 | 9.5065
2030 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2030 | 81.4832 | 13.5413 | 2.7868 | 0.12368 | 0 | 2.9105 | 2030 | 704.7093 | 115.0314 | 23.989 | 1.0506 | 0 | 25.0396 |  | 2030 | 349.7725 | 56.7226 | 9.4296 | 0.51807 | 0 | 9.9477 | 2030 | 393.8378 | 65.0445 | 13.6068 | 0.59407 | 0 | 14.2009 | 2030 | 603.3014 | 98.8395 | 20.8868 | 0.90273 | 0 | 21.7895 | 2030 | 304.3621 | 49.7092 | 9.7481 | 0.45401 | 0 | 10.2021
Total | 200 | 13.3 | 1.15 | 0.023 | 12.2993 | 12.2993 |  | Total | 483.217 | 80.3146 | 13.5617 | 0.73354 | 0 | 28.0065 | Total | 4001.0902 | 659.9064 | 114.795 | 6.0271 | 0 | 243.4729 |  | Total | 1743.5818 | 283.9546 | 42.2576 | 2.5935 | 0 | 92.7677 | Total | 2877.8584 | 475.4306 | 81.6659 | 4.3423 | 0 | 158.2952 | Total | 2718.4416 | 448.0235 | 82.1075 | 4.0919 | 0 | 210.0832 | Total | 1677.7765 | 276.1226 | 46.044 | 2.5219 | 0 | 98.0634
Low Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 12.1471 |  | NPV | [5 empty] | 39.932 | NPV | [5 empty] | 344.5794 |  | NPV | [5 empty] | 130.3025 | NPV | [5 empty] | 230.1634 | NPV | [5 empty] | 282.3506 | NPV | [5 empty] | 138.6864
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.32971 | 0.0065941 | 5.2483 | 0.3363 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.34492 | 0.0068984 | 5.6721 | 0.68812 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2025 | 44.1055 | 7.3336 | 0.98783 | 0.06698 | 0 | 1.0548 | 2025 | 393.6579 | 65.2042 | 9.1312 | 0.59553 | 0 | 9.7267 |  | 2025 | 131.0436 | 21.4774 | 2.8069 | 0.19616 | 0 | 3.0031 | 2025 | 326.3775 | 54.0477 | 7.5311 | 0.49364 | 0 | 8.0248 | 2025 | 158.6816 | 26.3311 | 3.6266 | 0.24049 | 0 | 3.867 | 2025 | 153.2281 | 25.3372 | 3.4784 | 0.23141 | 0 | 3.7099
2026 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2026 | 56.0708 | 9.3215 | 1.3394 | 0.085137 | 0 | 1.4245 | 2026 | 551.449 | 90.967 | 13.5574 | 0.83083 | 0 | 14.3882 |  | 2026 | 176.7768 | 28.8239 | 3.8288 | 0.26326 | 0 | 4.092 | 2026 | 435.8405 | 71.9285 | 10.7298 | 0.65695 | 0 | 11.3868 | 2026 | 294.7932 | 48.8484 | 7.227 | 0.44615 | 0 | 7.6732 | 2026 | 210.0918 | 34.6085 | 5.0162 | 0.31609 | 0 | 5.3323
2027 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2027 | 63.8547 | 10.6104 | 1.6224 | 0.096908 | 0 | 1.7193 | 2027 | 564.7755 | 93.0603 | 14.5925 | 0.84995 | 0 | 15.4424 |  | 2027 | 211.2452 | 34.4787 | 4.6167 | 0.31491 | 0 | 4.9316 | 2027 | 427.2844 | 70.5278 | 11.1162 | 0.64415 | 0 | 11.7603 | 2027 | 373.0925 | 61.6627 | 9.6975 | 0.56319 | 0 | 10.2607 | 2027 | 225.9325 | 37.1899 | 5.6135 | 0.33967 | 0 | 5.9532
2028 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2028 | 68.7329 | 11.4236 | 2.1773 | 0.10434 | 0 | 2.2816 | 2028 | 633.7705 | 104.2448 | 20.2856 | 0.9521 | 0 | 21.2377 |  | 2028 | 278.7189 | 45.3072 | 7.4454 | 0.41381 | 0 | 7.8592 | 2028 | 471.7976 | 77.8496 | 15.2541 | 0.71103 | 0 | 15.9652 | 2028 | 529.6218 | 87.1645 | 17.1409 | 0.7961 | 0 | 17.937 | 2028 | 262.4888 | 43.0998 | 8.0214 | 0.39364 | 0 | 8.415
2029 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2029 | 82.3425 | 13.6786 | 2.7321 | 0.12493 | 0 | 2.857 | 2029 | 674.8209 | 110.5344 | 22.4688 | 1.0095 | 0 | 23.4784 |  | 2029 | 311.6242 | 50.6473 | 8.3711 | 0.46258 | 0 | 8.8337 | 2029 | 433.4637 | 71.5254 | 14.5645 | 0.65327 | 0 | 15.2177 | 2029 | 583.0173 | 95.6646 | 19.6191 | 0.87374 | 0 | 20.4928 | 2029 | 287.7826 | 47.1347 | 9.076 | 0.4305 | 0 | 9.5065
2030 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2030 | 81.4832 | 13.5413 | 2.7868 | 0.12368 | 0 | 2.9105 | 2030 | 704.7093 | 115.0314 | 23.989 | 1.0506 | 0 | 25.0396 |  | 2030 | 349.7725 | 56.7226 | 9.4296 | 0.51807 | 0 | 9.9477 | 2030 | 393.8378 | 65.0445 | 13.6068 | 0.59407 | 0 | 14.2009 | 2030 | 603.3014 | 98.8395 | 20.8868 | 0.90273 | 0 | 21.7895 | 2030 | 304.3621 | 49.7092 | 9.7481 | 0.45401 | 0 | 10.2021
Total | 200 | 13.3 | 0.67463 | 0.013493 | 10.9204 | 10.9204 |  | Total | 483.217 | 80.3146 | 13.5617 | 0.73354 | 0 | 42.2124 | Total | 4001.0902 | 659.9064 | 114.795 | 6.0271 | 0 | 368.0469 |  | Total | 1743.5818 | 283.9546 | 42.2576 | 2.5935 | 0 | 139.9264 | Total | 2877.8584 | 475.4306 | 81.6659 | 4.3423 | 0 | 239.1317 | Total | 2718.4416 | 448.0235 | 82.1075 | 4.0919 | 0 | 317.4262 |  | 1677.7765 | 276.1226 | 46.044 | 2.5219 | 0 | 148.0995
High Cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 14.4264 |  | NPV | [5 empty] | 25.9606 | NPV | [5 empty] | 222.7021 |  | NPV | [5 empty] | 84.2834 | NPV | [5 empty] | 150.1522 | NPV | [5 empty] | 179.4364 | NPV | [5 empty] | 89.7267
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 8.45 | 0.57349 | 0.01147 | 7.3492 | 0.58496 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 8.84 | 0.59996 | 0.011999 | 7.8721 | 1.1969 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2025 | 44.1055 | 7.3336 | 0.98783 | 0.06698 | 0 | 1.0548 | 2025 | 393.6579 | 65.2042 | 9.1312 | 0.59553 | 0 | 9.7267 |  | 2025 | 131.0436 | 21.4774 | 2.8069 | 0.19616 | 0 | 3.0031 | 2025 | 326.3775 | 54.0477 | 7.5311 | 0.49364 | 0 | 8.0248 | 2025 | 158.6816 | 26.3311 | 3.6266 | 0.24049 | 0 | 3.867 | 2025 | 153.2281 | 25.3372 | 3.4784 | 0.23141 | 0 | 3.7099
2026 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2026 | 56.0708 | 9.3215 | 1.3394 | 0.085137 | 0 | 1.4245 | 2026 | 551.449 | 90.967 | 13.5574 | 0.83083 | 0 | 14.3882 |  | 2026 | 176.7768 | 28.8239 | 3.8288 | 0.26326 | 0 | 4.092 | 2026 | 435.8405 | 71.9285 | 10.7298 | 0.65695 | 0 | 11.3868 | 2026 | 294.7932 | 48.8484 | 7.227 | 0.44615 | 0 | 7.6732 | 2026 | 210.0918 | 34.6085 | 5.0162 | 0.31609 | 0 | 5.3323
2027 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2027 | 63.8547 | 10.6104 | 1.6224 | 0.096908 | 0 | 1.7193 | 2027 | 564.7755 | 93.0603 | 14.5925 | 0.84995 | 0 | 15.4424 |  | 2027 | 211.2452 | 34.4787 | 4.6167 | 0.31491 | 0 | 4.9316 | 2027 | 427.2844 | 70.5278 | 11.1162 | 0.64415 | 0 | 11.7603 | 2027 | 373.0925 | 61.6627 | 9.6975 | 0.56319 | 0 | 10.2607 | 2027 | 225.9325 | 37.1899 | 5.6135 | 0.33967 | 0 | 5.9532
2028 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2028 | 68.7329 | 11.4236 | 2.1773 | 0.10434 | 0 | 2.2816 | 2028 | 633.7705 | 104.2448 | 20.2856 | 0.9521 | 0 | 21.2377 |  | 2028 | 278.7189 | 45.3072 | 7.4454 | 0.41381 | 0 | 7.8592 | 2028 | 471.7976 | 77.8496 | 15.2541 | 0.71103 | 0 | 15.9652 | 2028 | 529.6218 | 87.1645 | 17.1409 | 0.7961 | 0 | 17.937 | 2028 | 262.4888 | 43.0998 | 8.0214 | 0.39364 | 0 | 8.415
2029 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2029 | 82.3425 | 13.6786 | 2.7321 | 0.12493 | 0 | 2.857 | 2029 | 674.8209 | 110.5344 | 22.4688 | 1.0095 | 0 | 23.4784 |  | 2029 | 311.6242 | 50.6473 | 8.3711 | 0.46258 | 0 | 8.8337 | 2029 | 433.4637 | 71.5254 | 14.5645 | 0.65327 | 0 | 15.2177 | 2029 | 583.0173 | 95.6646 | 19.6191 | 0.87374 | 0 | 20.4928 | 2029 | 287.7826 | 47.1347 | 9.076 | 0.4305 | 0 | 9.5065
2030 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2030 | 81.4832 | 13.5413 | 2.7868 | 0.12368 | 0 | 2.9105 | 2030 | 704.7093 | 115.0314 | 23.989 | 1.0506 | 0 | 25.0396 |  | 2030 | 349.7725 | 56.7226 | 9.4296 | 0.51807 | 0 | 9.9477 | 2030 | 393.8378 | 65.0445 | 13.6068 | 0.59407 | 0 | 14.2009 | 2030 | 603.3014 | 98.8395 | 20.8868 | 0.90273 | 0 | 21.7895 | 2030 | 304.3621 | 49.7092 | 9.7481 | 0.45401 | 0 | 10.2021
Total | 200 | 17.29 | 1.1735 | 0.023469 | 15.2213 | 15.2213 |  | Total | 483.217 | 80.3146 | 13.5617 | 0.73354 | 0 | 33.9068 | Total | 4001.0902 | 659.9064 | 114.795 | 6.0271 | 0 | 295.1373 |  | Total | 1743.5818 | 283.9546 | 42.2576 | 2.5935 | 0 | 112.3473 | Total | 2877.8584 | 475.4306 | 81.6659 | 4.3423 | 0 | 191.8314 | Total | 2718.4416 | 448.0235 | 82.1075 | 4.0919 | 0 | 254.6117 | Total | 1677.7765 | 276.1226 | 46.044 | 2.5219 | 0 | 118.8245
Low cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 7.768 |  | NPV | [5 empty] | 25.9606 | NPV | [5 empty] | 222.7021 |  | NPV | [5 empty] | 84.2834 | NPV | [5 empty] | 150.1522 | NPV | [5 empty] | 179.4364 | NPV | [5 empty] | 89.7267
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 4.55 | 0.3088 | 0.0061761 | 3.9573 | 0.31498 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 4.76 | 0.32306 | 0.0064611 | 4.2388 | 0.6445 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2025 | 44.1055 | 7.3336 | 0.98783 | 0.06698 | 0 | 1.0548 | 2025 | 393.6579 | 65.2042 | 9.1312 | 0.59553 | 0 | 9.7267 |  | 2025 | 131.0436 | 21.4774 | 2.8069 | 0.19616 | 0 | 3.0031 | 2025 | 326.3775 | 54.0477 | 7.5311 | 0.49364 | 0 | 8.0248 | 2025 | 158.6816 | 26.3311 | 3.6266 | 0.24049 | 0 | 3.867 | 2025 | 153.2281 | 25.3372 | 3.4784 | 0.23141 | 0 | 3.7099
2026 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2026 | 56.0708 | 9.3215 | 1.3394 | 0.085137 | 0 | 1.4245 | 2026 | 551.449 | 90.967 | 13.5574 | 0.83083 | 0 | 14.3882 |  | 2026 | 176.7768 | 28.8239 | 3.8288 | 0.26326 | 0 | 4.092 | 2026 | 435.8405 | 71.9285 | 10.7298 | 0.65695 | 0 | 11.3868 | 2026 | 294.7932 | 48.8484 | 7.227 | 0.44615 | 0 | 7.6732 | 2026 | 210.0918 | 34.6085 | 5.0162 | 0.31609 | 0 | 5.3323
2027 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2027 | 63.8547 | 10.6104 | 1.6224 | 0.096908 | 0 | 1.7193 | 2027 | 564.7755 | 93.0603 | 14.5925 | 0.84995 | 0 | 15.4424 |  | 2027 | 211.2452 | 34.4787 | 4.6167 | 0.31491 | 0 | 4.9316 | 2027 | 427.2844 | 70.5278 | 11.1162 | 0.64415 | 0 | 11.7603 | 2027 | 373.0925 | 61.6627 | 9.6975 | 0.56319 | 0 | 10.2607 | 2027 | 225.9325 | 37.1899 | 5.6135 | 0.33967 | 0 | 5.9532
2028 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2028 | 68.7329 | 11.4236 | 2.1773 | 0.10434 | 0 | 2.2816 | 2028 | 633.7705 | 104.2448 | 20.2856 | 0.9521 | 0 | 21.2377 |  | 2028 | 278.7189 | 45.3072 | 7.4454 | 0.41381 | 0 | 7.8592 | 2028 | 471.7976 | 77.8496 | 15.2541 | 0.71103 | 0 | 15.9652 | 2028 | 529.6218 | 87.1645 | 17.1409 | 0.7961 | 0 | 17.937 | 2028 | 262.4888 | 43.0998 | 8.0214 | 0.39364 | 0 | 8.415
2029 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2029 | 82.3425 | 13.6786 | 2.7321 | 0.12493 | 0 | 2.857 | 2029 | 674.8209 | 110.5344 | 22.4688 | 1.0095 | 0 | 23.4784 |  | 2029 | 311.6242 | 50.6473 | 8.3711 | 0.46258 | 0 | 8.8337 | 2029 | 433.4637 | 71.5254 | 14.5645 | 0.65327 | 0 | 15.2177 | 2029 | 583.0173 | 95.6646 | 19.6191 | 0.87374 | 0 | 20.4928 | 2029 | 287.7826 | 47.1347 | 9.076 | 0.4305 | 0 | 9.5065
2030 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2030 | 81.4832 | 13.5413 | 2.7868 | 0.12368 | 0 | 2.9105 | 2030 | 704.7093 | 115.0314 | 23.989 | 1.0506 | 0 | 25.0396 |  | 2030 | 349.7725 | 56.7226 | 9.4296 | 0.51807 | 0 | 9.9477 | 2030 | 393.8378 | 65.0445 | 13.6068 | 0.59407 | 0 | 14.2009 | 2030 | 603.3014 | 98.8395 | 20.8868 | 0.90273 | 0 | 21.7895 | 2030 | 304.3621 | 49.7092 | 9.7481 | 0.45401 | 0 | 10.2021
Total | 200 | 9.31 | 0.63186 | 0.012637 | 8.1961 | 8.1961 |  | Total | 483.217 | 80.3146 | 13.5617 | 0.73354 | 0 | 33.9068 | Total | 4001.0902 | 659.9064 | 114.795 | 6.0271 | 0 | 295.1373 |  | Total | 1743.5818 | 283.9546 | 42.2576 | 2.5935 | 0 | 112.3473 | Total | 2877.8584 | 475.4306 | 81.6659 | 4.3423 | 0 | 191.8314 | Total | 2718.4416 | 448.0235 | 82.1075 | 4.0919 | 0 | 254.6117 | Total | 1677.7765 | 276.1226 | 46.044 | 2.5219 | 0 | 118.8245

## Option 1B
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M |  | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change |  | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change
Base | 5.9% | 100% | 20.8 | 16.5208 | 9.761 | 276.1596 | 75.6977 | 167.9092 | 211.8824 | 92.8448 | 119.334 | 148.282 | 65.7822 |  | 26.2818 | 292.6803 | 92.2185 | 184.43 | 228.4031 | 109.3656 | 135.6896 | 164.8027 | 82.303
High Discount rate | 8.6% | 100% | 20.8 | 14.826 | 3.0895 | 181.6097 | 47.4942 | 110.5784 | 135.8564 | 58.8207 | 76.6238 | 95.7256 | 41.0629 |  | 17.9155 | 196.4357 | 62.3202 | 125.4044 | 150.6823 | 73.6467 | 91.3015 | 110.5516 | 55.8889
Low Discount rate | 3.2% | 100% | 20.8 | 18.4797 | 21.9498 | 438.9244 | 124.6242 | 266.2153 | 343.8854 | 151.862 | 193.2145 | 239.1198 | 108.6848 |  | 40.4295 | 457.4041 | 143.1039 | 284.695 | 362.3651 | 170.3418 | 211.5094 | 257.5995 | 127.1645
High Cost | 5.9% | 130% | 20.8 | 21.477 | 4.8048 | 271.2033 | 70.7415 | 162.953 | 206.9261 | 87.8886 | 114.4274 | 143.3257 | 60.826 |  | 26.2818 | 292.6803 | 92.2185 | 184.43 | 228.4031 | 109.3656 | 135.6896 | 164.8027 | 82.303
Low Cost | 5.9% | 70% | 20.8 | 11.5645 | 14.7173 | 281.1158 | 80.6539 | 172.8654 | 216.8386 | 97.8011 | 124.2407 | 153.2382 | 70.7385 |  | 26.2818 | 292.6803 | 92.2185 | 184.43 | 228.4031 | 109.3656 | 135.6896 | 164.8027 | 82.303
Base
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Base Weighted
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 16.5208 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 292.6803 |  | NPV | [5 empty] | 92.2185 | NPV | [5 empty] | 184.43 | NPV | [5 empty] | 228.4031 | NPV | [5 empty] | 109.3656 | 0
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.44115 | 0.008823 | 5.6533 | 0.44997 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.46151 | 0.0092302 | 6.0554 | 0.92071 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 100 | 7.5 | 0.50902 | 0.01018 | 6.9648 | 1.4399 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.0705 | 3.0068 | 0.21071 | 0 | 3.2175 | 2025 | 381.3035 | 63.1967 | 8.7981 | 0.5772 | 0 | 9.3753 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9803 | 3.7591 | 0.25555 | 0 | 4.0147
2026 | 0 | 0 | 0 | 0 | 0 | 1.4399 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 702.047 | 116.0337 | 17.269 | 1.0598 | 0 | 18.3288 |  | 2026 | 191.8124 | 31.3288 | 4.1503 | 0.28614 | 0 | 4.4364 | 2026 | 537.2838 | 88.8184 | 13.2316 | 0.81121 | 0 | 14.0428 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 252.4421 | 41.676 | 6.0458 | 0.38064 | 0 | 6.4264
2027 | 0 | 0 | 0 | 0 | 0 | 1.4399 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 121.8565 | 18.8143 | 1.113 | 0 | 19.9272 |  | 2027 | 230.8453 | 37.7435 | 5.0402 | 0.34472 | 0 | 5.3849 | 2027 | 526.4193 | 87.0328 | 13.6992 | 0.7949 | 0 | 14.4941 | 2027 | 447.9812 | 75.3365 | 11.6185 | 0.68807 | 0 | 12.3066 | 2027 | 273.1168 | 45.3557 | 6.7912 | 0.41425 | 0 | 7.2055
2028 | 0 | 0 | 0 | 0 | 0 | 1.4399 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 137.9532 | 25.2873 | 1.26 | 0 | 26.5472 |  | 2028 | 303.1878 | 49.3823 | 8.0942 | 0.45102 | 0 | 8.5453 | 2028 | 579.9182 | 95.8553 | 18.7508 | 0.87548 | 0 | 19.6263 | 2028 | 657.8397 | 108.5036 | 21.2907 | 0.991 | 0 | 22.2817 | 2028 | 308.7026 | 52.6537 | 9.4428 | 0.4809 | 0 | 9.9237
2029 | 0 | 0 | 0 | 0 | 0 | 1.4399 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 913.6894 | 150.1387 | 30.4348 | 1.3713 | 0 | 31.806 |  | 2029 | 340.8426 | 55.5145 | 9.1535 | 0.50703 | 0 | 9.6605 | 2029 | 539.1028 | 89.1157 | 18.1188 | 0.81392 | 0 | 18.9327 | 2029 | 746.298 | 122.7933 | 25.1233 | 1.1215 | 0 | 26.2448 | 2029 | 355.4457 | 58.4414 | 11.2824 | 0.53377 | 0 | 11.8161
2030 | 0 | 0 | 0 | 0 | 0 | 1.4399 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 960.5408 | 157.3583 | 32.71 | 1.4372 | 0 | 34.1473 |  | 2030 | 387.5876 | 63.0186 | 10.4478 | 0.57557 | 0 | 11.0233 | 2030 | 483.0887 | 79.9069 | 16.693 | 0.72982 | 0 | 17.4228 | 2030 | 787.6516 | 129.436 | 27.2773 | 1.1822 | 0 | 28.4594 | 2030 | 378.1785 | 62.0377 | 12.1949 | 0.56661 | 0 | 12.7615
#REF! | 300 | 20.8 | 1.4117 | 0.028233 | 18.6735 | 18.6735 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5012.7175 | 837.9718 | 145.2896 | 7.6535 | 0 | 396.8412 |  | Total | 1879.2769 | 306.5558 | 45.6518 | 2.7999 | 0 | 123.922 | Total | 3436.3732 | 568.433 | 98.1549 | 5.1917 | 0 | 239.2208 | Total | 3305.5606 | 548.3701 | 100.9042 | 5.0084 | 0 | 329.5838 | Total | 1968.2235 | 327.188 | 54.6065 | 2.9883 | 0 | 147.3423
High Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 14.826 |  | NPV | [5 empty] | 17.9155 | NPV | [5 empty] | 196.4357 |  | NPV | [5 empty] | 62.3202 | NPV | [5 empty] | 125.4044 | NPV | [5 empty] | 150.6823 | NPV | [5 empty] | 73.6467
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.56203 | 0.011241 | 5.9591 | 0.57327 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.58797 | 0.011759 | 6.3402 | 1.173 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 100 | 7.5 | 0.6485 | 0.01297 | 7.1997 | 1.8345 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.0705 | 3.0068 | 0.21071 | 0 | 3.2175 | 2025 | 381.3035 | 63.1967 | 8.7981 | 0.5772 | 0 | 9.3753 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9803 | 3.7591 | 0.25555 | 0 | 4.0147
2026 | 0 | 0 | 0 | 0 | 0 | 1.8345 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 702.047 | 116.0337 | 17.269 | 1.0598 | 0 | 18.3288 |  | 2026 | 191.8124 | 31.3288 | 4.1503 | 0.28614 | 0 | 4.4364 | 2026 | 537.2838 | 88.8184 | 13.2316 | 0.81121 | 0 | 14.0428 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 252.4421 | 41.676 | 6.0458 | 0.38064 | 0 | 6.4264
2027 | 0 | 0 | 0 | 0 | 0 | 1.8345 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 121.8565 | 18.8143 | 1.113 | 0 | 19.9272 |  | 2027 | 230.8453 | 37.7435 | 5.0402 | 0.34472 | 0 | 5.3849 | 2027 | 526.4193 | 87.0328 | 13.6992 | 0.7949 | 0 | 14.4941 | 2027 | 447.9812 | 75.3365 | 11.6185 | 0.68807 | 0 | 12.3066 | 2027 | 273.1168 | 45.3557 | 6.7912 | 0.41425 | 0 | 7.2055
2028 | 0 | 0 | 0 | 0 | 0 | 1.8345 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 137.9532 | 25.2873 | 1.26 | 0 | 26.5472 |  | 2028 | 303.1878 | 49.3823 | 8.0942 | 0.45102 | 0 | 8.5453 | 2028 | 579.9182 | 95.8553 | 18.7508 | 0.87548 | 0 | 19.6263 | 2028 | 657.8397 | 108.5036 | 21.2907 | 0.991 | 0 | 22.2817 | 2028 | 308.7026 | 52.6537 | 9.4428 | 0.4809 | 0 | 9.9237
2029 | 0 | 0 | 0 | 0 | 0 | 1.8345 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 913.6894 | 150.1387 | 30.4348 | 1.3713 | 0 | 31.806 |  | 2029 | 340.8426 | 55.5145 | 9.1535 | 0.50703 | 0 | 9.6605 | 2029 | 539.1028 | 89.1157 | 18.1188 | 0.81392 | 0 | 18.9327 | 2029 | 746.298 | 122.7933 | 25.1233 | 1.1215 | 0 | 26.2448 | 2029 | 355.4457 | 58.4414 | 11.2824 | 0.53377 | 0 | 11.8161
2030 | 0 | 0 | 0 | 0 | 0 | 1.8345 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 960.5408 | 157.3583 | 32.71 | 1.4372 | 0 | 34.1473 |  | 2030 | 387.5876 | 63.0186 | 10.4478 | 0.57557 | 0 | 11.0233 | 2030 | 483.0887 | 79.9069 | 16.693 | 0.72982 | 0 | 17.4228 | 2030 | 787.6516 | 129.436 | 27.2773 | 1.1822 | 0 | 28.4594 | 2030 | 378.1785 | 62.0377 | 12.1949 | 0.56661 | 0 | 12.7615
Total | 300 | 20.8 | 1.7985 | 0.03597 | 19.499 | 19.499 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 28.328 | Total | 5012.7175 | 837.9718 | 145.2896 | 7.6535 | 0 | 325.9945 |  | Total | 1879.2769 | 306.5558 | 45.6518 | 2.7999 | 0 | 102.1593 | Total | 3436.3732 | 568.433 | 98.1549 | 5.1917 | 0 | 196.7466 | Total | 3305.5606 | 548.3701 | 100.9042 | 5.0084 | 0 | 270.9148 | Total | 1968.2235 | 327.188 | 54.6065 | 2.9883 | 0 | 121.2025
Low Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 18.4797 |  | NPV | [5 empty] | 40.4295 | NPV | [5 empty] | 457.4041 |  | NPV | [5 empty] | 143.1039 | NPV | [5 empty] | 284.695 | NPV | [5 empty] | 362.3651 | NPV | [5 empty] | 170.3418
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.32971 | 0.0065941 | 5.2483 | 0.3363 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.34492 | 0.0068984 | 5.6721 | 0.68812 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 100 | 7.5 | 0.38043 | 0.0076086 | 6.6381 | 1.0762 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.0705 | 3.0068 | 0.21071 | 0 | 3.2175 | 2025 | 381.3035 | 63.1967 | 8.7981 | 0.5772 | 0 | 9.3753 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9803 | 3.7591 | 0.25555 | 0 | 4.0147
2026 | 0 | 0 | 0 | 0 | 0 | 1.0762 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 702.047 | 116.0337 | 17.269 | 1.0598 | 0 | 18.3288 |  | 2026 | 191.8124 | 31.3288 | 4.1503 | 0.28614 | 0 | 4.4364 | 2026 | 537.2838 | 88.8184 | 13.2316 | 0.81121 | 0 | 14.0428 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 252.4421 | 41.676 | 6.0458 | 0.38064 | 0 | 6.4264
2027 | 0 | 0 | 0 | 0 | 0 | 1.0762 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 121.8565 | 18.8143 | 1.113 | 0 | 19.9272 |  | 2027 | 230.8453 | 37.7435 | 5.0402 | 0.34472 | 0 | 5.3849 | 2027 | 526.4193 | 87.0328 | 13.6992 | 0.7949 | 0 | 14.4941 | 2027 | 447.9812 | 75.3365 | 11.6185 | 0.68807 | 0 | 12.3066 | 2027 | 273.1168 | 45.3557 | 6.7912 | 0.41425 | 0 | 7.2055
2028 | 0 | 0 | 0 | 0 | 0 | 1.0762 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 137.9532 | 25.2873 | 1.26 | 0 | 26.5472 |  | 2028 | 303.1878 | 49.3823 | 8.0942 | 0.45102 | 0 | 8.5453 | 2028 | 579.9182 | 95.8553 | 18.7508 | 0.87548 | 0 | 19.6263 | 2028 | 657.8397 | 108.5036 | 21.2907 | 0.991 | 0 | 22.2817 | 2028 | 308.7026 | 52.6537 | 9.4428 | 0.4809 | 0 | 9.9237
2029 | 0 | 0 | 0 | 0 | 0 | 1.0762 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 913.6894 | 150.1387 | 30.4348 | 1.3713 | 0 | 31.806 |  | 2029 | 340.8426 | 55.5145 | 9.1535 | 0.50703 | 0 | 9.6605 | 2029 | 539.1028 | 89.1157 | 18.1188 | 0.81392 | 0 | 18.9327 | 2029 | 746.298 | 122.7933 | 25.1233 | 1.1215 | 0 | 26.2448 | 2029 | 355.4457 | 58.4414 | 11.2824 | 0.53377 | 0 | 11.8161
2030 | 0 | 0 | 0 | 0 | 0 | 1.0762 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 960.5408 | 157.3583 | 32.71 | 1.4372 | 0 | 34.1473 |  | 2030 | 387.5876 | 63.0186 | 10.4478 | 0.57557 | 0 | 11.0233 | 2030 | 483.0887 | 79.9069 | 16.693 | 0.72982 | 0 | 17.4228 | 2030 | 787.6516 | 129.436 | 27.2773 | 1.1822 | 0 | 28.4594 | 2030 | 378.1785 | 62.0377 | 12.1949 | 0.56661 | 0 | 12.7615
Total | 300 | 20.8 | 1.0551 | 0.021101 | 17.5585 | 17.5585 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 42.7177 | Total | 5012.7175 | 837.9718 | 145.2896 | 7.6535 | 0 | 497.7443 |  | Total | 1879.2769 | 306.5558 | 45.6518 | 2.7999 | 0 | 154.687 | Total | 3436.3732 | 568.433 | 98.1549 | 5.1917 | 0 | 299.5649 | Total | 3305.5606 | 548.3701 | 100.9042 | 5.0084 | 0 | 413.034 |  | 1968.2235 | 327.188 | 54.6065 | 2.9883 | 0 | 184.4667
High Cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 21.477 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 292.6803 |  | NPV | [5 empty] | 92.2185 | NPV | [5 empty] | 184.43 | NPV | [5 empty] | 228.4031 | NPV | [5 empty] | 109.3656
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 8.45 | 0.57349 | 0.01147 | 7.3492 | 0.58496 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 8.84 | 0.59996 | 0.011999 | 7.8721 | 1.1969 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 100 | 9.75 | 0.66172 | 0.013234 | 9.0542 | 1.8719 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.0705 | 3.0068 | 0.21071 | 0 | 3.2175 | 2025 | 381.3035 | 63.1967 | 8.7981 | 0.5772 | 0 | 9.3753 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9803 | 3.7591 | 0.25555 | 0 | 4.0147
2026 | 0 | 0 | 0 | 0 | 0 | 1.8719 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 702.047 | 116.0337 | 17.269 | 1.0598 | 0 | 18.3288 |  | 2026 | 191.8124 | 31.3288 | 4.1503 | 0.28614 | 0 | 4.4364 | 2026 | 537.2838 | 88.8184 | 13.2316 | 0.81121 | 0 | 14.0428 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 252.4421 | 41.676 | 6.0458 | 0.38064 | 0 | 6.4264
2027 | 0 | 0 | 0 | 0 | 0 | 1.8719 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 121.8565 | 18.8143 | 1.113 | 0 | 19.9272 |  | 2027 | 230.8453 | 37.7435 | 5.0402 | 0.34472 | 0 | 5.3849 | 2027 | 526.4193 | 87.0328 | 13.6992 | 0.7949 | 0 | 14.4941 | 2027 | 447.9812 | 75.3365 | 11.6185 | 0.68807 | 0 | 12.3066 | 2027 | 273.1168 | 45.3557 | 6.7912 | 0.41425 | 0 | 7.2055
2028 | 0 | 0 | 0 | 0 | 0 | 1.8719 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 137.9532 | 25.2873 | 1.26 | 0 | 26.5472 |  | 2028 | 303.1878 | 49.3823 | 8.0942 | 0.45102 | 0 | 8.5453 | 2028 | 579.9182 | 95.8553 | 18.7508 | 0.87548 | 0 | 19.6263 | 2028 | 657.8397 | 108.5036 | 21.2907 | 0.991 | 0 | 22.2817 | 2028 | 308.7026 | 52.6537 | 9.4428 | 0.4809 | 0 | 9.9237
2029 | 0 | 0 | 0 | 0 | 0 | 1.8719 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 913.6894 | 150.1387 | 30.4348 | 1.3713 | 0 | 31.806 |  | 2029 | 340.8426 | 55.5145 | 9.1535 | 0.50703 | 0 | 9.6605 | 2029 | 539.1028 | 89.1157 | 18.1188 | 0.81392 | 0 | 18.9327 | 2029 | 746.298 | 122.7933 | 25.1233 | 1.1215 | 0 | 26.2448 | 2029 | 355.4457 | 58.4414 | 11.2824 | 0.53377 | 0 | 11.8161
2030 | 0 | 0 | 0 | 0 | 0 | 1.8719 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 960.5408 | 157.3583 | 32.71 | 1.4372 | 0 | 34.1473 |  | 2030 | 387.5876 | 63.0186 | 10.4478 | 0.57557 | 0 | 11.0233 | 2030 | 483.0887 | 79.9069 | 16.693 | 0.72982 | 0 | 17.4228 | 2030 | 787.6516 | 129.436 | 27.2773 | 1.1822 | 0 | 28.4594 | 2030 | 378.1785 | 62.0377 | 12.1949 | 0.56661 | 0 | 12.7615
Total | 300 | 27.04 | 1.8352 | 0.036704 | 24.2755 | 24.2755 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5012.7175 | 837.9718 | 145.2896 | 7.6535 | 0 | 396.8412 |  | Total | 1879.2769 | 306.5558 | 45.6518 | 2.7999 | 0 | 123.922 | Total | 3436.3732 | 568.433 | 98.1549 | 5.1917 | 0 | 239.2208 | Total | 3305.5606 | 548.3701 | 100.9042 | 5.0084 | 0 | 329.5838 | Total | 1968.2235 | 327.188 | 54.6065 | 2.9883 | 0 | 147.3423
Low cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 11.5645 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 292.6803 |  | NPV | [5 empty] | 92.2185 | NPV | [5 empty] | 184.43 | NPV | [5 empty] | 228.4031 | NPV | [5 empty] | 109.3656
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 4.55 | 0.3088 | 0.0061761 | 3.9573 | 0.31498 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 4.76 | 0.32306 | 0.0064611 | 4.2388 | 0.6445 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 100 | 5.25 | 0.35631 | 0.0071262 | 4.8754 | 1.0079 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.0705 | 3.0068 | 0.21071 | 0 | 3.2175 | 2025 | 381.3035 | 63.1967 | 8.7981 | 0.5772 | 0 | 9.3753 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9803 | 3.7591 | 0.25555 | 0 | 4.0147
2026 | 0 | 0 | 0 | 0 | 0 | 1.0079 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 702.047 | 116.0337 | 17.269 | 1.0598 | 0 | 18.3288 |  | 2026 | 191.8124 | 31.3288 | 4.1503 | 0.28614 | 0 | 4.4364 | 2026 | 537.2838 | 88.8184 | 13.2316 | 0.81121 | 0 | 14.0428 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 252.4421 | 41.676 | 6.0458 | 0.38064 | 0 | 6.4264
2027 | 0 | 0 | 0 | 0 | 0 | 1.0079 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 121.8565 | 18.8143 | 1.113 | 0 | 19.9272 |  | 2027 | 230.8453 | 37.7435 | 5.0402 | 0.34472 | 0 | 5.3849 | 2027 | 526.4193 | 87.0328 | 13.6992 | 0.7949 | 0 | 14.4941 | 2027 | 447.9812 | 75.3365 | 11.6185 | 0.68807 | 0 | 12.3066 | 2027 | 273.1168 | 45.3557 | 6.7912 | 0.41425 | 0 | 7.2055
2028 | 0 | 0 | 0 | 0 | 0 | 1.0079 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 137.9532 | 25.2873 | 1.26 | 0 | 26.5472 |  | 2028 | 303.1878 | 49.3823 | 8.0942 | 0.45102 | 0 | 8.5453 | 2028 | 579.9182 | 95.8553 | 18.7508 | 0.87548 | 0 | 19.6263 | 2028 | 657.8397 | 108.5036 | 21.2907 | 0.991 | 0 | 22.2817 | 2028 | 308.7026 | 52.6537 | 9.4428 | 0.4809 | 0 | 9.9237
2029 | 0 | 0 | 0 | 0 | 0 | 1.0079 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 913.6894 | 150.1387 | 30.4348 | 1.3713 | 0 | 31.806 |  | 2029 | 340.8426 | 55.5145 | 9.1535 | 0.50703 | 0 | 9.6605 | 2029 | 539.1028 | 89.1157 | 18.1188 | 0.81392 | 0 | 18.9327 | 2029 | 746.298 | 122.7933 | 25.1233 | 1.1215 | 0 | 26.2448 | 2029 | 355.4457 | 58.4414 | 11.2824 | 0.53377 | 0 | 11.8161
2030 | 0 | 0 | 0 | 0 | 0 | 1.0079 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 960.5408 | 157.3583 | 32.71 | 1.4372 | 0 | 34.1473 |  | 2030 | 387.5876 | 63.0186 | 10.4478 | 0.57557 | 0 | 11.0233 | 2030 | 483.0887 | 79.9069 | 16.693 | 0.72982 | 0 | 17.4228 | 2030 | 787.6516 | 129.436 | 27.2773 | 1.1822 | 0 | 28.4594 | 2030 | 378.1785 | 62.0377 | 12.1949 | 0.56661 | 0 | 12.7615
Total | 300 | 14.56 | 0.98817 | 0.019763 | 13.0714 | 13.0714 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5012.7175 | 837.9718 | 145.2896 | 7.6535 | 0 | 396.8412 |  | Total | 1879.2769 | 306.5558 | 45.6518 | 2.7999 | 0 | 123.922 | Total | 3436.3732 | 568.433 | 98.1549 | 5.1917 | 0 | 239.2208 | Total | 3305.5606 | 548.3701 | 100.9042 | 5.0084 | 0 | 329.5838 | Total | 1968.2235 | 327.188 | 54.6065 | 2.9883 | 0 | 147.3423

## Option 1C
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M |  | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change |  | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change
Base | 5.9% | 100% | 28.3 | 21.9444 | 4.3375 | 282.189 | 71.0422 | 171.1115 | 227.7798 | 90.4765 | 117.9977 | 151.292 | 62.7072 |  | 26.2818 | 304.1333 | 92.9866 | 193.0559 | 249.7242 | 112.4209 | 139.7226 | 173.2364 | 84.6515
High Discount rate | 8.6% | 100% | 28.3 | 19.4892 | -1.5737 | 184.2059 | 43.3198 | 111.7291 | 144.6821 | 56.0946 | 74.5642 | 96.4727 | 37.9754 |  | 17.9155 | 203.6951 | 62.809 | 131.2183 | 164.1713 | 75.5838 | 93.8585 | 115.9618 | 57.4646
Low Discount rate | 3.2% | 100% | 28.3 | 24.8123 | 15.6172 | 451.5155 | 119.5568 | 273.3682 | 372.8401 | 150.5766 | 193.6075 | 246.5795 | 106.0398 |  | 40.4295 | 476.3278 | 144.3691 | 298.1805 | 397.6524 | 175.389 | 218.1717 | 271.3919 | 130.8522
High Cost | 5.9% | 130% | 28.3 | 28.5277 | -2.2458 | 275.6057 | 64.4589 | 164.5282 | 221.1965 | 83.8932 | 111.4802 | 144.7087 | 56.1239 |  | 26.2818 | 304.1333 | 92.9866 | 193.0559 | 249.7242 | 112.4209 | 139.7226 | 173.2364 | 84.6515
Low Cost | 5.9% | 70% | 28.3 | 15.361 | 10.9208 | 288.7723 | 77.6255 | 177.6948 | 234.3631 | 97.0598 | 124.5151 | 157.8753 | 69.2905 |  | 26.2818 | 304.1333 | 92.9866 | 193.0559 | 249.7242 | 112.4209 | 139.7226 | 173.2364 | 84.6515
Base
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Base Weighted
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 21.9444 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 304.1333 |  | NPV | [5 empty] | 92.9866 | NPV | [5 empty] | 193.0559 | NPV | [5 empty] | 249.7242 | NPV | [5 empty] | 112.4209 | 0
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.44115 | 0.008823 | 5.6533 | 0.44997 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.46151 | 0.0092302 | 6.0554 | 0.92071 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 15 | 1.018 | 0.020361 | 13.9296 | 1.9591 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 1.9591 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.7671 | 14.3293 | 0.88381 | 0 | 15.2131 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 1.9591 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 1.9591 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 1.9591 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 140.2108 | 27.957 | 1.2806 | 0 | 29.2376 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 1.9591 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 188.2472 | 34.8546 | 1.7193 | 0 | 36.5739 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 150.3808 | 31.46 | 1.3735 | 0 | 32.8335 | 2030 | 395.7183 | 70.0661 | 12.7619 | 0.63994 | 0 | 13.4018
Total | 400 | 28.3 | 1.9207 | 0.038414 | 25.6383 | 25.6383 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5126.4893 | 909.7325 | 148.8378 | 8.3089 | 0 | 415.0386 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 125.1323 | Total | 3602.4118 | 604.0987 | 102.811 | 5.5174 | 0 | 250.2956 | Total | 3519.4339 | 592.1634 | 108.1407 | 5.4084 | 0 | 363.6934 | Total | 1999.2733 | 345.9121 | 55.5579 | 3.1593 | 0 | 152.1942
High Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 19.4892 |  | NPV | [5 empty] | 17.9155 | NPV | [5 empty] | 203.6951 |  | NPV | [5 empty] | 62.809 | NPV | [5 empty] | 131.2183 | NPV | [5 empty] | 164.1713 | NPV | [5 empty] | 75.5838
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.56203 | 0.011241 | 5.9591 | 0.57327 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.58797 | 0.011759 | 6.3402 | 1.173 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 15 | 1.297 | 0.02594 | 14.3995 | 2.4959 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 2.4959 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.7671 | 14.3293 | 0.88381 | 0 | 15.2131 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 2.4959 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 2.4959 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 2.4959 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 140.2108 | 27.957 | 1.2806 | 0 | 29.2376 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 2.4959 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 188.2472 | 34.8546 | 1.7193 | 0 | 36.5739 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 150.3808 | 31.46 | 1.3735 | 0 | 32.8335 | 2030 | 395.7183 | 70.0661 | 12.7619 | 0.63994 | 0 | 13.4018
Total | 400 | 28.3 | 2.447 | 0.04894 | 26.6987 | 26.6987 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 28.328 | Total | 5126.4893 | 909.7325 | 148.8378 | 8.3089 | 0 | 340.7598 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 103.1413 | Total | 3602.4118 | 604.0987 | 102.811 | 5.5174 | 0 | 205.7326 | Total | 3519.4339 | 592.1634 | 108.1407 | 5.4084 | 0 | 298.5911 | Total | 1999.2733 | 345.9121 | 55.5579 | 3.1593 | 0 | 125.1393
Low Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 24.8123 |  | NPV | [5 empty] | 40.4295 | NPV | [5 empty] | 476.3278 |  | NPV | [5 empty] | 144.3691 | NPV | [5 empty] | 298.1805 | NPV | [5 empty] | 397.6524 | NPV | [5 empty] | 175.389
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.32971 | 0.0065941 | 5.2483 | 0.3363 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.34492 | 0.0068984 | 5.6721 | 0.68812 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 15 | 0.76086 | 0.015217 | 13.2762 | 1.4642 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 1.4642 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.7671 | 14.3293 | 0.88381 | 0 | 15.2131 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 1.4642 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 1.4642 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 1.4642 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 140.2108 | 27.957 | 1.2806 | 0 | 29.2376 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 1.4642 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 188.2472 | 34.8546 | 1.7193 | 0 | 36.5739 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 150.3808 | 31.46 | 1.3735 | 0 | 32.8335 | 2030 | 395.7183 | 70.0661 | 12.7619 | 0.63994 | 0 | 13.4018
Total | 400 | 28.3 | 1.4355 | 0.02871 | 24.1966 | 24.1966 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 42.7177 | Total | 5126.4893 | 909.7325 | 148.8378 | 8.3089 | 0 | 520.9504 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 156.2305 | Total | 3602.4118 | 604.0987 | 102.811 | 5.5174 | 0 | 313.688 | Total | 3519.4339 | 592.1634 | 108.1407 | 5.4084 | 0 | 456.5321 |  | 1999.2733 | 345.9121 | 55.5579 | 3.1593 | 0 | 190.6541
High Cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 28.5277 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 304.1333 |  | NPV | [5 empty] | 92.9866 | NPV | [5 empty] | 193.0559 | NPV | [5 empty] | 249.7242 | NPV | [5 empty] | 112.4209
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 8.45 | 0.57349 | 0.01147 | 7.3492 | 0.58496 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 8.84 | 0.59996 | 0.011999 | 7.8721 | 1.1969 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 19.5 | 1.3234 | 0.026469 | 18.1085 | 2.5468 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 2.5468 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.7671 | 14.3293 | 0.88381 | 0 | 15.2131 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 2.5468 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 2.5468 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 2.5468 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 140.2108 | 27.957 | 1.2806 | 0 | 29.2376 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 2.5468 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 188.2472 | 34.8546 | 1.7193 | 0 | 36.5739 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 150.3808 | 31.46 | 1.3735 | 0 | 32.8335 | 2030 | 395.7183 | 70.0661 | 12.7619 | 0.63994 | 0 | 13.4018
Total | 400 | 36.79 | 2.4969 | 0.049938 | 33.3298 | 33.3298 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5126.4893 | 909.7325 | 148.8378 | 8.3089 | 0 | 415.0386 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 125.1323 | Total | 3602.4118 | 604.0987 | 102.811 | 5.5174 | 0 | 250.2956 | Total | 3519.4339 | 592.1634 | 108.1407 | 5.4084 | 0 | 363.6934 | Total | 1999.2733 | 345.9121 | 55.5579 | 3.1593 | 0 | 152.1942
Low cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 15.361 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 304.1333 |  | NPV | [5 empty] | 92.9866 | NPV | [5 empty] | 193.0559 | NPV | [5 empty] | 249.7242 | NPV | [5 empty] | 112.4209
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 4.55 | 0.3088 | 0.0061761 | 3.9573 | 0.31498 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 4.76 | 0.32306 | 0.0064611 | 4.2388 | 0.6445 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 10.5 | 0.71262 | 0.014252 | 9.7507 | 1.3714 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 1.3714 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.7671 | 14.3293 | 0.88381 | 0 | 15.2131 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 1.3714 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 1.3714 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 1.3714 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 140.2108 | 27.957 | 1.2806 | 0 | 29.2376 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 1.3714 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 188.2472 | 34.8546 | 1.7193 | 0 | 36.5739 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 150.3808 | 31.46 | 1.3735 | 0 | 32.8335 | 2030 | 395.7183 | 70.0661 | 12.7619 | 0.63994 | 0 | 13.4018
Total | 400 | 19.81 | 1.3445 | 0.02689 | 17.9468 | 17.9468 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5126.4893 | 909.7325 | 148.8378 | 8.3089 | 0 | 415.0386 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 125.1323 | Total | 3602.4118 | 604.0987 | 102.811 | 5.5174 | 0 | 250.2956 | Total | 3519.4339 | 592.1634 | 108.1407 | 5.4084 | 0 | 363.6934 | Total | 1999.2733 | 345.9121 | 55.5579 | 3.1593 | 0 | 152.1942

## Option 1D
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M |  | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change |  | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change
Base | 5.9% | 100% | 35.8 | 27.3679 | -1.0861 | 276.8156 | 65.6186 | 165.6888 | 222.5362 | 85.0655 | 112.6449 | 145.9146 | 57.2838 |  | 26.2818 | 304.1835 | 92.9866 | 193.0567 | 249.9041 | 112.4334 | 139.7391 | 173.2826 | 84.6517
High Discount rate | 8.6% | 100% | 35.8 | 24.1523 | -6.2369 | 179.5744 | 38.6567 | 107.0666 | 140.1326 | 51.4393 | 69.9581 | 91.8387 | 33.3124 |  | 17.9155 | 203.7267 | 62.809 | 131.219 | 164.2849 | 75.5917 | 93.8689 | 115.991 | 57.4647
Low Discount rate | 3.2% | 100% | 35.8 | 31.1449 | 9.2846 | 445.2662 | 113.2242 | 267.0366 | 366.8058 | 144.2649 | 187.3657 | 240.3235 | 99.7075 |  | 40.4295 | 476.4111 | 144.3691 | 298.1815 | 397.9507 | 175.4098 | 218.1992 | 271.4684 | 130.8524
High Cost | 5.9% | 130% | 35.8 | 35.5783 | -9.2965 | 268.6052 | 57.4083 | 157.4784 | 214.3258 | 76.8551 | 104.5166 | 137.7042 | 49.0734 |  | 26.2818 | 304.1835 | 92.9866 | 193.0567 | 249.9041 | 112.4334 | 139.7391 | 173.2826 | 84.6517
Low Cost | 5.9% | 70% | 35.8 | 19.1576 | 7.1243 | 285.026 | 73.829 | 173.8992 | 230.7466 | 93.2759 | 120.7732 | 154.125 | 65.4942 |  | 26.2818 | 304.1835 | 92.9866 | 193.0567 | 249.9041 | 112.4334 | 139.7391 | 173.2826 | 84.6517
Base
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Base Weighted
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 27.3679 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 304.1835 |  | NPV | [5 empty] | 92.9866 | NPV | [5 empty] | 193.0567 | NPV | [5 empty] | 249.9041 | NPV | [5 empty] | 112.4334 | 0
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.44115 | 0.008823 | 5.6533 | 0.44997 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.46151 | 0.0092302 | 6.0554 | 0.92071 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 300 | 22.5 | 1.5271 | 0.030541 | 20.8944 | 2.4783 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 2.4783 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.9024 | 14.3293 | 0.88504 | 0 | 15.2143 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 2.4783 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 2.4783 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 2.4783 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 141.8208 | 27.957 | 1.2953 | 0 | 29.2523 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 2.4783 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 190.224 | 34.8546 | 1.7374 | 0 | 36.592 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 155.8408 | 31.46 | 1.4233 | 0 | 32.8833 | 2030 | 395.7183 | 70.5603 | 12.7619 | 0.64445 | 0 | 13.4063
Total | 500 | 35.8 | 2.4297 | 0.048594 | 32.6031 | 32.6031 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5126.4893 | 911.7093 | 148.8378 | 8.3269 | 0 | 415.1193 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 125.1323 | Total | 3602.4118 | 604.2341 | 102.811 | 5.5187 | 0 | 250.2956 | Total | 3519.4339 | 599.2334 | 108.1407 | 5.473 | 0 | 363.9821 | Total | 1999.2733 | 346.4063 | 55.5579 | 3.1638 | 0 | 152.2144
High Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 24.1523 |  | NPV | [5 empty] | 17.9155 | NPV | [5 empty] | 203.7267 |  | NPV | [5 empty] | 62.809 | NPV | [5 empty] | 131.219 | NPV | [5 empty] | 164.2849 | NPV | [5 empty] | 75.5917
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.56203 | 0.011241 | 5.9591 | 0.57327 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.58797 | 0.011759 | 6.3402 | 1.173 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 300 | 22.5 | 1.9455 | 0.03891 | 21.5992 | 3.1574 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 3.1574 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.9024 | 14.3293 | 0.88504 | 0 | 15.2143 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 3.1574 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 3.1574 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 3.1574 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 141.8208 | 27.957 | 1.2953 | 0 | 29.2523 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 3.1574 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 190.224 | 34.8546 | 1.7374 | 0 | 36.592 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 155.8408 | 31.46 | 1.4233 | 0 | 32.8833 | 2030 | 395.7183 | 70.5603 | 12.7619 | 0.64445 | 0 | 13.4063
Total | 500 | 35.8 | 3.0955 | 0.06191 | 33.8985 | 33.8985 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 28.328 | Total | 5126.4893 | 911.7093 | 148.8378 | 8.3269 | 0 | 340.8253 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 103.1413 | Total | 3602.4118 | 604.2341 | 102.811 | 5.5187 | 0 | 205.7326 | Total | 3519.4339 | 599.2334 | 108.1407 | 5.473 | 0 | 298.8254 | Total | 1999.2733 | 346.4063 | 55.5579 | 3.1638 | 0 | 125.1557
Low Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 31.1449 |  | NPV | [5 empty] | 40.4295 | NPV | [5 empty] | 476.4111 |  | NPV | [5 empty] | 144.3691 | NPV | [5 empty] | 298.1815 | NPV | [5 empty] | 397.9507 | NPV | [5 empty] | 175.4098
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.32971 | 0.0065941 | 5.2483 | 0.3363 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.34492 | 0.0068984 | 5.6721 | 0.68812 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 300 | 22.5 | 1.1413 | 0.022826 | 19.9143 | 1.8522 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 1.8522 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.9024 | 14.3293 | 0.88504 | 0 | 15.2143 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 1.8522 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 1.8522 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 1.8522 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 141.8208 | 27.957 | 1.2953 | 0 | 29.2523 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 1.8522 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 190.224 | 34.8546 | 1.7374 | 0 | 36.592 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 155.8408 | 31.46 | 1.4233 | 0 | 32.8833 | 2030 | 395.7183 | 70.5603 | 12.7619 | 0.64445 | 0 | 13.4063
Total | 500 | 35.8 | 1.8159 | 0.036318 | 30.8347 | 30.8347 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 42.7177 | Total | 5126.4893 | 911.7093 | 148.8378 | 8.3269 | 0 | 521.0534 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 156.2305 | Total | 3602.4118 | 604.2341 | 102.811 | 5.5187 | 0 | 313.688 | Total | 3519.4339 | 599.2334 | 108.1407 | 5.473 | 0 | 456.9003 |  | 1999.2733 | 346.4063 | 55.5579 | 3.1638 | 0 | 190.6798
High Cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 35.5783 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 304.1835 |  | NPV | [5 empty] | 92.9866 | NPV | [5 empty] | 193.0567 | NPV | [5 empty] | 249.9041 | NPV | [5 empty] | 112.4334
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 8.45 | 0.57349 | 0.01147 | 7.3492 | 0.58496 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 8.84 | 0.59996 | 0.011999 | 7.8721 | 1.1969 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 300 | 29.25 | 1.9852 | 0.039703 | 27.1627 | 3.2218 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 3.2218 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.9024 | 14.3293 | 0.88504 | 0 | 15.2143 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 3.2218 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 3.2218 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 3.2218 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 141.8208 | 27.957 | 1.2953 | 0 | 29.2523 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 3.2218 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 190.224 | 34.8546 | 1.7374 | 0 | 36.592 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 155.8408 | 31.46 | 1.4233 | 0 | 32.8833 | 2030 | 395.7183 | 70.5603 | 12.7619 | 0.64445 | 0 | 13.4063
Total | 500 | 46.54 | 3.1586 | 0.063172 | 42.384 | 42.384 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5126.4893 | 911.7093 | 148.8378 | 8.3269 | 0 | 415.1193 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 125.1323 | Total | 3602.4118 | 604.2341 | 102.811 | 5.5187 | 0 | 250.2956 | Total | 3519.4339 | 599.2334 | 108.1407 | 5.473 | 0 | 363.9821 | Total | 1999.2733 | 346.4063 | 55.5579 | 3.1638 | 0 | 152.2144
Low cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 19.1576 |  | NPV | [5 empty] | 26.2818 | NPV | [5 empty] | 304.1835 |  | NPV | [5 empty] | 92.9866 | NPV | [5 empty] | 193.0567 | NPV | [5 empty] | 249.9041 | NPV | [5 empty] | 112.4334
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 4.55 | 0.3088 | 0.0061761 | 3.9573 | 0.31498 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 4.76 | 0.32306 | 0.0064611 | 4.2388 | 0.6445 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 300 | 15.75 | 1.0689 | 0.021379 | 14.6261 | 1.7348 |  | 2025 | 45.2874 | 7.5418 | 1.013 | 0.068882 | 0 | 1.0819 | 2025 | 434.6132 | 73.7671 | 10.0036 | 0.67374 | 0 | 10.6773 |  | 2025 | 140.6005 | 23.1194 | 3.0068 | 0.21116 | 0 | 3.218 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | 0 | 9.6545 | 2025 | 160.7512 | 27.0875 | 3.6453 | 0.2474 | 0 | 3.8927 | 2025 | 166.4471 | 27.9925 | 3.7591 | 0.25567 | 0 | 4.0148
2026 | 0 | 0 | 0 | 0 | 0 | 1.7348 |  | 2026 | 57.9546 | 9.6707 | 1.3819 | 0.088326 | 0 | 1.4702 | 2026 | 706.3006 | 121.2229 | 17.2935 | 1.1072 | 0 | 18.4007 |  | 2026 | 192.2572 | 31.5089 | 4.1564 | 0.28778 | 0 | 4.4442 | 2026 | 582.2536 | 96.9024 | 14.3293 | 0.88504 | 0 | 15.2143 | 2026 | 329.1051 | 55.7003 | 8.0394 | 0.50873 | 0 | 8.5481 | 2026 | 253.6167 | 43.0183 | 6.0534 | 0.3929 | 0 | 6.4463
2027 | 0 | 0 | 0 | 0 | 0 | 1.7348 |  | 2027 | 65.2694 | 10.9114 | 1.6552 | 0.099657 | 0 | 1.7549 | 2027 | 731.0832 | 128.6545 | 18.8143 | 1.175 | 0 | 19.9893 |  | 2027 | 231.228 | 37.9889 | 5.0448 | 0.34696 | 0 | 5.3918 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0 | 15.5497 | 2027 | 447.9812 | 76.2414 | 11.6185 | 0.69634 | 0 | 12.3149 | 2027 | 273.2125 | 47.1165 | 6.7924 | 0.43033 | 0 | 7.2227
2028 | 0 | 0 | 0 | 0 | 0 | 1.7348 |  | 2028 | 69.3929 | 11.6396 | 2.1948 | 0.10631 | 0 | 2.3011 | 2028 | 792.8368 | 142.1618 | 25.2873 | 1.2984 | 0 | 26.5857 |  | 2028 | 304.8778 | 49.9271 | 8.1351 | 0.456 | 0 | 8.5911 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | 0 | 20.5388 | 2028 | 665.5766 | 113.0298 | 21.5107 | 1.0323 | 0 | 22.5431 | 2028 | 309.1251 | 53.8421 | 9.453 | 0.49176 | 0 | 9.9448
2029 | 0 | 0 | 0 | 0 | 0 | 1.7348 |  | 2029 | 83.6253 | 14.0563 | 2.7706 | 0.12838 | 0 | 2.899 | 2029 | 957.7658 | 174.8146 | 31.8139 | 1.5966 | 0 | 33.4105 |  | 2029 | 344.0352 | 56.4061 | 9.2354 | 0.51518 | 0 | 9.7506 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0 | 19.9926 | 2029 | 831.0742 | 141.8208 | 27.957 | 1.2953 | 0 | 29.2523 | 2029 | 367.2629 | 64.8333 | 11.6476 | 0.59214 | 0 | 12.2398
2030 | 0 | 0 | 0 | 0 | 0 | 1.7348 |  | 2030 | 82.2928 | 13.8869 | 2.8108 | 0.12683 | 0 | 2.9377 | 2030 | 1025.9827 | 190.224 | 34.8546 | 1.7374 | 0 | 36.592 |  | 2030 | 392.3049 | 64.2433 | 10.5713 | 0.58676 | 0 | 11.158 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0 | 17.9271 | 2030 | 909.0117 | 155.8408 | 31.46 | 1.4233 | 0 | 32.8833 | 2030 | 395.7183 | 70.5603 | 12.7619 | 0.64445 | 0 | 13.4063
Total | 500 | 25.06 | 1.7008 | 0.034016 | 22.8222 | 22.8222 |  | Total | 490.4498 | 82.1123 | 13.7424 | 0.74996 | 0 | 34.303 | Total | 5126.4893 | 911.7093 | 148.8378 | 8.3269 | 0 | 415.1193 |  | Total | 1889.7042 | 309.6913 | 45.9089 | 2.8285 | 0 | 125.1323 | Total | 3602.4118 | 604.2341 | 102.811 | 5.5187 | 0 | 250.2956 | Total | 3519.4339 | 599.2334 | 108.1407 | 5.473 | 0 | 363.9821 | Total | 1999.2733 | 346.4063 | 55.5579 | 3.1638 | 0 | 152.2144

## Option 2
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M |  | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M | Gross Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change |  | Central | Step Change | Slow change | Fast change | High DER | Base_Weighting | Equal_Weighting | Equal_ISP | Excluding Step Change
Base | 5.9% | 100% | 90.7 | 67.0685 | -35.8258 | 279.5066 | 34.2114 | 123.6015 | 188.1238 | 60.5166 | 91.7044 | 117.9235 | 21.5403 |  | 31.2427 | 346.5751 | 101.2799 | 190.67 | 255.1923 | 127.5851 | 158.1022 | 184.992 | 88.6088
High Discount rate | 8.6% | 100% | 90.7 | 58.2868 | -36.8465 | 173.52 | 10.2458 | 71.3942 | 109.696 | 27.5182 | 48.4834 | 65.6019 | 1.9867 |  | 21.4403 | 231.8069 | 68.5327 | 129.681 | 167.9828 | 85.805 | 106.1873 | 123.8887 | 60.2736
Low Discount rate | 3.2% | 100% | 90.7 | 77.4997 | -29.7089 | 466.3021 | 79.5742 | 216.7834 | 328.4178 | 121.6146 | 170.3352 | 212.2737 | 59.2349 |  | 47.7908 | 543.8018 | 157.0739 | 294.2831 | 405.9175 | 199.1143 | 247.0599 | 289.7734 | 136.7346
High Cost | 5.9% | 130% | 90.7 | 87.1891 | -55.9463 | 259.3861 | 14.0908 | 103.4809 | 168.0032 | 40.3961 | 71.7851 | 97.8029 | 1.4198 |  | 31.2427 | 346.5751 | 101.2799 | 190.67 | 255.1923 | 127.5851 | 158.1022 | 184.992 | 88.6088
Low Cost | 5.9% | 70% | 90.7 | 46.948 | -15.7052 | 299.6272 | 54.3319 | 143.722 | 208.2443 | 80.6372 | 111.6238 | 138.044 | 41.6609 |  | 31.2427 | 346.5751 | 101.2799 | 190.67 | 255.1923 | 127.5851 | 158.1022 | 184.992 | 88.6088
Base
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Base Weighted
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 67.0685 |  | NPV | [5 empty] | 31.2427 | NPV | [5 empty] | 346.5751 |  | NPV | [5 empty] | 101.2799 | NPV | [5 empty] | 190.67 | NPV | [5 empty] | 255.1923 | NPV | [5 empty] | 127.5851 | 0
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.44115 | 0.008823 | 5.6533 | 0.44997 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.46151 | 0.0092302 | 6.0554 | 0.92071 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.92071 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 77.4 | 5.2531 | 0.10506 | 71.8767 | 6.2788 |  | 2025 | 45.9832 | 7.6466 | 1.0296 | 0.069839 | 1.3679 | 2.4674 | 2025 | 529.8255 | 87.8839 | 12.2978 | 0.80267 | -0.029215 | 13.0713 |  | 2025 | 142.0475 | 23.311 | 3.0397 | 0.21291 | 1.8745 | 5.1272 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | -0.029215 | 9.6253 | 2025 | 181.4473 | 30.1242 | 4.1411 | 0.27513 | -0.029215 | 4.3871 | 2025 | 190.9599 | 31.622 | 4.3492 | 0.28881 | 1.1453 | 5.7833
2026 | 0 | 0 | 0 | 0 | 0 | 6.2788 |  | 2026 | 59.1861 | 9.8407 | 1.413 | 0.089879 | 0.49165 | 1.9945 | 2026 | 803.5445 | 132.9423 | 19.7759 | 1.2142 | -0.056586 | 20.9335 |  | 2026 | 194.4207 | 31.7635 | 4.2057 | 0.29011 | 1.4559 | 5.9517 | 2026 | 582.2536 | 96.6578 | 14.3293 | 0.88281 | -0.056586 | 15.1555 | 2026 | 362.2541 | 60.0821 | 8.8799 | 0.54875 | -0.056586 | 9.3721 | 2026 | 279.0843 | 46.0968 | 6.7019 | 0.42102 | 0.59565 | 7.7186
2027 | 0 | 0 | 0 | 0 | 0 | 6.2788 |  | 2027 | 67.1291 | 11.1561 | 1.7046 | 0.10189 | 0.75079 | 2.5573 | 2027 | 853.1373 | 141.057 | 22.0689 | 1.2883 | 0.12707 | 23.4843 |  | 2027 | 233.9871 | 38.2671 | 5.1077 | 0.34951 | -0.67469 | 4.7825 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0.12707 | 15.6768 | 2027 | 488.9922 | 80.9615 | 12.7145 | 0.73945 | 0.12707 | 13.581 | 2027 | 305.3456 | 50.4091 | 7.6465 | 0.4604 | 0.23849 | 8.3454
2028 | 0 | 0 | 0 | 0 | 0 | 6.2788 |  | 2028 | 71.8565 | 11.9442 | 2.2756 | 0.10909 | -0.047026 | 2.3376 | 2028 | 967.6027 | 159.8142 | 30.9959 | 1.4596 | -1.2839 | 31.1716 |  | 2028 | 308.2493 | 50.2259 | 8.2279 | 0.45873 | 0.94619 | 9.6328 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | -1.2839 | 19.2549 | 2028 | 710.0415 | 117.2009 | 22.979 | 1.0704 | -1.2839 | 22.7655 | 2028 | 354.8912 | 58.4821 | 10.9437 | 0.53414 | -0.10795 | 11.3699
2029 | 0 | 0 | 0 | 0 | 0 | 6.2788 |  | 2029 | 86.7119 | 14.4068 | 2.8755 | 0.13158 | 0.15092 | 3.158 | 2029 | 1077.0558 | 177.308 | 35.8867 | 1.6194 | 0.30349 | 37.8096 |  | 2029 | 348.0053 | 56.7083 | 9.3446 | 0.51794 | 0.96003 | 10.8226 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0.30349 | 20.2961 | 2029 | 848.2091 | 139.7638 | 28.5601 | 1.2765 | 0.30349 | 30.1401 | 2029 | 399.6212 | 65.7075 | 12.7456 | 0.60013 | 0.39134 | 13.7371
2030 | 0 | 0 | 0 | 0 | 0 | 6.2788 |  | 2030 | 85.8501 | 14.2691 | 2.935 | 0.13032 | 0.69551 | 3.7608 | 2030 | 1140.065 | 187.1537 | 38.8348 | 1.7093 | 0.14099 | 40.6851 |  | 2030 | 396.4585 | 64.4971 | 10.6856 | 0.58907 | 0.0053736 | 11.28 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0.14099 | 18.0681 | 2030 | 910.5491 | 149.8903 | 31.5378 | 1.369 | 0.14099 | 33.0478 | 2030 | 427.0559 | 70.0473 | 13.8476 | 0.63976 | 0.38435 | 14.8717
Total | 400 | 90.7 | 6.1557 | 0.12311 | 83.5854 | 83.5854 |  | Total | 503.3443 | 83.6692 | 14.1493 | 0.76418 | 3.4098 | 39.3056 | Total | 5849.1378 | 967.0234 | 170.6306 | 8.8321 | -0.79817 | 473.5984 |  | Total | 1907.5689 | 311.2704 | 46.3703 | 2.8429 | 4.5673 | 135.129 | Total | 3602.4118 | 603.9894 | 102.811 | 5.5164 | -0.79817 | 246.542 | Total | 3677.4271 | 607.5355 | 112.7221 | 5.5488 | -0.79817 | 369.682 | Total | 2190.8488 | 361.4081 | 61.3249 | 3.3009 | 2.6472 | 171.8346
High Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 58.2868 |  | NPV | [5 empty] | 21.4403 | NPV | [5 empty] | 231.8069 |  | NPV | [5 empty] | 68.5327 | NPV | [5 empty] | 129.681 | NPV | [5 empty] | 167.9828 | NPV | [5 empty] | 85.805
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.56203 | 0.011241 | 5.9591 | 0.57327 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.58797 | 0.011759 | 6.3402 | 1.173 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.173 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 77.4 | 6.6925 | 0.13385 | 74.3012 | 7.9994 |  | 2025 | 45.9832 | 7.6466 | 1.0296 | 0.069839 | 1.3679 | 2.4674 | 2025 | 529.8255 | 87.8839 | 12.2978 | 0.80267 | -0.029215 | 13.0713 |  | 2025 | 142.0475 | 23.311 | 3.0397 | 0.21291 | 1.8745 | 5.1272 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | -0.029215 | 9.6253 | 2025 | 181.4473 | 30.1242 | 4.1411 | 0.27513 | -0.029215 | 4.3871 | 2025 | 190.9599 | 31.622 | 4.3492 | 0.28881 | 1.1453 | 5.7833
2026 | 0 | 0 | 0 | 0 | 0 | 7.9994 |  | 2026 | 59.1861 | 9.8407 | 1.413 | 0.089879 | 0.49165 | 1.9945 | 2026 | 803.5445 | 132.9423 | 19.7759 | 1.2142 | -0.056586 | 20.9335 |  | 2026 | 194.4207 | 31.7635 | 4.2057 | 0.29011 | 1.4559 | 5.9517 | 2026 | 582.2536 | 96.6578 | 14.3293 | 0.88281 | -0.056586 | 15.1555 | 2026 | 362.2541 | 60.0821 | 8.8799 | 0.54875 | -0.056586 | 9.3721 | 2026 | 279.0843 | 46.0968 | 6.7019 | 0.42102 | 0.59565 | 7.7186
2027 | 0 | 0 | 0 | 0 | 0 | 7.9994 |  | 2027 | 67.1291 | 11.1561 | 1.7046 | 0.10189 | 0.75079 | 2.5573 | 2027 | 853.1373 | 141.057 | 22.0689 | 1.2883 | 0.12707 | 23.4843 |  | 2027 | 233.9871 | 38.2671 | 5.1077 | 0.34951 | -0.67469 | 4.7825 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0.12707 | 15.6768 | 2027 | 488.9922 | 80.9615 | 12.7145 | 0.73945 | 0.12707 | 13.581 | 2027 | 305.3456 | 50.4091 | 7.6465 | 0.4604 | 0.23849 | 8.3454
2028 | 0 | 0 | 0 | 0 | 0 | 7.9994 |  | 2028 | 71.8565 | 11.9442 | 2.2756 | 0.10909 | -0.047026 | 2.3376 | 2028 | 967.6027 | 159.8142 | 30.9959 | 1.4596 | -1.2839 | 31.1716 |  | 2028 | 308.2493 | 50.2259 | 8.2279 | 0.45873 | 0.94619 | 9.6328 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | -1.2839 | 19.2549 | 2028 | 710.0415 | 117.2009 | 22.979 | 1.0704 | -1.2839 | 22.7655 | 2028 | 354.8912 | 58.4821 | 10.9437 | 0.53414 | -0.10795 | 11.3699
2029 | 0 | 0 | 0 | 0 | 0 | 7.9994 |  | 2029 | 86.7119 | 14.4068 | 2.8755 | 0.13158 | 0.15092 | 3.158 | 2029 | 1077.0558 | 177.308 | 35.8867 | 1.6194 | 0.30349 | 37.8096 |  | 2029 | 348.0053 | 56.7083 | 9.3446 | 0.51794 | 0.96003 | 10.8226 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0.30349 | 20.2961 | 2029 | 848.2091 | 139.7638 | 28.5601 | 1.2765 | 0.30349 | 30.1401 | 2029 | 399.6212 | 65.7075 | 12.7456 | 0.60013 | 0.39134 | 13.7371
2030 | 0 | 0 | 0 | 0 | 0 | 7.9994 |  | 2030 | 85.8501 | 14.2691 | 2.935 | 0.13032 | 0.69551 | 3.7608 | 2030 | 1140.065 | 187.1537 | 38.8348 | 1.7093 | 0.14099 | 40.6851 |  | 2030 | 396.4585 | 64.4971 | 10.6856 | 0.58907 | 0.0053736 | 11.28 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0.14099 | 18.0681 | 2030 | 910.5491 | 149.8903 | 31.5378 | 1.369 | 0.14099 | 33.0478 | 2030 | 427.0559 | 70.0473 | 13.8476 | 0.63976 | 0.38435 | 14.8717
Total | 400 | 90.7 | 7.8425 | 0.15685 | 86.6005 | 86.6005 |  | Total | 503.3443 | 83.6692 | 14.1493 | 0.76418 | 3.4098 | 32.387 | Total | 5849.1378 | 967.0234 | 170.6306 | 8.8321 | -0.79817 | 388.2747 |  | Total | 1907.5689 | 311.2704 | 46.3703 | 2.8429 | 4.5673 | 111.2526 | Total | 3602.4118 | 603.9894 | 102.811 | 5.5164 | -0.79817 | 202.687 | Total | 3677.4271 | 607.5355 | 112.7221 | 5.5488 | -0.79817 | 303.4502 | Total | 2190.8488 | 361.4081 | 61.3249 | 3.3009 | 2.6472 | 141.0753
Low Discount rate
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 77.4997 |  | NPV | [5 empty] | 47.7908 | NPV | [5 empty] | 543.8018 |  | NPV | [5 empty] | 157.0739 | NPV | [5 empty] | 294.2831 | NPV | [5 empty] | 405.9175 | NPV | [5 empty] | 199.1143
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 6.5 | 0.32971 | 0.0065941 | 5.2483 | 0.3363 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 6.8 | 0.34492 | 0.0068984 | 5.6721 | 0.68812 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.68812 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 77.4 | 3.926 | 0.078521 | 68.5051 | 4.6927 |  | 2025 | 45.9832 | 7.6466 | 1.0296 | 0.069839 | 1.3679 | 2.4674 | 2025 | 529.8255 | 87.8839 | 12.2978 | 0.80267 | -0.029215 | 13.0713 |  | 2025 | 142.0475 | 23.311 | 3.0397 | 0.21291 | 1.8745 | 5.1272 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | -0.029215 | 9.6253 | 2025 | 181.4473 | 30.1242 | 4.1411 | 0.27513 | -0.029215 | 4.3871 | 2025 | 190.9599 | 31.622 | 4.3492 | 0.28881 | 1.1453 | 5.7833
2026 | 0 | 0 | 0 | 0 | 0 | 4.6927 |  | 2026 | 59.1861 | 9.8407 | 1.413 | 0.089879 | 0.49165 | 1.9945 | 2026 | 803.5445 | 132.9423 | 19.7759 | 1.2142 | -0.056586 | 20.9335 |  | 2026 | 194.4207 | 31.7635 | 4.2057 | 0.29011 | 1.4559 | 5.9517 | 2026 | 582.2536 | 96.6578 | 14.3293 | 0.88281 | -0.056586 | 15.1555 | 2026 | 362.2541 | 60.0821 | 8.8799 | 0.54875 | -0.056586 | 9.3721 | 2026 | 279.0843 | 46.0968 | 6.7019 | 0.42102 | 0.59565 | 7.7186
2027 | 0 | 0 | 0 | 0 | 0 | 4.6927 |  | 2027 | 67.1291 | 11.1561 | 1.7046 | 0.10189 | 0.75079 | 2.5573 | 2027 | 853.1373 | 141.057 | 22.0689 | 1.2883 | 0.12707 | 23.4843 |  | 2027 | 233.9871 | 38.2671 | 5.1077 | 0.34951 | -0.67469 | 4.7825 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0.12707 | 15.6768 | 2027 | 488.9922 | 80.9615 | 12.7145 | 0.73945 | 0.12707 | 13.581 | 2027 | 305.3456 | 50.4091 | 7.6465 | 0.4604 | 0.23849 | 8.3454
2028 | 0 | 0 | 0 | 0 | 0 | 4.6927 |  | 2028 | 71.8565 | 11.9442 | 2.2756 | 0.10909 | -0.047026 | 2.3376 | 2028 | 967.6027 | 159.8142 | 30.9959 | 1.4596 | -1.2839 | 31.1716 |  | 2028 | 308.2493 | 50.2259 | 8.2279 | 0.45873 | 0.94619 | 9.6328 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | -1.2839 | 19.2549 | 2028 | 710.0415 | 117.2009 | 22.979 | 1.0704 | -1.2839 | 22.7655 | 2028 | 354.8912 | 58.4821 | 10.9437 | 0.53414 | -0.10795 | 11.3699
2029 | 0 | 0 | 0 | 0 | 0 | 4.6927 |  | 2029 | 86.7119 | 14.4068 | 2.8755 | 0.13158 | 0.15092 | 3.158 | 2029 | 1077.0558 | 177.308 | 35.8867 | 1.6194 | 0.30349 | 37.8096 |  | 2029 | 348.0053 | 56.7083 | 9.3446 | 0.51794 | 0.96003 | 10.8226 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0.30349 | 20.2961 | 2029 | 848.2091 | 139.7638 | 28.5601 | 1.2765 | 0.30349 | 30.1401 | 2029 | 399.6212 | 65.7075 | 12.7456 | 0.60013 | 0.39134 | 13.7371
2030 | 0 | 0 | 0 | 0 | 0 | 4.6927 |  | 2030 | 85.8501 | 14.2691 | 2.935 | 0.13032 | 0.69551 | 3.7608 | 2030 | 1140.065 | 187.1537 | 38.8348 | 1.7093 | 0.14099 | 40.6851 |  | 2030 | 396.4585 | 64.4971 | 10.6856 | 0.58907 | 0.0053736 | 11.28 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0.14099 | 18.0681 | 2030 | 910.5491 | 149.8903 | 31.5378 | 1.369 | 0.14099 | 33.0478 | 2030 | 427.0559 | 70.0473 | 13.8476 | 0.63976 | 0.38435 | 14.8717
Total | 400 | 90.7 | 4.6007 | 0.092013 | 79.4255 | 79.4255 |  | Total | 503.3443 | 83.6692 | 14.1493 | 0.76418 | 3.4098 | 49.0972 | Total | 5849.1378 | 967.0234 | 170.6306 | 8.8321 | -0.79817 | 595.6286 |  | Total | 1907.5689 | 311.2704 | 46.3703 | 2.8429 | 4.5673 | 168.9788 | Total | 3602.4118 | 603.9894 | 102.811 | 5.5164 | -0.79817 | 308.9012 | Total | 3677.4271 | 607.5355 | 112.7221 | 5.5488 | -0.79817 | 464.1691 |  | 2190.8488 | 361.4081 | 61.3249 | 3.3009 | 2.6472 | 215.7004
High Cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 87.1891 |  | NPV | [5 empty] | 31.2427 | NPV | [5 empty] | 346.5751 |  | NPV | [5 empty] | 101.2799 | NPV | [5 empty] | 190.67 | NPV | [5 empty] | 255.1923 | NPV | [5 empty] | 127.5851
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 8.45 | 0.57349 | 0.01147 | 7.3492 | 0.58496 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 8.84 | 0.59996 | 0.011999 | 7.8721 | 1.1969 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 1.1969 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 100.62 | 6.829 | 0.13658 | 93.4397 | 8.1625 |  | 2025 | 45.9832 | 7.6466 | 1.0296 | 0.069839 | 1.3679 | 2.4674 | 2025 | 529.8255 | 87.8839 | 12.2978 | 0.80267 | -0.029215 | 13.0713 |  | 2025 | 142.0475 | 23.311 | 3.0397 | 0.21291 | 1.8745 | 5.1272 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | -0.029215 | 9.6253 | 2025 | 181.4473 | 30.1242 | 4.1411 | 0.27513 | -0.029215 | 4.3871 | 2025 | 190.9599 | 31.622 | 4.3492 | 0.28881 | 1.1453 | 5.7833
2026 | 0 | 0 | 0 | 0 | 0 | 8.1625 |  | 2026 | 59.1861 | 9.8407 | 1.413 | 0.089879 | 0.49165 | 1.9945 | 2026 | 803.5445 | 132.9423 | 19.7759 | 1.2142 | -0.056586 | 20.9335 |  | 2026 | 194.4207 | 31.7635 | 4.2057 | 0.29011 | 1.4559 | 5.9517 | 2026 | 582.2536 | 96.6578 | 14.3293 | 0.88281 | -0.056586 | 15.1555 | 2026 | 362.2541 | 60.0821 | 8.8799 | 0.54875 | -0.056586 | 9.3721 | 2026 | 279.0843 | 46.0968 | 6.7019 | 0.42102 | 0.59565 | 7.7186
2027 | 0 | 0 | 0 | 0 | 0 | 8.1625 |  | 2027 | 67.1291 | 11.1561 | 1.7046 | 0.10189 | 0.75079 | 2.5573 | 2027 | 853.1373 | 141.057 | 22.0689 | 1.2883 | 0.12707 | 23.4843 |  | 2027 | 233.9871 | 38.2671 | 5.1077 | 0.34951 | -0.67469 | 4.7825 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0.12707 | 15.6768 | 2027 | 488.9922 | 80.9615 | 12.7145 | 0.73945 | 0.12707 | 13.581 | 2027 | 305.3456 | 50.4091 | 7.6465 | 0.4604 | 0.23849 | 8.3454
2028 | 0 | 0 | 0 | 0 | 0 | 8.1625 |  | 2028 | 71.8565 | 11.9442 | 2.2756 | 0.10909 | -0.047026 | 2.3376 | 2028 | 967.6027 | 159.8142 | 30.9959 | 1.4596 | -1.2839 | 31.1716 |  | 2028 | 308.2493 | 50.2259 | 8.2279 | 0.45873 | 0.94619 | 9.6328 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | -1.2839 | 19.2549 | 2028 | 710.0415 | 117.2009 | 22.979 | 1.0704 | -1.2839 | 22.7655 | 2028 | 354.8912 | 58.4821 | 10.9437 | 0.53414 | -0.10795 | 11.3699
2029 | 0 | 0 | 0 | 0 | 0 | 8.1625 |  | 2029 | 86.7119 | 14.4068 | 2.8755 | 0.13158 | 0.15092 | 3.158 | 2029 | 1077.0558 | 177.308 | 35.8867 | 1.6194 | 0.30349 | 37.8096 |  | 2029 | 348.0053 | 56.7083 | 9.3446 | 0.51794 | 0.96003 | 10.8226 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0.30349 | 20.2961 | 2029 | 848.2091 | 139.7638 | 28.5601 | 1.2765 | 0.30349 | 30.1401 | 2029 | 399.6212 | 65.7075 | 12.7456 | 0.60013 | 0.39134 | 13.7371
2030 | 0 | 0 | 0 | 0 | 0 | 8.1625 |  | 2030 | 85.8501 | 14.2691 | 2.935 | 0.13032 | 0.69551 | 3.7608 | 2030 | 1140.065 | 187.1537 | 38.8348 | 1.7093 | 0.14099 | 40.6851 |  | 2030 | 396.4585 | 64.4971 | 10.6856 | 0.58907 | 0.0053736 | 11.28 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0.14099 | 18.0681 | 2030 | 910.5491 | 149.8903 | 31.5378 | 1.369 | 0.14099 | 33.0478 | 2030 | 427.0559 | 70.0473 | 13.8476 | 0.63976 | 0.38435 | 14.8717
Total | 400 | 117.91 | 8.0024 | 0.16005 | 108.661 | 108.661 |  | Total | 503.3443 | 83.6692 | 14.1493 | 0.76418 | 3.4098 | 39.3056 | Total | 5849.1378 | 967.0234 | 170.6306 | 8.8321 | -0.79817 | 473.5984 |  | Total | 1907.5689 | 311.2704 | 46.3703 | 2.8429 | 4.5673 | 135.129 | Total | 3602.4118 | 603.9894 | 102.811 | 5.5164 | -0.79817 | 246.542 | Total | 3677.4271 | 607.5355 | 112.7221 | 5.5488 | -0.79817 | 369.682 | Total | 2190.8488 | 361.4081 | 61.3249 | 3.3009 | 2.6472 | 171.8346
Low cost
[8 empty] | Benefits | Central | [5 empty] | Benefits | Step Change | [6 empty] | Benefits | Slow Change | [5 empty] | Benefits | Fast change | [5 empty] | Benefits | High DER | [5 empty] | Benefits | Central weighting
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 46.948 |  | NPV | [5 empty] | 31.2427 | NPV | [5 empty] | 346.5751 |  | NPV | [5 empty] | 101.2799 | NPV | [5 empty] | 190.67 | NPV | [5 empty] | 255.1923 | NPV | [5 empty] | 127.5851
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 100 | 4.55 | 0.3088 | 0.0061761 | 3.9573 | 0.31498 |  | 2022 | 18.138 | 3.0189 | 0.37891 | 0.027572 | 0 | 0.40649 | 2022 | 26.915 | 4.8416 | 0.51061 | 0.04422 | 0 | 0.55483 |  | 2022 | 62.8596 | 10.2664 | 1.2541 | 0.093767 | 0 | 1.3479 | 2022 | 41.0567 | 6.8183 | 0.86339 | 0.062274 | 0 | 0.92567 | 2022 | 23.0182 | 3.9087 | 0.46883 | 0.0357 | 0 | 0.50453 | 2022 | 31.5127 | 5.2864 | 0.63064 | 0.048283 | 0 | 0.67892
2023 | 100 | 4.76 | 0.32306 | 0.0064611 | 4.2388 | 0.6445 |  | 2023 | 31.9646 | 5.3139 | 0.70984 | 0.048534 | 0 | 0.75838 | 2023 | 128.5894 | 21.8754 | 2.8379 | 0.1998 | 0 | 3.0377 |  | 2023 | 101.5947 | 16.6252 | 2.0255 | 0.15184 | 0 | 2.1774 | 2023 | 127.7848 | 21.1824 | 2.8881 | 0.19347 | 0 | 3.0816 | 2023 | 52.5341 | 8.8289 | 1.1581 | 0.080638 | 0 | 1.2387 | 2023 | 73.5283 | 12.2821 | 1.5708 | 0.11218 | 0 | 1.683
2024 | 0 | 0 | 0 | 0 | 0 | 0.6445 |  | 2024 | 36.5248 | 6.0728 | 0.82721 | 0.055465 | 0 | 0.88268 | 2024 | 322.4027 | 54.1474 | 7.4221 | 0.49455 | 0 | 7.9167 |  | 2024 | 119.9463 | 19.6059 | 2.4795 | 0.17907 | 0 | 2.6585 | 2024 | 220.4154 | 36.5065 | 5.1118 | 0.33343 | 0 | 5.4453 | 2024 | 100.3815 | 16.775 | 2.2828 | 0.15321 | 0 | 2.436 | 2024 | 128.8496 | 21.4747 | 2.889 | 0.19614 | 0 | 3.0851
2025 | 200 | 54.18 | 3.6771 | 0.073543 | 50.3137 | 4.3952 |  | 2025 | 45.9832 | 7.6466 | 1.0296 | 0.069839 | 1.3679 | 2.4674 | 2025 | 529.8255 | 87.8839 | 12.2978 | 0.80267 | -0.029215 | 13.0713 |  | 2025 | 142.0475 | 23.311 | 3.0397 | 0.21291 | 1.8745 | 5.1272 | 2025 | 393.1251 | 65.4002 | 9.0572 | 0.59732 | -0.029215 | 9.6253 | 2025 | 181.4473 | 30.1242 | 4.1411 | 0.27513 | -0.029215 | 4.3871 | 2025 | 190.9599 | 31.622 | 4.3492 | 0.28881 | 1.1453 | 5.7833
2026 | 0 | 0 | 0 | 0 | 0 | 4.3952 |  | 2026 | 59.1861 | 9.8407 | 1.413 | 0.089879 | 0.49165 | 1.9945 | 2026 | 803.5445 | 132.9423 | 19.7759 | 1.2142 | -0.056586 | 20.9335 |  | 2026 | 194.4207 | 31.7635 | 4.2057 | 0.29011 | 1.4559 | 5.9517 | 2026 | 582.2536 | 96.6578 | 14.3293 | 0.88281 | -0.056586 | 15.1555 | 2026 | 362.2541 | 60.0821 | 8.8799 | 0.54875 | -0.056586 | 9.3721 | 2026 | 279.0843 | 46.0968 | 6.7019 | 0.42102 | 0.59565 | 7.7186
2027 | 0 | 0 | 0 | 0 | 0 | 4.3952 |  | 2027 | 67.1291 | 11.1561 | 1.7046 | 0.10189 | 0.75079 | 2.5573 | 2027 | 853.1373 | 141.057 | 22.0689 | 1.2883 | 0.12707 | 23.4843 |  | 2027 | 233.9871 | 38.2671 | 5.1077 | 0.34951 | -0.67469 | 4.7825 | 2027 | 564.8414 | 94.449 | 14.6871 | 0.86263 | 0.12707 | 15.6768 | 2027 | 488.9922 | 80.9615 | 12.7145 | 0.73945 | 0.12707 | 13.581 | 2027 | 305.3456 | 50.4091 | 7.6465 | 0.4604 | 0.23849 | 8.3454
2028 | 0 | 0 | 0 | 0 | 0 | 4.3952 |  | 2028 | 71.8565 | 11.9442 | 2.2756 | 0.10909 | -0.047026 | 2.3376 | 2028 | 967.6027 | 159.8142 | 30.9959 | 1.4596 | -1.2839 | 31.1716 |  | 2028 | 308.2493 | 50.2259 | 8.2279 | 0.45873 | 0.94619 | 9.6328 | 2028 | 606.9932 | 101.8449 | 19.6086 | 0.93018 | -1.2839 | 19.2549 | 2028 | 710.0415 | 117.2009 | 22.979 | 1.0704 | -1.2839 | 22.7655 | 2028 | 354.8912 | 58.4821 | 10.9437 | 0.53414 | -0.10795 | 11.3699
2029 | 0 | 0 | 0 | 0 | 0 | 4.3952 |  | 2029 | 86.7119 | 14.4068 | 2.8755 | 0.13158 | 0.15092 | 3.158 | 2029 | 1077.0558 | 177.308 | 35.8867 | 1.6194 | 0.30349 | 37.8096 |  | 2029 | 348.0053 | 56.7083 | 9.3446 | 0.51794 | 0.96003 | 10.8226 | 2029 | 569.1389 | 96.2673 | 19.1134 | 0.87924 | 0.30349 | 20.2961 | 2029 | 848.2091 | 139.7638 | 28.5601 | 1.2765 | 0.30349 | 30.1401 | 2029 | 399.6212 | 65.7075 | 12.7456 | 0.60013 | 0.39134 | 13.7371
2030 | 0 | 0 | 0 | 0 | 0 | 4.3952 |  | 2030 | 85.8501 | 14.2691 | 2.935 | 0.13032 | 0.69551 | 3.7608 | 2030 | 1140.065 | 187.1537 | 38.8348 | 1.7093 | 0.14099 | 40.6851 |  | 2030 | 396.4585 | 64.4971 | 10.6856 | 0.58907 | 0.0053736 | 11.28 | 2030 | 496.8026 | 84.8631 | 17.1521 | 0.77508 | 0.14099 | 18.0681 | 2030 | 910.5491 | 149.8903 | 31.5378 | 1.369 | 0.14099 | 33.0478 | 2030 | 427.0559 | 70.0473 | 13.8476 | 0.63976 | 0.38435 | 14.8717
Total | 400 | 63.49 | 4.309 | 0.08618 | 58.5098 | 58.5098 |  | Total | 503.3443 | 83.6692 | 14.1493 | 0.76418 | 3.4098 | 39.3056 | Total | 5849.1378 | 967.0234 | 170.6306 | 8.8321 | -0.79817 | 473.5984 |  | Total | 1907.5689 | 311.2704 | 46.3703 | 2.8429 | 4.5673 | 135.129 | Total | 3602.4118 | 603.9894 | 102.811 | 5.5164 | -0.79817 | 246.542 | Total | 3677.4271 | 607.5355 | 112.7221 | 5.5488 | -0.79817 | 369.682 | Total | 2190.8488 | 361.4081 | 61.3249 | 3.3009 | 2.6472 | 171.8346