## Index
The National Electricity Market Constraint Report 2017
Electronic Material
This spreadsheet provides (for each calendar year):
* Constraint equation changes year on year comparison
* Binding constraint equations (energy and FCAS separately)
* Binding Impact of constraint equations
* Summary of binding/binding impact constraint equations by region
* Summary of binding/binding impact constraint equations for System Normal vs Outages
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
* Network and generation augmentations
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page
Binding constraints:
A constraint equation is a linear equation, with a left hand side (LHS) and a right hand side (RHS). A constraint is binding when LHS=RHS, which means it has reached its upper limit.
In some cases, the binding results for several constraint equation IDs have been combined. This is due to some limits being represented by several constraint equations, to either:
• Move each generator from a maximum calculation onto the LHS of separate constraint equations (such as the New South Wales to Queensland voltage stability limit).
• Manage the same limit under different network configurations (such as Yallourn W1 switched into 500 kV or 220 kV mode).
• Combine different values of network support for the same generator(s).
Binding Impact:
Binding Impact is used to distinguish between the severities of different binding constraint equations. It represents the financial pain associated with that binding constraint equation and can be a good way of picking up congestion issues. It is a relative term, not an absolute term.

## Constraint Changes
Constraint changes by region and year
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Ad-Hoc | 19 | 1 | 0 | 0 | 0 | 1
Constraint Automation - Real Time | 0 | 24316 | 24110 | 11484 | 22603 | 29805
Constraint Automation | 148 | 139 | 166 | 98 | 64 | 20
DATASNAP | 254 | 92 | 87 | 105 | 115 | 44
FCAS | 444 | 295 | 255 | 543 | 257 | 267
NSW | 787 | 2345 | 5272 | 6332 | 1973 | 2455
Negative Residue | 6 | 0 | 0 | 0 | 0 | 0
Non-Conformance | 8 | 6 | 3 | 5 | 5 | 52
Other | 2 | 2 | 0 | 2 | 0 | 0
Outage Ramping | 27050 | 22066 | 19888 | 21056 | 20484 | 16928
PASA | 3 | 3 | 12 | 0 | 0 | 0
Qld | 308 | 330 | 270 | 118 | 206 | 246
Quick | 231 | 84 | 93 | 101 | 359 | 386
SA | 584 | 1101 | 600 | 1001 | 3197 | 1775
Tas | 859 | 1114 | 726 | 121 | 1050 | 134
Vic | 1412 | 359 | 637 | 3541 | 3251 | 1376
Total constraint eqns | 9745 | 9935 | 10303 | 11231 | 11660 | 11578
Total changes without outage ramping and CA-RT | 5065 | 5871 | 8121 | 11967 | 10477 | 6756
Total number of constraints
| 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Constraint Equations | 7746 | 7697 | 8275 | 8902 | 9523 | 9745 | 9935 | 10303 | 11231 | 11660 | 11578
Constraint Sets | 3366 | 3369 | 3431 | 3559 | 3657 | 3597 | 3410 | 3424 | 3630 | 3778 | 3917
Constraint Functions |  |  | 347 | 382 | 390 | 401 | 366 | 359 | 364 | 373 | 387
Increase in Constraint Equations |  |  | 578 | 627 | 621 | 222 | 190 | 368 | 928 | 429 | -82

## Binding
Constraint Equation ID | 2017 Hours | 2016 Hours | Description | Type | Region
N^^V_NIL_1 | 1806.4167 | 81.9167 | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL | NSW
N_X_MBTE2_A & N_X_MBTE2_B | 1203.3333 | 568.75 | Out = two Directlink cables | Outage | NSW
V::N_NIL_xxx | 624.5 | 1054.25 | Out = Nil, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria and all the binding results have been combined. | NIL | Vic
#YABULU2_E | 590.0833 | 0 | QGAR1.ENERGY * 1 <= 55 (Wt = 360) | Other | Quick
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 517.1667 | 0 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Qld
S_WIND_1200_AUTO & S_NIL_STRENGTH_1 | 390.4167 | 0 | Upper limit of 1295 MW for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements. Automatically swamps out when required combination is online. | NIL | SA
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 311.9167 | 1014.5 | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV These constraint equations maintain flow on the South Morang F2 transformer below its continuous rating. | NIL | Vic
I_CTRL_ISSUE_TE | 311.4167 | 44.25 | DC Link Control Issue Constraint for Terranora | Outage | Other
V:S_600_HY_TEST_DYN | 288.5 | 181.75 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
S>V_NIL_NIL_RBNW | 282.4167 | 586.8333 | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips This constraint equation normally sets the upper limit on Murraylink. | NIL | SA
#YWPS2_E | 252.5833 | 0 | VYP22.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
N^N_KKLS_1 | 233.8333 | 2.3333 | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. | Outage | NSW
N_X_MBTE_3A & N_X_MBTE_3B | 224 | 864.6667 | Out = all three Directlink cables | Outage | NSW
S:V_500_HY_TEST_DYN | 208 | 0.83333 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
N_MBTE1_B | 206.4167 | 10.0833 | Out = one Directlink cable, Queensland to NSW limit | Outage | NSW
#OSB-AG_P_E | 205.5 | 0 | SNBN1.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
#OSB-AG_O_E | 205.4167 | 0 | SNBN1.ENERGY * 1 >= 135 (Wt = 65) | Other | Quick
V_T_NIL_FCSPS | 194.75 | 48.3333 | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) This constraint equation binds when there is high import to Tasmania or a low amount of load is enabled for tripping. | NIL | Vic
T>T_NIL_110_1 | 188.0833 | 153.9167 | Out = Nil, avoid overloading the Derby to Scottsdale Tee 110 kV line on no line trips This constraint equation was implemented in mid-2013 with the Musselroe Wind Farm commissioning. It binds with high output from Musselroe. | NIL | Tas
#WRWF1_E | 184.9167 | 0 | NWRK1W.ENERGY * 1 <= 130 (Wt = 360) | Other | Quick
V::N_SMF2_xxx | 183.6667 | 10.4167 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#TORRB2_P_E | 174.5 | 0 | STSB2.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 148.25 | 576.5 | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator This voltage collapse limit is split into 7 constraint equations to co-optimise with each of the 6 largest generators in Queensland. Overall N^^Q_NIL_B1 (for trip of Kogan Creek) binds for the most number of intervals. | NIL | NSW
V_T_NIL_BL1 | 145.8333 | 13.1667 | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL | Vic
Q>NIL_BI_xxx | 139.5 | 1408.75 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104 and 7105 (T022 Callide A to T152 Gladstone South) 132 kV lines open with 132 kV intact between T022 Callide A and H015 Lilyvale. | NIL | Qld
V_S_NIL_ROCOF | 134.4167 | 393.0833 | Out = Nil, limit Victoria to SA on Heywood flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL | Vic
T_MRWF_QLIM_xx | 118.8333 | 39.75 | Out = Nil, limit Musselroe Wind Farm based on status of the DVARs, capacitor banks or synchronous condensers at Musselroe The binding results from the six constraint equations have been combined. | NIL | Tas
#WATERLWF_E | 118.75 | 3.75 | SWLE.ENERGY * 1 <= 80 (Wt = 360) | Other | Quick
#KSP1_E | 111.6667 | 0 | QROG1K.ENERGY * 1 <= 35 (Wt = 360) | Other | Quick
S>NIL_WERB_WEWT | 104.25 | 43.8333 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
#HDWF3_E | 103.3333 | 0 | SHDW3H.ENERGY * 1 <= 98 (Wt = 360) | Other | Quick
#TORRB2_O_E | 103 | 0 | STSB2.ENERGY * 1 >= 40 (Wt = 65) | Other | Quick
S>NIL_HUWT_STBG | 97 | 78.9167 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line overload on loss of Hummocks - Waterloo line | NIL | SA
T>T_LIPM_110_2A | 89.8333 | 0.91667 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
SVML_ZERO | 83.5833 | 173.75 | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage | SA
N>N-CHKK_TE_1 | 82.75 | 16.75 | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
#PPCCGT_O_E | 81.3333 | 2.4167 | SPPT.ENERGY * 1 >= 165 (Wt = 65) | Other | Quick
#PPCCGT_P_E | 77 | 0 | SPPT.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
V:S_600_HY_TEST | 75.4167 | 47.75 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
Q>N-MUTE_758 | 68.9167 | 0.083333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
T_TAMARCCGT_GCS | 65.4167 | 0.91667 | Limit output of Tamar Valley Power Station based on load available for shedding by Tamar Valley 220 kV generation control scheme (GCS) | NIL | Tas
T:T_LIPM_1 | 63.1667 | 0.33333 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Tas
VS_050 | 59.25 | 0 | Victoria to South Australia on Heywood upper transfer limit of 50 MW | Outage | Vic
#NBHWF1_E | 54.3333 | 49.3333 | SBEL1A.ENERGY * 1 <= 34 (Wt = 360) | Other | Quick
S>NIL_SGBN_SGSE-T2 | 54.0833 | 16.9167 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
V^SML_NSWRB_2 | 53.1667 | 153.9167 | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL | Vic
V::N_HWSM_xxx | 52.8333 | 33.5833 | Out = Hazelwood to South Morang 500 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
S_HALWF_0 | 52.25 | 1.25 | Discretionary upper limit for Hallett wind farm generation of 0 MW | Outage | SA
T_ROCOF_1 | 49.25 | 0 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL | Tas
Q:N_NIL_BI_POT | 49.0833 | 0 | Out = Nil, avoid transient instability for a trip of a Boyne Island potline (400 MW) For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_OSC or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
S:V_500_HY_TEST | 48.3333 | 0.083333 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
S-SNWWF_0 | 46.3333 | 27.5 | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
T>T_TUNN3_110_1 | 45.3333 | 7.0833 | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Meadowbank Tee 2 to New Norfolk 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
V::S_SETB_TBSE_2 | 45.3333 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | SA
#N-Q-MNSP1_I_E | 44.0833 | 40.25 | Quick constraint equation applied to Terranora Interconnector at various levels | Other | Quick
#KIATAWF1_E | 43 | 0 | VHOG1K.ENERGY * 1 <= 31 (Wt = 360) | Other | Quick
V>>V_NIL_2_TIE | 42.3333 | 0 | Out = Nil, avoid pre-contingent O/L of the South Morang F2 500/330 kV transformer, Yallourn unit 1 in 220kV mode, all 220kV buses tied at Hazelwood, feedback | NIL | Vic
S>NWBCB6225_TX1 | 40.9167 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 66/132kV TX1 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage | SA
#TORRB4_P_E | 40.8333 | 0 | STSB4.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 40 | 98.25 | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies These constraint equations are dependent on the Terranora load as well as all 3 cables of Directlink being in service. In May 2011 the constraint equation Q>NIL_757+758_B was replaced with two constraint equations Q>NIL_MUTE_757 and Q>NIL_MUTE_758. The binding results for each have been combined. | NIL | Qld
S>NIL_NIL_NWMH2 | 37 | 37.4167 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
#BALDHWF1_E | 35.1667 | 0 | VMWT9B.ENERGY * 1 = 0 (Wt = 360) | Other | Quick
V>>V_NIL_5 | 34.75 | 0.58333 | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL | Vic
T>T_NIL_BL_110_18_1 | 33.1667 | 0.58333 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
N>LSDU_LSDU | 33 | 109.9167 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
S_SA_WIND_1200 | 32.1667 | 0 | Discretionary upper limit for South Australian wind generation of 1200 MW. | Outage | SA
#OAKLAND1_E | 31.25 | 5.5 | VTGT3A.ENERGY * 1 <= 30 (Wt = 360) | Other | Quick
S_DVRB2_270 | 30.75 | 0 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | SA
Q>N-MUTE_757 | 30.3333 | 2.5 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
N^Q_NIL_A | 30.25 | 82.0833 | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL | NSW
NSA_S_PORxxx | 30.0833 | 43.3333 | Network Support Agreement for Port Lincoln Units 1 and 2 | Outage | SA
V>>V_SMTXF2_6 | 29.9167 | 2.0833 | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage | Vic
N^^V_DDMSX5_1 | 29.4167 | 0 | Out = Dederang - Murray (67 or 68) and Darlington Pt - Buronga (X5) lines, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
SV_250 | 29 | 0 | SA to Victoria on Heywood upper transfer limit of 250 MW | Outage | SA
#MACARTH1_E | 28.8333 | 0 | VTRT1M.ENERGY * 1 <= 210 (Wt = 360) | Other | Quick
S:VS_650_HY_TEST_DYN | 28.75 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
#YABULU_E | 28.6667 | 0 | QTYP.ENERGY * 1 <= 100 (Wt = 360) | Other | Quick
S_WATERLWF_RB | 27.4167 | 0 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | SA
#TORRA1_P_E | 26.8333 | 0 | STSA1.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
#TORRA2_P_E | 26.1667 | 0 | STSA2.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
Q:N_AR_CP2_AR_2L-G | 26 | 6.5 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
T>>T_NIL_BL_EXP_7C | 25.9167 | 82.5833 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
S_PLN_ISL2 | 25.75 | 7.5 | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
S_PLN_ISL32 | 25.5833 | 6.25 | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
#MPP_1_E | 25.25 | 0 | QBCK1.ENERGY * 1 <= 320 (Wt = 360) | Other | Quick
#TORRB4_O_E | 24.25 | 0 | STSB4.ENERGY * 1 >= 40 (Wt = 65) | Other | Quick
V>>V_KTS_TX_A3_2A_R | 24.25 | 7.0833 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
#MP2_E | 23.9167 | 0 | NMTP2.ENERGY * 1 <= 660 (Wt = 360) | Other | Quick
#TORRB3_C_E | 23.5833 | 0 | STSB3.ENERGY * 1 <= 60 (Wt = 48) | Other | Quick
N_NIL_TE_B | 23.4167 | 1.6667 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
T>T_NIL_220_14_HM | 23.4167 | 0 | Out = Nil, West Coast 220/110 kV parallel closed, avoid overloading a Farrell to Sheffield line for loss of the parallel line, feedback | NIL | Tas
#TORRA4_P_E | 23.1667 | 0 | STSA4.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
#TORRB3_P_E | 22.75 | 0 | STSB3.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
#TORRA1_O_E | 22.5 | 0 | STSA1.ENERGY * 1 >= 40 (Wt = 65) | Other | Quick
VSML_220 | 22.4167 | 468.3333 | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL | Vic
#TORRA2_O_E | 21.9167 | 0 | STSA2.ENERGY * 1 >= 40 (Wt = 65) | Other | Quick
#PPCCGT_C_E | 21.8333 | 0 | SPPT.ENERGY * 1 <= 168 (Wt = 48) | Other | Quick
SVML_ROC_80 | 21.6667 | 33.9167 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
#TORRA4_O_E | 21.5833 | 0 | STSA4.ENERGY * 1 >= 40 (Wt = 65) | Other | Quick
T^V_NIL_11 | 21.5 | 2 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
N>>N-NIL__3_OPENED & CLOSED | 21.25 | 61.3333 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
NC_V_KIATAWF1 | 21 | 0 | Non Conformance Constraint for Kiata Wind Farm | Other | Non-Conformance
VSML_ZERO | 20.75 | 301.5 | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
V_ML_TRMO | 20.6667 | 0 | Out = Moorabool to Mortlake or Moorabool to Tarrone 500 kV line, limit nett loading to < 50 MW on the remaining 500 kV line into Moorabool. | Outage | Vic
V_MACARTHUR_ZERO | 20.5833 | 39.1667 | Macarthur upper limit of 0 MW | Outage | Vic
VSML_ROC_80 | 20.5 | 27.1667 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
#OSB-AG_C_E | 20.3333 | 0 | SNBN1.ENERGY * 1 <= 139 (Wt = 48) | Other | Quick
N^^V_MSUT_1 | 20.0833 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
QNTE_150 | 19.6667 | 0 | Qld to NSW on Terranora Interconnector upper transfer limit of 150 MW | Outage | Qld
NQTE_ROC | 19.5 | 85.8333 | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL | NSW
Q:N_NIL_OSC | 19.4167 | 0 | Out = Nil, Queensland to NSW oscillatory stability limit This constraint equation sets the upper limit from Queensland to NSW to 1078 MW. For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
#TORRB3_O_E | 19.0833 | 0 | STSB3.ENERGY * 1 >= 40 (Wt = 65) | Other | Quick
NRM_QLD1_NSW1 | 18.8333 | 7 | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
S_HALWF2_0 | 18.3333 | 0 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | SA
S>NWCB6024+25_TX3 | 18.25 | 4.3333 | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | SA
TV_525 | 18.25 | 0 | Tas to Vic on Basslink upper limit of 525 MW | Outage | Tas
N>N-96H+96R_TE_1 | 18.1667 | 0.58333 | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage | NSW
V_MTMERCER_ZERO | 17.8333 | 44 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
V_OWF_TGTSNRBHTN_30 | 17.8333 | 0 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Vic
T>T_NIL_110_2 | 17.5833 | 0.25 | Out = NIL, avoid O/L Scottsdale Tee to Norwood 110 kV line (flow to Norwood) on trip of Scottsdale to Norwood 110 kV line or 110/22 kV txfmr at Scottsdale, feedback. Swamped when Musselroe Runback Control Scheme available | NIL | Tas
S>V_NWRB_RBMWP3 | 17.4167 | 0 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage | SA
S>>BLMK_CNRB_WEMWP4 | 17.3333 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV on trip of Canowi-Robertstown 275kV line(this trips Hallet wind farm and Hallet GT, and offloads Davenport-Canowie 275kV line), Feedback | Outage | SA
QNTE_ROC | 16.8333 | 85.75 | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
#TORRB2_E | 16.4167 | 0 | STSB2.ENERGY * 1 <= 120 (Wt = 35) | Other | Quick
T::T_NIL_4 | 15.5833 | 9.25 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
T_FASH_MAXGEN_1 | 15.5 | 9.4167 | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Tas
T>T_NIL_BL_IMP_7CC | 14.8333 | 86.5 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
N^^V_DDWG | 14.75 | 0 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
NSA_Q_GSTONE34_xxx | 14.6667 | 13.5833 | Gladstone 3 + 4 >= various levels for Network Support Agreement The binding results from three constraint equations that set the minimum level of Gladstone 3 and 4 generation have been combined. | Outage | Qld
V::N_BYPASS_HW_SY_xxx | 14.3333 | 5.8333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
#TORRB1_C_E | 14.1667 | 0 | STSB1.ENERGY * 1 <= 60 (Wt = 48) | Other | Quick
N^^V_SMTXH1_1 | 14.1667 | 3.25 | Out = South Morang H1 or H2 500/330 kV txfmr, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
S>RB_275KV_S_BUS_9 | 14 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage | SA
N>>Q_LDMU_B | 13.1667 | 0 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage | NSW
TVBL_ROC | 12.75 | 3.4167 | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL | Tas
S_SECB_LG3 | 12.6667 | 0 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
V>S_460_DYN | 12.5833 | 18.0833 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Vic
#TORRB2_C_E | 12.5833 | 0 | STSB2.ENERGY * 1 <= 60 (Wt = 48) | Other | Quick
VTBL_ROC | 12.5833 | 4.4167 | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL | Vic
N^^V_DDSM1 | 12.5 | 4.25 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
S>BLMK_BWPA_HUWT | 12.5 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
#MSTUART2_D_E | 12.25 | 0 | QMSP2.ENERGY * 1 = 30 (Wt = 755) | Other | Quick
V>>N-NIL_HA | 12.1667 | 367.9167 | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | NIL | Vic
N>N-X_96H+9W2+96L_1 | 12.0833 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Kempsey-Raleigh (9W2) and Lismore-Tenterfield (96L) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD | Outage | NSW
#NSW1-QLD1_RAMP_I_F | 11.5833 | 1.25 | NSW1-QLD1 >= MIN(-207, InitialFlow + 200) (Wt=35) | Other | Quick
#AGLHAL_O_E | 11.25 | 0 | SHPS1.ENERGY * 1 = 14 (Wt = 755) | Other | Quick
#TORRB1_E | 11.25 | 48.9167 | STSB1.ENERGY * 1 <= 200 (Wt = 360) | Other | Quick
N^^Q_NIL_A | 11.25 | 0 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | NSW
S_TBL_0 | 11 | 8.25 | Discretionary upper limit for The Bluff generation of 0 MW | Outage | SA
V::N_KTSY_xxx | 11 | 6.1667 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S_V_NIL_ROCOF | 10.75 | 5.6667 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL | SA
#MSTUART3_D_E | 10.6667 | 0 | QMSP3M.ENERGY * 1 = 45 (Wt = 755) | Other | Quick
QNTE_OSCILLATE | 10.6667 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Qld
S_NBH_0 | 10.5 | 0 | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | SA
T^V_NIL_BL_6 | 10.5 | 7.75 | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
VS_250_DYN | 10.5 | 244.8333 | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Vic
S>V_CB6033+6225_TX2 | 10.4167 | 4.6667 | Out= North West Bend_CB6033 and CB6225; avoid O/L of North West Bend transformer 132/66kV #2 on trip of either Robertstown-NWB #2 132kV line or NWB-Monash #2 132kV line . | Outage | SA
S>>X_MKRB+6573+74_1 | 10.25 | 0 | Out= Mokota-Robertstown 275kV line AND Robertstown CB6573 and CB6574, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Robt 275/132kV TX1, and Dav-Can 275kV line and trips Hallet GT & WF), Feedback | Outage | SA
S-STTX_SNWF | 10.0833 | 210 | Out = Snowtown 132/33 kV transformer or Snowtown CB4593 or CB6265, limit Snowtown wind farm generation to 0 MW | Outage | SA
#BOCORWF1_E | 9.0833 | 0 | NCMA3B.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
T>T_NWSD_110_1 | 9.0833 | 0 | Out= Norwood - Scottsdale 110kV direct line, avoid O/L Scotdale Tee to Norwood 110kV line on Nil trip, Feedback | Outage | Tas
V>>V_KTS_TX_A2_2A_R | 9.0833 | 54.75 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
#HDWF2_E | 8.8333 | 0 | SHDW2H.ENERGY * 1 <= 50 (Wt = 360) | Other | Quick
T::T_NIL_3 | 8.8333 | 0 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. Swamped if Tamar CCGT OOS. | NIL | Tas
Q:N_TW330_CB5102_OSC | 8.4167 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage | Qld
Q:N_BI_POT_WIV_N-2 | 8.1667 | 0 | Out= Nil, limit Qld to NSW on QNI to avoid transient instability on trip of both Wivenhoe pumps | Outage | Qld
N>N-NIL_LSDU | 7.9167 | 14.3333 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line This constraint equation binds for high exports from NSW to Qld. | NIL | NSW
Q>NIL_MRTA_B | 7.8333 | 19.6667 | Out = Nil, avoid overloading Middle Ridge to Tangkam (732) 110 kV line on no contingencies | NIL | Qld
S>RB_275KV_N_BUS_1 | 7.75 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | SA
V::N_SMF2_SD2 | 7.75 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage | Vic
T_T_FASH_1_N-2 | 7.5 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
V::N_X_HWSM_SMF2_xxx | 7.3333 | 0 | Out= Hazelwood-South Morang 500kV line & South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#PPCCGT_E | 6.8333 | 16.9167 | SPPT.ENERGY * 1 <= 170 (Wt = 35) | Other | Quick
N^N-967_LS_SVC | 6.8333 | 0 | Out= Koolkhan to Lismore (967) and Lismore SVC, avoid Voltage collapse on CoffsHarbour to Lismore(89) trip; TG formulation only | Outage | NSW
V_OWF_NRB_0 | 6.6667 | 0 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Vic
NC_N_VP5 | 6.5 | 4.4167 | Non Conformance Constraint for Vales Point VP5 Power Station | Other | Non-Conformance
V:SS_820_HY_TEST_DYN | 6.5 | 16 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
#SNOWTWN1_E | 6.25 | 46.25 | SNWF1T.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
Q:N_ARSVC_AR_2L-G | 6.1667 | 0.58333 | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
#HPRL1_L5 | 6 | 0 | (SMTL2H.LOWER5MIN + SMTL2H.LOWERREG) * 1 <= 0 (Wt = 4) | Other | Quick
#HPRL1_L6 | 6 | 0 | SMTL2H.LOWER6SEC * 1 <= 0 (Wt = 8) | Other | Quick
NSA_V_BDL0xxx | 6 | 24.75 | Bairnsdale Unit 1 or 2 >= various levels for Network Support Agreement The binding results from xx constraint equations that set the minimum level of Bairnsdale 1 or 2 generation have been combined. | Outage | Vic
N_BROKENH1_ZERO | 6 | 22.0833 | Broken Hill Solar Farm upper limit of 0 MW | Outage | NSW
#HPRG1_R5 | 5.9167 | 0 | (SMTL1H.RAISE5MIN + SMTL1H.RAISEREG) * 1 <= 0 (Wt = 4) | Other | Quick
#HPRG1_R6 | 5.9167 | 0 | SMTL1H.RAISE6SEC * 1 <= 0 (Wt = 8) | Other | Quick
#HPRL1_L60 | 5.75 | 0 | SMTL2H.LOWER60SEC * 1 <= 0 (Wt = 6) | Other | Quick
N_NYNGANSF_010 | 5.75 | 23.0833 | Nyngan Solar Farm upper limit of 10 MW | Outage | NSW
T>T_FASH_3_N-2 | 5.6667 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV line (flow to Burnie) for loss of both Farrell to Sheffield 220 kV lines | Outage | Tas
S>BGTX_BGBR_HUWT | 5.5 | 0 | Out= Bungama 275/132kV TX, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap windfarm), Feedback | Outage | SA
#VIC1_E_20170319 | 5.4167 | 0 | Multiple VIC1 LHS <= 210 (Wt = 35) | Other | Quick
S:VS_650_HY_TEST | 5.4167 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
V:S_ARDM_560 | 5.4167 | 1.0833 | Maintain maximum transfer limit of 560 MW on Heywood IC from VIC to SA to avoid oscillatory instability | Outage | Vic
V>>V-JNWG_RADIAL_1A | 5.4167 | 6.8333 | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage | Vic
#AGLHAL_P_E | 5.25 | 0 | SHPS1.ENERGY * 1 <= 205 (Wt = 50) | Other | Quick
N>>N-NIL__B_15M | 5.25 | 0.16667 | Out= Nil, avoid O/L Upper Tumut to Canberra (01) using 15 mins rating on trip of Lower Tumut to Canberra (07) line, Feedback | NIL | NSW
V::N_LTWG_xxx | 5.1667 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#HPRG1_R60 | 5 | 0 | SMTL1H.RAISE60SEC * 1 <= 0 (Wt = 6) | Other | Quick
N>N-X_96H+9W2_1 | 5 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Kempsey-Raleigh (9W2) and 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD | Outage | NSW
NSA_Q_BARCALDN | 4.9167 | 46.6667 | Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine for the outage of Clermont to Lilyvale (7153) 132 kV line This constraint equation is used for planned outages of the Clermont to Lilyvale (7153) or Barcaldine to Clermont (7154) 132 kV lines | Outage | Qld
T_V_NIL_FCSPS | 4.9167 | 0.5 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
V::N_DDSM_xxx | 4.9167 | 13.8333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S>>NIL_TBTU_TBCG_1 | 4.8333 | 0 | Out=NIL, avoid O/L Tailem Bend-Cherry Gardens 275kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
T_V_NIL_BL1 | 4.8333 | 1.8333 | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL | Tas
V>V_ROYP6_1AR | 4.8333 | 0 | Out = Rowville to Yallourn No. 6 220 kV line, radial mode, prevent O/L of the Rowville to Yallourn No. 7 or No. 8 220 kV line for trip of the parallel No. 8 or No. 7 220 kV line, Yallourn W1 on 220 kV, feedback | Outage | Vic
NC_N_VP6 | 4.75 | 1.25 | Non Conformance Constraint for Vales Point VP6 Power Station | Other | Non-Conformance
NRM_VIC1_SA1 | 4.75 | 26.75 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
#HPRL1_RR | 4.6667 | 0 | SMTL2H.RAISEREG * 1 <= 0 (Wt = 10) | Other | Quick
NC_N_SITHE01 | 4.6667 | 24.5 | Non Conformance Constraint for Smithfield Energy Facility | Other | Non-Conformance
T::T_HA_GT_PM_5 | 4.6667 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT in service. | Outage | Tas
T_T_FASH_2_N-2 | 4.6667 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh >= 90% of West Coast load | Outage | Tas
V>>V_KTS_TX_A3_2_P | 4.6667 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, all HWPS 220kV bus tied, feedback | Outage | Vic
#DARTM1_E | 4.5833 | 0 | VDPS.ENERGY * 1 <= 185 (Wt = 360) | Other | Quick
#LADBROK1_C_E | 4.5 | 0 | SPEW1.ENERGY * 1 <= 5 (Wt = 48) | Other | Quick
S>BRTW_BWPA_HUWT | 4.4167 | 15.6667 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
#NYNGAN1_E | 4.1667 | 74.9167 | Quick constraint equation to limit Nyngan solar farm to various levels This constraint equation was invoked in 2016 for the Nyngan solar farm commissioning. | Other | Quick
T>T_PMSH_IMP_4C | 4 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
N^N-X_96H_LS_SVC | 3.9167 | 3.1667 | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Coffs Harbour to Lismore (89) trip; TG formulation only | Outage | NSW
N_BOCORWF1_ZERO | 3.9167 | 0 | Boco Rock WF upper limit of 0 MW | Outage | NSW
VN_0850 | 3.9167 | 0.25 | Discretionary Vic to NSW transfer upper limit of 850 MW | Outage | Vic
#HPRG1_LR | 3.75 | 0 | SMTL1H.LOWERREG * 1 <= 0 (Wt = 10) | Other | Quick
N>N-BAMB_132_OPEN_B | 3.75 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage | NSW
V::S_NIL_MAXG_xxx | 3.75 | 397.75 | Out = Nil, avoid transient instability for trip of the largest generation unit in South Australia There are two constraint equations that make up the transient stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
S>>NIL_SETB_SETB_1 | 3.6667 | 11 | Out= Nil, avoid O/L one South East-Tailem Bend 275kV on trip of other South East-Tailem Bend 275kV line, feedback | NIL | SA
T>T_GTSH_IMP_4K | 3.6667 | 103.4167 | Out = Sheffield to Georgetown 220 kV line, avoid overloading Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action | Outage | Tas
N^^Q_LS_VC_B4 | 3.5833 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage | NSW
Q_RS_260 | 3.5833 | 0 | Ross cut-set discretionary upper limit of 260 MW | Outage | Qld
S>X_NWCB6225+6021_T1 | 3.5833 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225 (which also causes an outage of North West Bend to Monash #1 132 kV line), avoid overloading North West Bend 132/66 kV #1 transformer on trip of North West Bend to Morgan Whyalla pump 1 132 kV line | Outage | SA
V>>V_HWYP1_3_TIE | 3.5833 | 0 | Out= Hazelwood to Yallourn No.1 220kV line, avoid O/L Yallourn to Hazelwood No.2 220kV line on trip of Yallourn to Rowville No.7 or No.8 220kV line, all 220kV buses tied at Hazelwood, Feedback | Outage | Vic
NC_V_YWPS1 | 3.5 | 14.3333 | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Other | Non-Conformance
N>N-NIL_MBDU | 3.4167 | 0.083333 | Out = Nil, avoid overloading Mullumbimby to Dunoon (9U6 or 9U7) 132 kV line on trip of the other Mullumbimby to Dunoon (9U7 or 9U6) 132 kV line | NIL | NSW
V>SML_BUDP_2 | 3.4167 | 25.1667 | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage | Vic
S>NIL_NIL_SETX12 | 3.3333 | 1.5 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
CA_MQS_47FE2B0C_01 | 3.25 | 0 | Constraint Automation, O/L FARRELL TRANSF T2 for CTG LTAL on trip of FARRELL_SHEFFIELD #2 220KV LINE. Generated by STNET[MANFL] Host MANEEMP1(MQ) | Outage | Constraint Automation
Q>NIL_MRTA_A | 3.25 | 6.8333 | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Qld
V::S_PP+TIPSB_MG | 3.25 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of half of Pelican Point PS(GT11 + ST18) + largest TIPS B unit declared as credible (South East Capacitor Available). | Outage | SA
N^^V_EPMB_1 | 3.1667 | 0.91667 | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
S>>X_CNRB+CB_02 | 3.1667 | 0 | Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line(this offloads Robertstown #1 275/132kV TX and Trips Hallet Hill WF) | Outage | SA
T>T_TU_LE_WA12_2 | 3.1667 | 0 | Out = either Tungatinah to Waddamana 110kV line (direct or via Lake Echo tee), avoid O/L the remaining Tungatinah to Waddamana 110 kV line (flow to North) on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, feedback | Outage | Tas
V>S_460 | 3.0833 | 3.5833 | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | Outage | Vic
V::S_PP+TIPSB_MG_2 | 3.0833 | 0 | Out =Nil(Note: with both Black Range series capacitors O/S); Vic-SA Tran. Stab limit for loss of SA largest generator with loss of half of Pelican Point PS (GT1 + ST) and largest TIPS B unit declared as credible (South East Capacitor Available). | Outage | SA
V>SML_NSWRB_10 | 3.0833 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
V::N_KTSY_MLSM_ET_xxx | 3 | 2 | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::N_X_HWSM_HWRO_xxx | 3 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
NC_N_TALWA1 | 2.9167 | 6 | Non Conformance Constraint for Tallawarra Power Station | Other | Non-Conformance
NC_Q_BRAEMAR3 | 2.9167 | 4.9167 | Non Conformance Constraint for Braemar 3 Power Station | Other | Non-Conformance
S>>BLMK_BWPA_BRTW | 2.9167 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
#JLA02_E | 2.8333 | 0 | VJLGA2.ENERGY * 1 <= 54 (Wt = 360) | Other | Quick
V::N_X_MLSM_EMTT_xxx | 2.8333 | 5.4167 | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V:SS_820_HY_TEST | 2.8333 | 3.1667 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
NC_S_NBHWF1 | 2.75 | 0 | Non Conformance Constraint for North Brown Hill Windfarm | Other | Non-Conformance
N_TARALGAWF_ZERO | 2.75 | 0 | Taralga WF upper limit of 0 MW | Outage | NSW
N>>N-NIL__3_OPENED & CLOSED | 2.6667 | 61.3333 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
T::T_NIL_2 | 2.6667 | 13.4167 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL | Tas
V>>SML_NIL_1 | 2.6667 | 0.16667 | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
V:S_PA_SVC_600 | 2.5833 | 38.25 | Out= one Para SVC (Note: both Black Range series caps I/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 600 MW | Outage | Vic
NC_Q_BRAEMAR2 | 2.5 | 2.3333 | Non Conformance Constraint for Braemar 2 Power Station | Other | Non-Conformance
NC_S_OSB-AG | 2.5 | 0.25 | Non Conformance Constraint for Osborne Power Station | Other | Non-Conformance
S>NIL_NIL_SGMYSE-T2 | 2.5 | 0 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on Nil trip (for Line component SECS assumed O/S or I/S), Feedback | NIL | SA
S_HPRG1_E | 2.5 | 0 | Out= Nil, Hornsdale Battery generation energy target <= 30 MW | NIL | SA
NC_V_YWPS2 | 2.4167 | 13.25 | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Other | Non-Conformance
N^^V_LTWG | 2.4167 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse in Southern NSW for either loss of the largest VIC generating unit or Basslink, or loss of a Murray to Dederang 330 kV line | Outage | NSW
T>T_FASH_1_N-2 | 2.4167 | 10 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
#MINTARO_C_E | 2.3333 | 0.66667 | SMPS.ENERGY * 1 <= 30 (Wt = 48) | Other | Quick
NC_Q_STAN-3 | 2.3333 | 0.75 | Non Conformance Constraint for Stanwell STAN-3 Power Station | Other | Non-Conformance
NC_V_JLA02 | 2.3333 | 0 | Non Conformance Constraint for Jeeralang A - 02 Power Station | Other | Non-Conformance
T::T_HA_GT_PM_4 | 2.3333 | 0.16667 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Tas
S>>NIL_TBCG_TBTU_1 | 2.25 | 35.25 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | SA
T^V_NIL_8 | 2.25 | 1 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
V>>V_ROTS_TX_2A_R | 2.25 | 99.25 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
VT_ZERO | 2.25 | 628.25 | Victoria to Tasmania on Basslink upper transfer limit of 0 MW 0 | Outage | Vic
S-HDWF2_0 | 2.1667 | 0 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW | Outage | SA
S::V_TBSE_TBSE_1 | 2.1667 | 2.4167 | Out = one Tailembend-South East 275kV line (NOTE: with both Black Range series capacitors I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines | Outage | SA
T>T_LIPM_110_2B | 2.1667 | 0 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
V::S_NIL_TBSE_1 | 2.1667 | 2.8333 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
T>T_NIL_BL_IMP_5F | 2.0833 | 0.083333 | Out = Nil, avoid overloading Hadspen to Georgetown No.1 220 kV line (flow to North) for trip of the Hadspen to Georgetown No.2 220 kV line with no SPS action This constraint only binds when the NCSPS control scheme is unavailable. | NIL | Tas
V>>SML_NIL_8 | 2.0833 | 0.25 | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
V^^S_SETB_TBSE_2 | 2.0833 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | SA
N_MOREESF1_ZERO | 2 | 2.5 | Moree Solar Farm upper limit of 0 MW | Outage | NSW
#DRYCGT3_C_E | 1.9167 | 0 | SDCA3.ENERGY * 1 <= 5 (Wt = 48) | Other | Quick
NC_V_BALDHWF1 | 1.9167 | 0 | Non Conformance Constraint for Bald Hills Wind Farm | Other | Non-Conformance
T>T_SH_TX | 1.9167 | 0.25 | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Tas
NC_Q_CPSA | 1.8333 | 0.75 | Non Conformance Constraint for Condamine Power Station | Other | Non-Conformance
NC_Q_GSTONE5 | 1.8333 | 0.41667 | Non Conformance Constraint for Gladstone 5 Power Station | Other | Non-Conformance
N^^V_LTMS | 1.8333 | 0 | Out = Lower Tumut to Murray 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
S_HDWF1_0 | 1.8333 | 0 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | SA
T>T_NIL_BL_5C | 1.8333 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
V>>V_MLSY_KTSBP_1AR | 1.8333 | 28.5 | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage | Vic
V>V_HWA34_OP2_1 | 1.8333 | 0 | Out = Hazelwood A3 or A4 500/220 kV txfmr, avoid O/L Yallourn to Rowville No. 5 220 kV line on trip of Hazelwood A4 or A3 500/220 kV txfmr, 3/5 parallel mode, Jeeralang B connected to HWPS B3/4 side, feedback | Outage | Vic
VN_0700 | 1.8333 | 0.41667 | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage | Vic
#N-Q-MNSP1_RAMP_I_F | 1.75 | 0.66667 | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Other | Quick
NC_S_SATGS1 | 1.75 | 0 | Non Conformance Constraint for Temp Gen South | Other | Non-Conformance
V:S_MSUT_560 | 1.75 | 0.66667 | Out = Murray - Upper Tumut (65) 330kV line, VIC to SA on Heywood upper transfer limit of 560 MW based on oscillatory stability. | Outage | Vic
V^SML_BAWB_3 | 1.75 | 0 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
#DRYCGT1_C_E | 1.6667 | 0 | SDCA1.ENERGY * 1 <= 5 (Wt = 48) | Other | Quick
N::V_DDMS | 1.6667 | 0 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage | NSW
NC_Q_MPP_2 | 1.6667 | 0.083333 | Non Conformance Constraint for Millmerran 2 Power Station | Other | Non-Conformance
S_BRBG_CMWF_0 | 1.6667 | 0 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | SA
VSML_-100 | 1.6667 | 0 | Vic to SA on ML upper transfer limit of -100 MW | Outage | Vic
NC_Q_STAN-2 | 1.5833 | 3.8333 | Non Conformance Constraint for Stanwell STAN-2 Power Station | Other | Non-Conformance
S>BRDV_BWPA_RHBR | 1.5833 | 0.25 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V>>N-LTUT_B | 1.5833 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
V::N_HWCB_xxx | 1.5 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V^^S_BLKRG_TBSE_2 | 1.5 | 9.8333 | Out = both or one Black Range series capacitors O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
#HPRG1_RR | 1.4167 | 0 | SMTL1H.RAISEREG * 1 <= 0 (Wt = 10) | Other | Quick
#QPS5_O_E | 1.4167 | 0 | SQPS5Q.ENERGY * 1 = 74 (Wt = 55) | Other | Quick
#QPS5_P_E | 1.4167 | 0 | SQPS5Q.ENERGY * 1 <= 0 (Wt = 50) | Other | Quick
NC_N_MP1 | 1.4167 | 4.0833 | Non Conformance Constraint for Mt Piper 1 Power Station | Other | Non-Conformance
S:V_420 | 1.4167 | 0 | South Australia to Victoria on both Heywood and Murraylink maximum transfer limit to avoid oscillatory instability This constraint equation was added, in January 2011, to a number of outage constraint sets across the NEM (except for Tasmania). The 420 MW value is the previous system normal limit. Throughout 2011 AEMO conducted studies as to whether the 420 MW limit was appropriate for various outages. In some cases the limit was increased. This work will continue in 2012. | Outage | SA
T::T_HA_GT_PM_3 | 1.4167 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. | Outage | Tas
NC_S_PPCCGT | 1.3333 | 0.41667 | Non Conformance Constraint for Pelican Point Power Station | Other | Non-Conformance
S_HPRL1_E | 1.3333 | 0 | Out= Nil, Hornsdale Battery load energy target <= 30 MW | NIL | SA
T>T_NIL_LIPM_N-2_2B | 1.3333 | 1.5833 | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to South) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
T>T_TUNN3_110_2 | 1.3333 | 0 | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Tas
V>>DDSH_DDGN_N-2 | 1.3333 | 0.66667 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage | Vic
NRM_SA1_VIC1 | 1.25 | 7.4167 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue
S>>CNLK_MKRB_WEMWP4 | 1.25 | 0 | Out= Canowie-Mt Lock 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV on trip of Mokota-Robertstown 275kV line( this offloads Belalie-Mokota 275kV line and trips Hallet Hill WF), Feedback | Outage | SA
S_HDWF3_0 | 1.25 | 0 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW | Outage | SA
S_LB2WF_CONF | 1.25 | 2.4167 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
#HPRL1_LR | 1.1667 | 0 | SMTL2H.LOWERREG * 1 <= 0 (Wt = 10) | Other | Quick
N>>N-NIL__S | 1.1667 | 1.5833 | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL | NSW
NC_Q_CPP_4 | 1.1667 | 0.25 | Non Conformance Constraint for Callide C CPP_4 | Other | Non-Conformance
S>NIL_BWMP_HUWT | 1.1667 | 13.4167 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
T^V_NIL_9 | 1.1667 | 23.6667 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
V>V_ROYP6_1BR | 1.1667 | 0 | Out = Rowville to Yallourn No. 6 220 kV line, radial mode, prevent O/L of the Rowville to Yallourn No. 7 or No. 8 220 kV line for trip of the Yallourn to Hazelwood No. 1 220 kV line (offloads HWPS-ROTS 1 & 2 220kV lines), Yallourn W1 on 500kV, feedback | Outage | Vic
V_S_ROCOF | 1.1667 | 31.8333 | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage | Vic
NC_V_LOYYB2 | 1.0833 | 0 | Non Conformance Constraint for Loy Yang B2 Power Station | Other | Non-Conformance
S>>CNRB_MKRB_WEMWP4 | 1.0833 | 13.75 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | SA
S>NIL_EDES_EDSB | 1.0833 | 0 | Out= NIL, avoid O/L Edinburgh-Salisbury 66kV line on trip of Edinburgh-Elizabeth South 66kV line, Feedback | NIL | SA
S>NIL_NIL_SGBN | 1.0833 | 0 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | SA
T>T_PMSH_2A | 1.0833 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow to George Town) for trip of the other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
T>T_TUMBNN2_110_3 | 1.0833 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.2 110kV lines, avoid O/L Tungatinah to New Norfolk No.3 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV line, Feedback | Outage | Tas
TV_550 | 1.0833 | 0 | Tas to Vic on Basslink upper limit of 550 MW | Outage | Tas
T^T_LIPM_1_DS | 1.0833 | 0 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line, dispatch only | Outage | Tas
T_MA_WESTCOAST_2 | 1.0833 | 0 | Limit Mackintosh to 90% of West Coast load | Outage | Tas
V>>V_NIL_1B | 1.0833 | 1.75 | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL | Vic
V_MORTLAKE12_ZERO | 1.0833 | 0 | Mortlake unit 1 & 2 upper limit of 0 MW | Outage | Vic
NC_Q_MPP_1 | 1 | 0.41667 | Non Conformance Constraint for Millmerran 1 Power Station | Other | Non-Conformance
N^^Q_AR_VC_B4 | 1 | 0 | Out= Armidale SVC, avoid Voltage Collapse on loss of Tarong North | Outage | NSW
N^^Q_TW_330_BUS3_B1 | 1 | 0 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | NSW
N^^V_DDSM2 | 1 | 3.4167 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse for loss of remaining Dederang to South Morang 330 kV line | Outage | NSW
V>NWBCB6225_TX1 | 1 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 132/66kV TX1 on trip of Monash-North West Bend #2 132kV line, Feedback | Outage | Vic
CA_SPS_482F72C7_01 | 0.91667 | 0 | Constraint Automation, O/L HWPS_YPS1_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
NC_N_MP2 | 0.91667 | 1.9167 | Non Conformance Constraint for Mt Piper 2 Power Station | Other | Non-Conformance
NC_Q_STAN-4 | 0.91667 | 0.5 | Non Conformance Constraint for Stanwell STAN-4 Power Station | Other | Non-Conformance
NC_Q_YABULU2 | 0.91667 | 0.25 | Non Conformance Constraint for Yabulu 2 Power Station | Other | Non-Conformance
NQ_000 | 0.91667 | 0 | NSW to Qld on QNI upper transfer limit of 0 MW | Outage | NSW
NRM_VIC1_NSW1 | 0.91667 | 2.0833 | Negative Residue Management constraint equation for VIC to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
QNTE_ZERO | 0.91667 | 3 | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW | Outage | Qld
N>>N-NIL__2_OPENED & CLOSED | 0.83333 | 0.75 | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | NSW
NC_Q_TNPS1 | 0.83333 | 2.25 | Non Conformance Constraint for Tarong North Power Station | Other | Non-Conformance
N^^Q_LS_VC_B1 | 0.83333 | 4.4167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
S>V_460_DYN | 0.83333 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | SA
V>>V_NIL_8 | 0.83333 | 1.4167 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL | Vic
NC_Q_BRAEMAR1 | 0.75 | 5.8333 | Non Conformance Constraint for Braemar 1 Power Station | Other | Non-Conformance
NC_Q_GSTONE2 | 0.75 | 0.41667 | Non Conformance Constraint for Gladstone 2 Power Station | Other | Non-Conformance
NC_Q_OAKEY1 | 0.75 | 0 | Non Conformance Constraint for Oakey 1 Power Station | Other | Non-Conformance
NC_Q_SWAN_E | 0.75 | 0 | Non Conformance Constraint for Swanbank E Power Station | Other | Non-Conformance
S-SNWF_WPWF_120 | 0.75 | 0 | Discretionary upper limit for Snowtown WF + Wattle Pt WF generation <= 120 MW | Outage | SA
S>>DVBL_LKDV_WEWT | 0.75 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East- Waterloo 132kV on trip of Mt Lock-Davenport 275kV line, Feedback | Outage | SA
S>>PARB_RBTU_WEWT | 0.75 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
V>>N-LTUT_2_30 | 0.75 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L using 30 mins rating on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
V_ARARAT_5 | 0.75 | 10.3333 | Ararat Wind Farm upper limit of 5 MW, limit to manage islanding risk | Outage | Vic
#HALLWF1_E | 0.66667 | 22.5833 | SHPS2W.ENERGY * 1 <= 5 (Wt = 360) | Other | Quick
#SATGS1_E | 0.66667 | 0 | SMVG1L.ENERGY * 1 = 15 (Wt = 30) | Other | Quick
NC_N_WRWF1 | 0.66667 | 0 | Non Conformance Constraint for White Rock Wind Farm | Other | Non-Conformance
NC_Q_TARONG#4 | 0.66667 | 0.58333 | Non Conformance Constraint for Tarong 4 Power Station | Other | Non-Conformance
NC_Q_YABULU | 0.66667 | 0.58333 | Non Conformance Constraint for Yabulu Power Station | Other | Non-Conformance
NC_S_HDWF2 | 0.66667 | 0 | Non Conformance Constraint for Hornsdale 2 Wind Farm | Other | Non-Conformance
NC_S_SATGN1 | 0.66667 | 0 | Non Conformance Constraint for Temp Gen North | Other | Non-Conformance
NC_V_YWPS3 | 0.66667 | 11.4167 | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Other | Non-Conformance
S>>BLMK_NIL_WEMWP4 | 0.66667 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on Nil trip, Feedback | NIL | SA
S>>KHKN_SETB_SETB | 0.66667 | 0 | Out= Keith-Kincraig 132 kV line (Note: with both Black Range series caps I/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage | SA
S>>WTTP_WERB_STBG | 0.66667 | 0 | Out= Waterloo-Templers 132kV line, avoid O/L Snowtown-Bungama T 132kV line on trip of Waterloo East-MWP4-Robertstown 132kV line, Feedback | Outage | SA
S_TIPSB2+B1_270 | 0.66667 | 0 | Discretionary upper limit for TIPS B2 + B1 <= 270 MW | Outage | SA
V::N_EPMB_xxx | 0.66667 | 7 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>N-NIL_HG | 0.66667 | 3.5 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
V>>SML_BESH_2 | 0.66667 | 0 | Out = Bendigo to Shepparton 220 kV line, avoid O/L Darlington Pt to Balranald to Buronga (X5/1 & X5/3) 220kV line on loss of Ballarat to Bendigo 220kV line, feedback | Outage | Vic
V_OAKLANDSHILL_42 | 0.66667 | 0 | Oaklands Hill Windfarm upper limit of 42 MW | Outage | Vic
#SATGN1_E | 0.58333 | 0 | SPAG1E.ENERGY * 1 = 15 (Wt = 30) | Other | Quick
#V-SA_RAMP_I_F | 0.58333 | 0.25 | V-SA >= MIN(-52, InitialFlow + 50) (Wt=35) | Other | Quick
N>N-BAMB_132_OPEN_A | 0.58333 | 68.75 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | NSW
NC_N_HUMENSW | 0.58333 | 4.5 | Non Conformance Constraint for Hume Hydro Power Station | Other | Non-Conformance
NC_S_MINTARO | 0.58333 | 0.25 | Non Conformance Constraint for Mintaro Gas Turbine | Other | Non-Conformance
NC_V_LOYYB1 | 0.58333 | 0.16667 | Non Conformance Constraint for Loy Yang B1 Power Station | Other | Non-Conformance
S>NIL_LKDV_CNRB | 0.58333 | 0 | Out= NIL, avoid O/L Canowi-Robertstown 275kV on trip of Mt Lock-Davenport 275kV line, Feedback | NIL | SA
T>T_BUSH1_220 | 0.58333 | 0 | Out = Burnie to Sheffield 220kV line, West Coast 220/110 kV parallel open, avoid O/L a Sheffield 220/110kV transformer for loss of the other Sheffield 220/110kV transformer | Outage | Tas
T_T_BA_JB_RC2_250 | 0.58333 | 3.25 | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
V::N_HORC_xxx | 0.58333 | 2 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#ARWF1_E | 0.5 | 5.4167 | VART1A.ENERGY * 1 <= 140 (Wt = 35) | Other | Quick
NC_Q_STAN-1 | 0.5 | 0.91667 | Non Conformance Constraint for Stanwell STAN-1 Power Station | Other | Non-Conformance
NC_V_YWPS4 | 0.5 | 12 | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Other | Non-Conformance
Q>STBS_STBS_BADU | 0.5 | 0 | Out= Stanwell to Broadsound (856 or 8831), avoid O/L Baralaba to Duaringa (7113/1) on trip of remaining Stanwell to Broadsound (856 or 8831) | Outage | Qld
S>>NIL_TBTU_TBMO_1 | 0.5 | 4.5 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
S^NIL_PL_MAX | 0.5 | 4.1667 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
T>T_PMSH_IMP_4D | 0.5 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
V::N_MLTR_xxx | 0.5 | 0.91667 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::N_SMF2_SD1 | 0.5 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage | Vic
V::N_X_HWSM_ROSM_xxx | 0.5 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_BLKRG_TBSE_2 | 0.5 | 55 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
V::S_NIL_SETB_SECP_1 | 0.5 | 1.25 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
VSML_-050 | 0.5 | 0 | Vic to SA on ML upper transfer limit of -50 MW | Outage | Vic
V_ARARAT_ZERO | 0.5 | 0.5 | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
CA_MQS_48D013FF_01 | 0.41667 | 0 | Constraint Automation, O/L ROBMW4_2 @MW_4 for CTG LSII on trip of BELALI-MOKOTA 275KV LINE. Generated by STNET[MANBL] Host MANEEMP1(MQ) | Outage | Constraint Automation
I_CTRL_ISSUE_ML | 0.41667 | 6.3333 | DC Link Control Issue Constraint for Murraylink | Outage | Other
NC_N_BW03 | 0.41667 | 0.083333 | Non Conformance Constraint for Bayswater 3 Power Station | Other | Non-Conformance
NC_N_ER01 | 0.41667 | 0 | Non Conformance Constraint for Eraring ER01 Power Station | Other | Non-Conformance
NC_Q_CPP_3 | 0.41667 | 0.41667 | Non Conformance Constraint for Callide C CPP_3 | Other | Non-Conformance
NC_Q_TARONG#2 | 0.41667 | 0.25 | Non Conformance Constraint for Tarong 2 Power Station | Other | Non-Conformance
NC_S_TORRB4 | 0.41667 | 0 | Non Conformance Constraint for Torrens B4 Power Station | Other | Non-Conformance
N_BLOWERNG_ZERO | 0.41667 | 0 | Blowering generation upper limit of 0 MW | Outage | NSW
N_GUNNING1_ZERO | 0.41667 | 5.25 | Discretionary upper limit for Gunning generation of 0 MW | Outage | NSW
T>T_NIL_BL_IMP_3F | 0.41667 | 0.083333 | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220 kV line with no SPS action, feedback | NIL | Tas
T>T_PMSH_2B | 0.41667 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
V::N_KGRC_xxx | 0.41667 | 9.6667 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>NWCB6024+25_TX1 | 0.41667 | 0 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #1 132/66kV TX on trip of Monash-North West Bend #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | Vic
VS_500 | 0.41667 | 0 | VIC to SA on Heywood upper transfer limit of 500 MW | Outage | Vic
V^^S_NIL_MAXG_xxx | 0.41667 | 0 | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off There are two constraint equations that make up the voltage stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
#NSW1-QLD1_RAMP_E_F | 0.33333 | 0 | NSW1-QLD1 <= MAX(190, InitialFlow - 200) (Wt=35) | Other | Quick
#T-V-MNSP1_RAMP_E_F | 0.33333 | 0.16667 | T-V-MNSP1 >= MIN(0, InitialFlow + 200) (Wt=35) | Other | Quick
N>>N-NIL_64 | 0.33333 | 1 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | NSW
N>>N-NIL__H_15M | 0.33333 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | NSW
NC_Q_TARONG#3 | 0.33333 | 0 | Non Conformance Constraint for Tarong 3 Power Station | Other | Non-Conformance
NC_V_JLB02 | 0.33333 | 0 | Non Conformance Constraint for Jeeralang B - 02 Power Station | Other | Non-Conformance
S:V_580 | 0.33333 | 0 | Out = One Heywood 500/275 kV txfmr (two remain in service), maintain maximum SA to VIC transfer limit of 580 MW on Heywood and Murraylink combined to avoid oscillatory instability | Outage | SA
T^T_LFWA_1_DS | 0.33333 | 0 | Out = Lindisfarne to Waddamana 220 kV line, avoid voltage instability or violations for loss of the other Lindisfarne to Waddamana 220 kV line line, dispatch only | Outage | Tas
V::N_HYMO_xxx | 0.33333 | 0.58333 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>N-LTWG_RADIAL_1 | 0.33333 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
V>>V_NIL_1A | 0.33333 | 1.25 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
VSML_-040 | 0.33333 | 0 | Vic to SA on ML upper transfer limit of -40 MW | Outage | Vic
V^SML_HORC_3 | 0.33333 | 0 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
#DRYCGT2_C_E | 0.25 | 0 | SDCA2.ENERGY * 1 <= 5 (Wt = 48) | Other | Quick
#STAN-3_E | 0.25 | 0 | QSTN3.ENERGY * 1 <= 260 (Wt = 360) | Other | Quick
#TORRB3_E | 0.25 | 0 | STSB3.ENERGY * 1 <= 0 (Wt = 50) | Other | Quick
#V-SA_RAMP_E_F | 0.25 | 0.083333 | V-SA <= MAX(50, InitialFlow - 30) (Wt=35) | Other | Quick
N>N-X_96H+9W2+9W5_1 | 0.25 | 0 | Out= Coffs Harbour-Koolkhan (96H) & Raleigh-Kempsey(9W2) & Macksville-Kempsey(9W5), avoid O/L Armidale-Coffs Harbour (96C) on trip of Armidale-Coffs Harbour (87), Swamp out when all 3 directlink cable O/S,Feedback, TG formulation in PD/ST | Outage | NSW
NC_N_LD03 | 0.25 | 0.25 | Non Conformance Constraint for Liddell LD03 Power Station | Other | Non-Conformance
NC_Q_KAREEYA3 | 0.25 | 0 | Non Conformance Constraint for Kareeya 3 Power Station | Other | Non-Conformance
Q>>BCRG_CLWU_BCCP | 0.25 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
Q_BRBRA_8839 | 0.25 | 0 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 | Outage | Qld
S_SECB_LG-1 | 0.25 | 0 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
T>>T_GTHA_EXP_3H | 0.25 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T>T_BWLF_110_4 | 0.25 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana 110 kV line, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Tas
V::N_SMSC_xxx | 0.25 | 19.0833 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>V_HWYP2_1_R | 0.25 | 0 | Out = Hazelwood to Yallourn No. 2 220 kV line, avoid O/L Yallourn to Hazelwood PS No.1 220kV line on trip of Yallourn to Rowville No.5 220kV line, Radial mode, YWG1 on 220kV, Feedback | Outage | Vic
VN_0800 | 0.25 | 3.6667 | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage | Vic
VSML_-080 | 0.25 | 0 | Vic to SA on ML upper transfer limit of -80 MW | Outage | Vic
#NSW1-QLD1_I_E | 0.16667 | 0 | NSW1-QLD1.ENERGY * -1 >= 100 (Wt = 0.0001) | Other | Quick
N>>N-NIL_01N | 0.16667 | 3.5833 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | NSW
N>>N-NIL__A_15M | 0.16667 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Upper Tumut to Canberra (01) line, Feedback | NIL | NSW
N>>V-X_BUDP_DDMS_A | 0.16667 | 0 | Out= Dederang to Murray (67 or 68) and Darlington Point to Buronga (X5) line, avoid the other Murray to Dederang (68 or 67) O/L on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback, Feedback | Outage | NSW
N>N-KKLS_TE_2 | 0.16667 | 0 | Out = Koolkhan to Lismore (967) 132 kV line, avoid overloading the Armidale to Glen Innes (96T) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects that this constraint equation will continue to bind for a reasonable portion of any future outage times. | Outage | NSW
NC_N_BW01 | 0.16667 | 0.083333 | Non Conformance Constraint for Bayswater 1 Power Station | Other | Non-Conformance
NC_Q_DDPS1 | 0.16667 | 0.33333 | Non Conformance Constraint for Darling Downs Power Station | Other | Non-Conformance
NC_S_QPS5 | 0.16667 | 0.083333 | Non Conformance Constraint for Quarantine QPS5 Power Station | Other | Non-Conformance
NC_S_TORRA1 | 0.16667 | 0 | Non Conformance Constraint for Torrens A1 Power Station | Other | Non-Conformance
NC_S_TORRB2 | 0.16667 | 0 | Non Conformance Constraint for Torrens B2 Power Station | Other | Non-Conformance
NC_S_TORRB3 | 0.16667 | 0.083333 | Non Conformance Constraint for Torrens B3 Power Station | Other | Non-Conformance
NC_V_BDL01 | 0.16667 | 1.6667 | Non Conformance constraint equation for Bairnsdale 1 Power Station | Other | Non-Conformance
NC_V_BDL02 | 0.16667 | 1 | Non conformance constraint equation for Bairnsdale 2 power station | Other | Non-Conformance
NC_V_HWPS3 | 0.16667 | 1.9167 | Non Conformance Constraint for Hazelwood HWPS 3 Power Station | Other | Non-Conformance
NC_V_JLA01 | 0.16667 | 0.25 | Non Conformance Constraint for Jeeralang A - 01 Power Station | Other | Non-Conformance
NC_V_LYA2 | 0.16667 | 0.083333 | Non Conformance Constraint for Loy Yang A2 Power Station | Other | Non-Conformance
Q:N_AR_CP2_BI_POT | 0.16667 | 0 | Out = Armidale capacitor bank (120MVAr), Qld to NSW on QNI Transient Stability Limit, Loss of Boyne Island 375MW potline, 1 or 2 Millmerran units I/S | Outage | Qld
S>BLMK_BWPA_CNRB | 0.16667 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Canowi-Robertstown 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>V_NWRB2_RBNW1 | 0.16667 | 35 | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage | SA
T>T_NIL_BL_110_8 | 0.16667 | 0 | Out = Nil, avoid overloading the New Norfolk to Creek Road 110 kV line (flow to south) for loss of the New Norfolk to Chapel St 110 kV line | NIL | Tas
T>T_NIL_BL_3C | 0.16667 | 0 | Out = Nil, avoid overloading a Hadspen to Palmerston 220 kV line for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action | NIL | Tas
TV_560 | 0.16667 | 0 | Tas to Vic on Basslink upper limit of 560 MW | Outage | Tas
TV_575 | 0.16667 | 0 | Tas to Vic on Basslink upper limit of 575 MW | Outage | Tas
T_FATI | 0.16667 | 0 | Out=Farrell-Tribute 220KV line. Energy <= 0MW | Outage | Tas
T_T_FASH_3_N-2 | 0.16667 | 0 | Out = Nil, loss of both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, Hampshire link open, constrain Reece Unit 1 to 0 MW as per Transend advice | Outage | Tas
V::S_NIL_SETB_SECP_2 | 0.16667 | 0.75 | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
V>>N-DPWG_X5_A | 0.16667 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Buronga (X5), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
V>>N-LTUT_G | 0.16667 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage | Vic
V>>V_BAEL_1 | 0.16667 | 0 | Out = Ballarat to Elaine 220 kV line section, avoid O/L Moorabool to Ballarat No. 1 220 kV line on trip of Moorabool to Terang 220 kV line, feedback | Outage | Vic
V>>V_DDSM_1 | 0.16667 | 20.8333 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Vic
V>>V_LTMS_1 | 0.16667 | 0 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage | Vic
V>SML_NSWRB_9 | 0.16667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Bendigo to Kerang 220 kV line for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
V>V_HWA34_OP2_2 | 0.16667 | 0 | Out = Hazelwood A3 or A4 500/220 kV txfmr, avoid O/L Yallourn to Rowville No. 7 or No. 8 220 kV line on trip of Hazelwood A4 or A3 500/220 kV txfmr, 3/5 parallel mode, Jeeralang B connected to HWPS B3/4 side, feedback | Outage | Vic
V>V_NIL_RADIAL_10 | 0.16667 | 1.8333 | Out = Nil, avoid O/L of Yallourn to Rowville No. 7 or No. 8 220 kV line for trip of the Yallourn to Rowville No. 8 or No. 7 220 kV line. Yallourn W1 on 220 kV side. Feedback | NIL | Vic
V^^S_KHKN_SETB | 0.16667 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
V^^S_NIL_SETB_SECP_1 | 0.16667 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Long Term Voltage Stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
V_OAKLANDSHILL_ZERO | 0.16667 | 0 | Oaklands Hill Windfarm upper limit of 0 MW | Outage | Vic
N^^V_MSUTLT_2 | 0.16667 | 0 | Out = Murray to Upper Tumut or Murray to Lower Tumut 330 kV line, avoid voltage collapse in Southern NSW for loss of Murray to Lower Tumut or Murray to Upper Tumut 330 kV line | Outage | NSW
#EILDON1_E | 0.083333 | 0 | VEPS1.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
CA_MQS_4780983C_01 | 0.083333 | 0 | Constraint Automation, O/L TABSES_2 @S_EAST for CTG LSIC on trip of T_BEND-S_EAST 275KV 1 LINE. Generated by STNET[MANBL] Host MANEEMP2(MQ) | Outage | Constraint Automation
CA_MQS_47B62C84_01 | 0.083333 | 0 | Constraint Automation, O/L SNWHUM_T @BUNGAM for CTG LS5R on trip of MINTAR-W_LOO 132KV LINE. Generated by STNET[MANFR] Host MANEEMP1(MQ) | Outage | Constraint Automation
N::Q_LDNC_TNT | 0.083333 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage | NSW
NC_N_ER02 | 0.083333 | 0.083333 | Non Conformance Constraint for Eraring ER02 Power Station | Other | Non-Conformance
NC_N_ER04 | 0.083333 | 0.33333 | Non Conformance Constraint for Eraring ER04 Power Station | Other | Non-Conformance
NC_Q_BARRON-2 | 0.083333 | 1.8333 | Non Conformance Constraint for Barron Gorge 2 Power Station | Other | Non-Conformance
NC_Q_GSTONE3 | 0.083333 | 0.16667 | Non Conformance Constraint for Gladstone 3 Power Station | Other | Non-Conformance
NC_Q_GSTONE4 | 0.083333 | 0.16667 | Non Conformance Constraint for Gladstone 4 Power Station | Other | Non-Conformance
NC_Q_GSTONE6 | 0.083333 | 0.58333 | Non Conformance Constraint for Gladstone 6 Power Station | Other | Non-Conformance
NC_Q_KPP_1 | 0.083333 | 0.5 | Non Conformance Constraint for Kogan Creek Power Station | Other | Non-Conformance
NC_Q_TARONG#1 | 0.083333 | 0.5 | Non Conformance Constraint for Tarong 1 Power Station | Other | Non-Conformance
NC_S_LKBONNY2 | 0.083333 | 0 | Non conformance constraint equation for Lake Bonney 2 wind farm | Other | Non-Conformance
NC_T_POAT220 | 0.083333 | 0.083333 | Non Conformance Constraint for Poatina 220kV Power Station | Other | Non-Conformance
NC_T_TUNGATIN | 0.083333 | 0.16667 | Non Conformance Constraint for Tungatinah Power Station | Other | Non-Conformance
NC_V_HWPS7 | 0.083333 | 1 | Non Conformance Constraint for Hazelwood HWPS 7 Power Station | Other | Non-Conformance
NC_V_HWPS8 | 0.083333 | 3.3333 | Non Conformance Constraint for Hazelwood HWPS 8 Power Station | Other | Non-Conformance
NC_V_MORTLK11 | 0.083333 | 0 | Non Conformance Constraint for Mortlake GT unit 1 | Other | Non-Conformance
NC_V_NPS | 0.083333 | 1 | Non Conformance Constraint for Newport Power Station | Other | Non-Conformance
N^^N_NIL_1 | 0.083333 | 1.4167 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
N^^V_LTUT_1 | 0.083333 | 0 | Out = lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
N_MBTE1_A | 0.083333 | 3.1667 | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
S-SNWF_WPWF_140 | 0.083333 | 0 | Discretionary upper limit for Snowtown WF + Wattle Pt WF generation <= 140 MW | Outage | SA
S>>BRTW_MKRB_WEMWP4 | 0.083333 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV on trip of Mokota-Robertstown 275kV(this trips Hallet Hill WF and offloads Belalie-Mokota 275kV line), Feedback | Outage | SA
S>>NIL_CNRB_WEMWP4 | 0.083333 | 0 | Out= Nil, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line (this offloads Mt Lock-Canowie 275kV line and trips Hallet WF and GTs), Feedback | NIL | SA
S>V_NIL_SETX_SETX1 | 0.083333 | 1.4167 | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL | SA
T>>T_NIL_BL_EXP_6E | 0.083333 | 79.5833 | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL | Tas
T>T_NIL_110_26_HM | 0.083333 | 0 | Out = Nil, West Coast 220/110 kV parallel closed, avoid overloading Waratah Tee to Hampshire 110 kV line for loss of a Farrell to Sheffield 220 kV line, feedback | NIL | Tas
T>T_NIL_BL_IMP_5FF | 0.083333 | 0.083333 | Out = Nil, avoid overloading Hadspen to Georgetown No.2 220 kV line for trip of the Hadspen to Georgetown No.1 220 kV line with no SPS action | NIL | Tas
T>T_PMSH_IMP_4B | 0.083333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T^V_NIL_BLCAP | 0.083333 | 1.8333 | Outage = Nil, Basslink HF7 98 MVAr cap bank unavailable, limit Basslink to 460 MW at George Town under conditions of low George Town 220 kV voltage. | NIL | Tas
T^^V_GTSH_1 | 0.083333 | 2.5 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
T_T_X_FASH_A | 0.083333 | 0 | Out = both Farrell to Sheffield lines, limit West Coast gen <= 110% of West Coast load | Outage | Tas
V::S_KHKN_SETB_2-DS | 0.083333 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of South East - Tailem Bend 275kV line.(NOTE:DS RHS ONLY) | Outage | SA
V>>N-LTUT_A | 0.083333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
V>V_NIL_RADIAL_3-4_7 | 0.083333 | 0 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split) | NIL | Vic
V>X_NWCB6225+6021_T1 | 0.083333 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225, avoid overloading North West Bend 132/66 kV #1 transformer on trip of North West Bend to Morgan Whyalla pump 1 132 kV line | Outage | Vic
VSML_VFRB_OFF | 0.083333 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL | Vic
V^^S_NIL_TBSE_1 | 0.083333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA

## Binding FCAS
Constraint Equation ID | 2017 Hours | 2016 Hours | Description | Type
F_I+NIL_MG_R5 | 7929.5 | 4108 | NEM raise 5 minute requirement for a NEM generation event The largest unit is usually Kogan Creek or one of the large NSW units. | NIL
F_I+NIL_MG_R6 | 7512.9167 | 3955 | NEM raise 6 second requirement for a NEM generation event | NIL
F_I+NIL_RREG | 7314 | 1339.5 | NEM Raise Regulation Requirement | NIL
F_I+NIL_MG_R60 | 7166 | 3886.25 | NEM raise 60 second requirement for a NEM generation event | NIL
F_I+LREG_0120 | 6988.9167 | 1434 | NEM Lower Regulation Requirement greater than 120 MW | NIL
F_I+ML_L6_0400 | 4516.3333 | 2899.5833 | NEM lower 6 second requirement for a NEM load event | NIL
F_I+NIL_APD_TL_L5 | 3631.6667 | 3203.25 | NEM lower 5 min Service Requirement for the loss of APD potlines | NIL
F_I+NIL_APD_TL_L60 | 3281.75 | 3140.8333 | NEM lower 60 sec Service Requirement for the loss of APD potlines | NIL
F_I+ML_L5_0400 | 3037.4167 | 667.5833 | NEM lower 5 minute requirement for a NEM load event The largest single load in the NEM is 400 MW at Boyne Island in Queensland. | NIL
F_MAIN++ML_L6_0400 | 2107.5833 | 354.9167 | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_BL_L60 | 1749.4167 | 228.5 | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL
F_MAIN++NIL_MG_R60 | 1562.25 | 635.1667 | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_I+ML_L60_0400 | 1534.8333 | 354.75 | NEM lower 60 second requirement for a NEM load event | NIL
F_MAIN++ML_L5_0400 | 1528.75 | 86.1667 | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_MAIN++LREG_0120 | 1335.4167 | 50.8333 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL
F_T+NIL_MG_R6 | 1325.1667 | 2952.0833 | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL
F_MAIN++APD_TL_L5 | 1308.3333 | 871.8333 | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
F_T+NIL_MG_R60 | 1220.75 | 2927.4167 | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R6 | 1204.9167 | 1214.9167 | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T++RREG_0050 | 1154.6667 | 294.0833 | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R6 | 1139.6667 | 395.4167 | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 1139.1667 | 249.5833 | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 1136.5 | 1199.8333 | Tasmania raise 60 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R60 | 1115.9167 | 395.9167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R6 | 1092.5833 | 465.75 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_DYN_RREG | 869.5833 | 2473.1667 | Mainland raise regulation requirement, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS | NIL
F_T+NIL_WF_TG_R5 | 864.8333 | 561.5833 | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_DYN_LREG | 862.25 | 4040 | Mainland lower regulation requirement, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS | NIL
F_MAIN++APD_TL_L60 | 851.8333 | 317.6667 | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
F_T+NIL_MG_R5 | 762.5833 | 900.3333 | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R5 | 718.25 | 469.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN+TASCAP_LREG | 675.8333 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_T+RREG_0050 | 497.1667 | 4175.25 | Tasmania raise regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 483.3333 | 4169.6667 | Out = Nil, raise 5 min requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 483.3333 | 4169.6667 | Out = Nil, raise 6 sec requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL
F_T+NIL_ML_L6 | 483.25 | 194.9167 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 483.25 | 4169.6667 | Out = Nil, raise 60 sec requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL
F_T+LREG_0050 | 483.25 | 4176.8333 | Tasmania lower regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L60 | 481.8333 | 197.4167 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN+ML_L6_0400 | 466.25 | 3590.8333 | Out = Nil, lower 6 sec requirement for a Mainland load event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN+TASCAP_RREG | 436.1667 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_MAIN+LREG_0120 | 431.75 | 84.5833 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_RREG | 424.9167 | 71.6667 | Mainland Raise Regulation Requirement, Basslink unable transfer FCAS | NIL
F_MAIN+ML_L5_0400 | 323.1667 | 57.25 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN++ML_L60_0400 | 281.6667 | 16.9167 | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_MAIN+ML_L60_0400 | 275.75 | 51.25 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_T++NIL_MG_RECL_R60 | 270.5833 | 22.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++NIL_MG_RECL_R6 | 264.0833 | 27.0833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++NIL_ML_L60 | 205.6667 | 121.0833 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_T+NIL_ML_L5 | 184.0833 | 0 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L5 | 178.5 | 4087 | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 178.0833 | 4079 | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink unable to transfer FCAS | NIL
F_S+LREG_0035 | 158.5833 | 531.5 | South Australia lower regulation FCAS requirement greater than 35 MW This constraint equation is normally invoked for a risk of islanding or an islanded South Australia | Outage
F_S+RREG_0035 | 155.75 | 532.4167 | South Australia raise regulation FCAS requirement greater than 35 MW This constraint equation is normally invoked for a risk of islanding or an islanded South Australia | Outage
F_T++NIL_WF_TG_R60 | 143.1667 | 60.3333 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_I+ML_L6_APD | 142 | 41.75 | NEM lower 6 second requirement for loss of APD potlines | Outage
F_T++NIL_WF_TG_R6 | 123.5 | 61 | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS Out= Nil, Tasmania raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++NIL_ML_L6 | 119.25 | 92.25 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_Q++ARDM_L60 | 108.0833 | 0 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 60 second requirement | Outage
F_Q++ARDM_L6 | 107.25 | 0 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage
F_T++LREG_0050 | 93.0833 | 47.9167 | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_Q++ARDM_L5 | 91.8333 | 0 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage
F_T++NIL_MG_RECL_R5 | 88.0833 | 28.5 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN++NIL_RREG | 87.6667 | 11.5 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL
F_V_APD01_R5 | 64.4167 | 27.3333 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage
F_V_APD01_R6 | 64.4167 | 27.5 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage
F_V_APD01_R60 | 64.4167 | 27.1667 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage
F_S++HYSE_L6_1 | 62.3333 | 53 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA lower 6 sec Requirement for risk of islanding, segment1 | Outage
F_Q++ARTW_L6 | 62.25 | 11.75 | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
F_Q++ARTW_L60 | 61.5833 | 11.75 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_V_APD01_L5 | 60.0833 | 26 | Out= NIL, APD Potline 1 L5 Requirement <= 0MW | Outage
F_T++NIL_MG_R60 | 57.4167 | 126 | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_T++NIL_MG_R6 | 56.9167 | 160.5833 | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_T++NIL_WF_TG_R5 | 55.6667 | 77.5 | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS In Nov 2013 educe by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_V_APD01_L60 | 53.1667 | 22.6667 | Out= NIL, APD Potline 1 L60 Requirement <= 0MW | Outage
F_V_APD01_L6 | 50.1667 | 22 | Out= NIL, APD Potline 1 L6 Requirement <= 0MW | Outage
F_S++HYSE_L60 | 45.8333 | 26.5 | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage
F_N_GUTHEGA_LREG | 44.1667 | 0 | Out= NIL, Guthega LREG Requirement <= 0MW | Outage
F_N_GUTHEGA_RREG | 43.8333 | 0 | Out= NIL, Guthega RREG Requirement <= 0MW | Outage
F_N_GUTHEGA_L5 | 43 | 0 | Out= NIL, Guthega L5 Requirement <= 0MW | Outage
F_N_GUTHEGA_R60 | 42.3333 | 0 | Out= NIL, Guthega R60 Requirement <= 0MW | Outage
F_N_GUTHEGA_R5 | 42.3333 | 0 | Out= NIL, Guthega R5 Requirement <= 0MW | Outage
F_N_GUTHEGA_L60 | 40.75 | 0 | Out= NIL, Guthega L60 Requirement <= 0MW | Outage
F_Q++ARTW_L5 | 38.0833 | 9.3333 | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
F_Q++MUTW_L6 | 37.9167 | 7.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
F_Q++MUTW_L60 | 36.5 | 8.25 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
F_Q++LDTW_L6 | 32.1667 | 1.0833 | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
F_Q++LDTW_L60 | 31 | 1.0833 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
F_MAIN++NIL_BL_R60 | 30.9167 | 3.1667 | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL
F_Q++MUTW_L5 | 28.0833 | 6.1667 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
F_T++NIL_ML_L5 | 21.5 | 34.6667 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_I+ML_L5_APD | 21 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage
F_I+ML_L60_APD | 20.25 | 273.0833 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | NIL
F_T++NIL_MG_R5 | 20.25 | 0 | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | Outage
F_Q++LDTW_L5 | 20.0833 | 0.58333 | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
F_Q_W/HOE#2_R5 | 18.5 | 0 | Out= NIL, W/HOE#2 R5 Requirement <= 0MW | Outage
F_MAIN++ML_L6_APD | 17.6667 | 1.3333 | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | Outage
F_I+WIP_N-2_ML_L6 | 15.6667 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 6 sec requirement | Outage
F_Q++ARDM_R60 | 12.0833 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 60 sec Requirement | Outage
F_Q++ARDM_R6 | 11.6667 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 6 sec Requirement | Outage
F_T+FASH_N-2_RREG | 10.25 | 21.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_MAIN++ML_L5_APD | 9.9167 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_ESTN++MLMO_L60 | 8.5 | 13.4167 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_MAIN++ML_L60_APD | 5.8333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_T++FASH_N-2_TG_R60 | 5.4167 | 3.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_Q++LDMU_L60 | 5.25 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
F_Q++LDMU_L6 | 5.1667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
F_T+BB_N-2_TG_R6_1 | 5 | 58.1667 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment1 | Outage
F_T+NIL_BB_TG_R60 | 4.5833 | 362.75 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_S_TIPSA1_R60 | 4.0833 | 0 | Out= NIL, Torrens Island A Unit 1 R60 Requirement <= 0MW | Outage
F_S_TIPSA1_R6 | 4.0833 | 0 | Out= NIL, Torrens Island A Unit 1 R6 Requirement <= 0MW | Outage
F_V+NIL_APD01_R60 | 4.0833 | 1.5 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_T++FASH_N-2_TG_R6 | 4 | 7.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_V+NIL_APD01_R5 | 3.9167 | 1.1667 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_APD01_R6 | 3.9167 | 1.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_V+NIL_APD01_L5 | 3.8333 | 1.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_QNV+MO_TG_R60 | 3.75 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 60 sec requirement for Mortlake generation loss on trip of other line, Basslink unable to transfer FCAS | Outage
F_V+NIL_APD01_L6 | 3.25 | 1.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_V+NIL_APD01_L60 | 3.1667 | 1.5 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_T++FARE_N-2_TG_R6 | 3.0833 | 1.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_Q++LDMU_L5 | 2.9167 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
F_T+NIL_BB_TG_R5 | 2.8333 | 0 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_T++COGT_TL_L6 | 2.8333 | 5.4167 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_I+TG_R5_0850 | 2.5 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 850 | Outage
F_I+TG_R60_0850 | 2.5 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 850 | Outage
F_Q_TARONG#2_R60 | 2.3333 | 0 | Out= NIL, Tarong 2 R60 Requirement <= 0MW | Outage
F_T+BB_N-2_TG_R5 | 2.1667 | 427.75 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+ML_L6_APD | 2.1667 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_T+FASH_N-2_TG_R6_1 | 2.0833 | 6.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage
F_T++CSGO_TG_R6 | 2 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_Q_TARONG#1_R60 | 1.9167 | 0 | Out= NIL, Tarong 1 R60 Requirement <= 0MW | Outage
F_S_TIPSA4_R60 | 1.8333 | 0 | Out= NIL, Torrens Island A Unit 4 R60 Requirement <= 0MW | Outage
F_S_TIPSA4_R6 | 1.8333 | 0 | Out= NIL, Torrens Island A Unit 4 R6 Requirement <= 0MW | Outage
F_Q_W/HOE_R5 | 1.75 | 0 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage
F_T++BB_N-2_TG_R6 | 1.6667 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T++BB_N-2_TG_R60 | 1.5833 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T+CSGO_TG_R6_1 | 1.3333 | 7.8333 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage
F_T++FARE_N-2_TG_R60 | 1.25 | 0.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T+FARE_N-2_RREG | 1.25 | 7.5833 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_T++FASH_N-2_TG_R5 | 1.1667 | 5.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_Q++NIL_R5 | 1.0833 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | Outage
F_T++BB_N-2_TG_R5 | 1.0833 | 0.25 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | NIL
F_I+RREG_0400 | 1 | 0.5 | NEM Raise Regulation Requirement greater than 400 MW | Other
F_T+NIL_BB_TG_R6 | 0.91667 | 376.5 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_MAIN++RREG_0400 | 0.83333 | 0 | Mainland Raise Regulation Requirement greater than 400 MW, Basslink able transfer FCAS | Other
F_Q++LDTW_R60 | 0.75 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
F_I+TG_R5_1300 | 0.75 | 2.5833 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1300 | Outage
F_I+TG_R6_1300 | 0.75 | 0 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1300 | Outage
F_I+TG_R60_1300 | 0.75 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1300 | Outage
F_T+FARE_N-2_TG_R6_1 | 0.66667 | 17.0833 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage
F_T+FASH_N-2_TG_R60 | 0.58333 | 52.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_ESTN++HYMO_L60 | 0.58333 | 5.4167 | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage
F_T++FARE_N-2_TG_R5 | 0.5 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T+BB_N-2_TG_R60 | 0.5 | 92.8333 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_Q++LDTW_R6 | 0.41667 | 2.1667 | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
F_T+CSGO_TG_R60 | 0.33333 | 27.5833 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_MAIN+ML_L60_APD | 0.33333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_Q_TARONG#2_R6 | 0.33333 | 2.1667 | Out= NIL, Tarong 2 R6 Requirement <= 0MW | Outage
F_Q_TARONG#1_R6 | 0.33333 | 0 | Out= NIL, Tarong 1 R6 Requirement <= 0MW | Outage
F_T+CSGO_TG_R5 | 0.33333 | 26.5 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_MAIN+ML_L5_APD | 0.33333 | 3.6667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_Q_MEWV_824_R5 | 0.25 | 0 | Out= Mt England to Wivenhoe (824) line, Raise 5 min requirement of zero for Wivenhoe #2 | Outage
F_I+TG_R60_1200 | 0.25 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1200 | Outage
F_I+TG_R6_1200 | 0.25 | 0 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1200 | Outage
F_I+TG_R5_1200 | 0.25 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1200 | Outage
F_I+LREG_0400 | 0.16667 | 0 | NEM Lower Regulation Requirement greater than 400 MW | Outage
F_T++CSGO_TG_R5 | 0.16667 | 5.0833 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Other
F_MAIN++LREG_0400 | 0.16667 | 0 | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage
F_I+TG_R60_1000 | 0.16667 | 6.3333 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1000 | Other
F_I+TG_R5_1000 | 0.16667 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1000 | Outage
F_Q_TARONG#1_RREG | 0.16667 | 0 | Out= NIL, Tarong 1 RREG Requirement <= 0MW | Outage
F_Q_TARONG#2_RREG | 0.16667 | 0 | Out= NIL, Tarong 2 RREG Requirement <= 0MW | Outage
F_T++NIL_BLSPS_L60_1 | 0.083333 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_T+FASH_N-2_TG_R5 | 0.083333 | 3.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_Q++ARDM_R5 | 0.083333 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 5 min Requirement | Other
F_T++NIL_BLSPS_L6_1 | 0.083333 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | Outage
F_MAIN++APD_TL_L6 | 0.083333 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_T++COGT_TL_L60 | 0.083333 | 4.75 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T+FARE_N-2_TG_R5 | 0.083333 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | NIL
F_MAIN+LREG_0400 | 0.083333 | 3.3333 | Mainland Lower Regulation Requirement greater than 350 MW, Basslink unable to transfer FCAS | Outage
F_T++NIL_BLSPS_L5 | 0.083333 | 0 | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL

## Binding Impact
Constraint Equation ID | 2017 Marginal Values | 2016 Marginal Values | 2017 Hours | 2016 Hours | Description | Type | Region
F_S+RREG_0035 | 6751450.4514 | 8814510.7975 | 155.5833 | 531.6667 | South Australia raise regulation FCAS requirement greater than 35 MW This constraint equation is normally invoked for a risk of islanding or an islanded South Australia | Outage | FCAS
F_S+LREG_0035 | 6679748.2302 | 9234805.6739 | 158.5833 | 531 | South Australia lower regulation FCAS requirement greater than 35 MW This constraint equation is normally invoked for a risk of islanding or an islanded South Australia | Outage | FCAS
S_WIND_1200_AUTO & S_NIL_STRENGTH_1 | 4746491.0083 | 0 | 397.3333 | 0 | Upper limit of 1295 MW for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements. Automatically swamps out when required combination is online. | NIL | SA
S_PLN_ISL2 | 4278377.5629 | 988797.2453 | 25.6667 | 7.4167 | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
S_PLN_ISL32 | 4152741.7133 | 239608.7624 | 25.5833 | 6.3333 | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
T>T_NIL_110_1 | 2282347.5986 | 1976229.6442 | 178.25 | 153.9167 | Out = Nil, avoid overloading the Derby to Scottsdale Tee 110 kV line on no line trips This constraint equation was implemented in mid-2013 with the Musselroe Wind Farm commissioning. It binds with high output from Musselroe. | NIL | Tas
T_MRWF_QLIM_xx | 1546815.5053 | 510541.3394 | 118.8333 | 39.75 | Out = Nil, limit Musselroe Wind Farm based on status of the DVARs, capacitor banks or synchronous condensers at Musselroe The binding results from the six constraint equations have been combined. | NIL | Tas
F_I+LREG_0120 | 1523661.4353 | 120561.6244 | 6959.75 | 1434 | NEM Lower Regulation Requirement greater than 120 MW | NIL | FCAS
F_I+NIL_RREG | 1481379.4495 | 168056.185 | 7280.9167 | 1339.5 | NEM Raise Regulation Requirement | NIL | FCAS
S>NIL_HUWT_STBG | 1227468.3407 | 968995.4238 | 96.8333 | 78.9167 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line overload on loss of Hummocks - Waterloo line | NIL | SA
F_I+NIL_MG_R6 | 1017635.5787 | 219670.5272 | 7509.4167 | 3955 | NEM raise 6 second requirement for a NEM generation event | NIL | FCAS
N>>N-NIL__3_OPENED | 801598.9429 | 288656.0362 | 23.8333 | 61.3333 | Out = Nil, avoid overloading Liddell to Muswellbrook (83) 330kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL | NSW
F_T+NIL_WF_TG_R6 | 761013.3893 | 231750.512 | 1211.1667 | 1214.5 | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
N^^V_NIL_1 | 736587.6863 | 42415.9673 | 1808.4167 | 81.9167 | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL | NSW
F_I+NIL_MG_R5 | 661829.0286 | 121786.1051 | 7927.6667 | 4108 | NEM raise 5 minute requirement for a NEM generation event The largest unit is usually Kogan Creek or one of the large NSW units. | NIL | FCAS
S_HALWF_0 | 660008.3712 | 2675.1433 | 52.0833 | 1.25 | Discretionary upper limit for Hallett wind farm generation of 0 MW | Outage | SA
NSA_S_PORxxx | 633602.6751 | 7120984.2478 | 22.75 | 42.8333 | Network Support Agreement for Port Lincoln Units 1 and 2 | Outage | SA
S-SNWWF_0 | 608566.0783 | 31321.7673 | 46.3333 | 27.5 | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
F_MAIN+NIL_DYN_RREG | 590159.5218 | 311962.7149 | 869.5833 | 2473 | Mainland raise regulation requirement, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS | NIL | FCAS
Q>NIL_BI_xxx | 589995.8774 | 0 | 139.9167 | 0 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104 and 7105 (T022 Callide A to T152 Gladstone South) 132 kV lines open with 132 kV intact between T022 Callide A and H015 Lilyvale. | NIL | Qld
V:S_600_HY_TEST_DYN | 582676.9054 | 76535.0348 | 289.25 | 181.8333 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 556067.8533 | 466660.5506 | 147.8333 | 576.5 | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator This voltage collapse limit is split into 7 constraint equations to co-optimise with each of the 6 largest generators in Queensland. Overall N^^Q_NIL_B1 (for trip of Kogan Creek) binds for the most number of intervals. | NIL | NSW
V^SML_NSWRB_2 | 441280.0408 | 518332.8654 | 52 | 153.9167 | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL | Vic
F_T+NIL_MG_R6 | 436152.927 | 300224.8701 | 1330.8333 | 2951.1667 | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL | FCAS
F_I+NIL_MG_R60 | 408139.9473 | 89934.6453 | 7164.4167 | 3886.25 | NEM raise 60 second requirement for a NEM generation event | NIL | FCAS
F_MAIN+NIL_DYN_LREG | 406317.0764 | 218244.1408 | 862.25 | 4039.6667 | Mainland lower regulation requirement, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS | NIL | FCAS
F_T+NIL_MG_RECL_R6 | 392954.5944 | 121663.6321 | 1091.3333 | 465.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
S>NIL_WERB_WEWT | 389842.3203 | 39865.3807 | 105.1667 | 43.8333 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
S_DVRB2_270 | 360127.0206 | 0 | 30.75 | 0 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | SA
Q_RS_260 | 348834.5527 | 0 | 3.5833 | 0 | Ross cut-set discretionary upper limit of 260 MW | Outage | Qld
F_MAIN++LREG_0120 | 333243.8217 | 4669.8601 | 1297.0833 | 50.75 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL | FCAS
S_SA_WIND_1200 | 276288.6797 | 0 | 32.1667 | 0 | Discretionary upper limit for South Australian wind generation of 1200 MW. | Outage | SA
NSA_V_BDL0xxx | 267715.9865 | 515000.6222 | 4 | 21.3333 | Bairnsdale Unit 1 or 2 >= various levels for Network Support Agreement The binding results from xx constraint equations that set the minimum level of Bairnsdale 1 or 2 generation have been combined. | Outage | Vic
F_T+RREG_0050 | 263753.9267 | 333579.6396 | 543.6667 | 4174.75 | Tasmania raise regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
S_WATERLWF_RB | 260514.302 | 0 | 27.5 | 0 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | SA
S_HALWF2_0 | 246487.125 | 0 | 18.3333 | 0 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | SA
N>>Q_LDMU_B | 241466.3429 | 0 | 11.9167 | 0 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage | NSW
N>>N-NIL__B_15M | 237706.2578 | 2431.7258 | 5.25 | 0.16667 | Out= Nil, avoid O/L Upper Tumut to Canberra (01) using 15 mins rating on trip of Lower Tumut to Canberra (07) line, Feedback | NIL | NSW
V_MTMERCER_ZERO | 235901.5035 | 547970.5293 | 17.8333 | 43.9167 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
S>NIL_SGBN_SGSE-T2 | 234062.2873 | 116502.081 | 53.9167 | 16.9167 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
V_OWF_TGTSNRBHTN_30 | 228038.5399 | 0 | 17.8333 | 0 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Vic
T>T_NIL_110_2 | 224020.6153 | 2889.2914 | 17.5833 | 0.25 | Out = NIL, avoid O/L Scottsdale Tee to Norwood 110 kV line (flow to Norwood) on trip of Scottsdale to Norwood 110 kV line or 110/22 kV txfmr at Scottsdale, feedback. Swamped when Musselroe Runback Control Scheme available | NIL | Tas
N_X_MBTE2_A & N_X_MBTE2_B | 206087.1432 | 74246.1154 | 1202.5833 | 568.75 | Out = two Directlink cables | Outage | NSW
N>N-CHKK_TE_1 | 204687.0891 | 6080.486 | 82.5 | 16.5 | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
F_T++RREG_0050 | 201134.5522 | 52112.6307 | 1109.4167 | 293.1667 | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
VS_050 | 195427.8757 | 0 | 59.4167 | 0 | Victoria to South Australia on Heywood upper transfer limit of 50 MW | Outage | Vic
V>>SML_NIL_8 | 185106.6913 | 79.8144 | 2.4167 | 0.25 | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
V::N_NIL_xxx | 181973.4356 | 238530.6921 | 608.9167 | 1054.25 | Out = Nil, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria and all the binding results have been combined. | NIL | Vic
Q>NIL_MRTA_B | 177122.8693 | 70158.9531 | 7.8333 | 19.6667 | Out = Nil, avoid overloading Middle Ridge to Tangkam (732) 110 kV line on no contingencies | NIL | Qld
T_TAMARCCGT_GCS | 168519.0338 | 12876.6617 | 65.9167 | 0.91667 | Limit output of Tamar Valley Power Station based on load available for shedding by Tamar Valley 220 kV generation control scheme (GCS) | NIL | Tas
F_MAIN+LREG_0120 | 167915.1982 | 11004.3277 | 478.0833 | 84.6667 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN+NIL_RREG | 160378.222 | 12028.3487 | 425 | 71.6667 | Mainland Raise Regulation Requirement, Basslink unable transfer FCAS | NIL | FCAS
S_SECB_LG3 | 159985.7851 | 0 | 12.6667 | 0 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
F_MAIN++NIL_MG_R6 | 156764.5211 | 28841.8605 | 1140.5 | 395.4167 | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 151610.5032 | 0 | 516.6667 | 0 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Qld
F_T+LREG_0050 | 149937.0085 | 148620.1161 | 483.25 | 4176 | Tasmania lower regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN+NIL_MG_R6 | 149440.4665 | 285458.9509 | 483.4167 | 4169.5 | Out = Nil, raise 6 sec requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL | FCAS
S_TBL_0 | 147294.4294 | 14696.9418 | 11 | 8.25 | Discretionary upper limit for The Bluff generation of 0 MW | Outage | SA
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 143896.5996 | 144341.5003 | 311.5 | 1014.5 | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV These constraint equations maintain flow on the South Morang F2 transformer below its continuous rating. | NIL | Vic
S_NBH_0 | 140621.8708 | 0 | 10.5 | 0 | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | SA
VSML_ROC_80 | 137511.248 | 119758.6117 | 20.0833 | 26.8333 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
S-STTX_SNWF | 132014.7542 | 1362930.1326 | 10.1667 | 210 | Out = Snowtown 132/33 kV transformer or Snowtown CB4593 or CB6265, limit Snowtown wind farm generation to 0 MW | Outage | SA
V_MORTLAKE12_ZERO | 130181.36 | 0 | 1.0833 | 0 | Mortlake unit 1 & 2 upper limit of 0 MW | Outage | Vic
F_MAIN++NIL_MG_R5 | 126189.2683 | 10679.6873 | 1141.3333 | 249.5833 | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
F_MAIN++NIL_MG_R60 | 123178.0361 | 34672.7649 | 1563 | 635.1667 | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
S>BLMK_BWPA_HUWT | 118867.1564 | 0 | 8.3333 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T>T_NWSD_110_1 | 112575.5745 | 0 | 9.1667 | 0 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752, avoid O/L Scottsdale Tee to Norwood 110kV line on Nil trip, Feedback | Outage | Tas
S>V_NIL_NIL_RBNW | 112551.1516 | 127119.9367 | 283.25 | 586.8333 | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips This constraint equation normally sets the upper limit on Murraylink. | NIL | SA
V:S_600_HY_TEST | 111858.1309 | 14234.5805 | 76.1667 | 47.9167 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
F_T++NIL_MG_RECL_R6 | 109899.9377 | 4149.9051 | 263.3333 | 27.0833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
N^Q_NIL_A | 108746.537 | 241713.872 | 29.5833 | 82.0833 | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL | NSW
T>T_TUNN3_110_1 | 95183.8674 | 73107.5532 | 45.3333 | 7.0833 | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Meadowbank Tee 2 to New Norfolk 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
N_MBTE1_B | 90623.913 | 3766.105 | 206 | 10.0833 | Out = one Directlink cable, Queensland to NSW limit | Outage | NSW
V_T_NIL_FCSPS | 87762.9926 | 27030.7353 | 194.5833 | 48 | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) This constraint equation binds when there is high import to Tasmania or a low amount of load is enabled for tripping. | NIL | Vic
V_OWF_NRB_0 | 87092.7289 | 0 | 6.5833 | 0 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Vic
V>>V_NIL_5 | 86009.0246 | 345.0988 | 35 | 0.58333 | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL | Vic
Q>STBS_STBS_BADU | 85200 | 0 | 0.5 | 0 | Out= Stanwell to Broadsound (856 or 8831), avoid O/L Baralaba to Duaringa (7113/1) on trip of remaining Stanwell to Broadsound (856 or 8831) | Outage | Qld
F_MAIN+NIL_MG_R60 | 84709.9548 | 195479.207 | 483.3333 | 4169.5 | Out = Nil, raise 60 sec requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL | FCAS
F_MAIN+NIL_MG_R5 | 82206.9969 | 169241.2103 | 483.4167 | 4169.5 | Out = Nil, raise 5 min requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL | FCAS
S>NIL_NIL_NWMH2 | 81847.4014 | 142012.7884 | 36.9167 | 36.9167 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
N_NYNGANSF_010 | 79422.7618 | 304496.3767 | 5.75 | 23 | Nyngan Solar Farm upper limit of 10 MW | Outage | NSW
N_BROKENH1_ZERO | 79177.3463 | 275825.0287 | 6 | 22.0833 | Broken Hill Solar Farm upper limit of 0 MW | Outage | NSW
F_T+NIL_WF_TG_R60 | 68447.908 | 13835.3316 | 1140 | 1200.3333 | Tasmania raise 60 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
S_HPRL1_E | 64847.8263 | 0 | 1.3333 | 0 | Out= Nil, Hornsdale Battery load energy target <= 40 MW | NIL | SA
S:V_500_HY_TEST_DYN | 63489.0564 | 73401.8118 | 189.5833 | 0.66667 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
NSA_Q_BARCALDN | 61385.7792 | 597006.3416 | 4.9167 | 46.4167 | Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine for the outage of Clermont to Lilyvale (7153) 132 kV line This constraint equation is used for planned outages of the Clermont to Lilyvale (7153) or Barcaldine to Clermont (7154) 132 kV lines | Outage | Qld
T>T_NIL_BL_110_18_1 | 60742.1132 | 729.6288 | 33.1667 | 0.58333 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
V_T_NIL_BL1 | 60567.5107 | 7101.5859 | 152.0833 | 12.9167 | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL | Vic
V::N_SMF2_xxx | 53910.4092 | 4028.1069 | 180.75 | 10.4167 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_T+NIL_MG_R60 | 53531.605 | 34429.2304 | 1223.5833 | 2926.0833 | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL | FCAS
F_T++NIL_MG_R6 | 52917.2372 | 55950.0522 | 56.5 | 160.5 | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
Q>NIL_MRTA_A | 51712.9757 | 69362.8085 | 3.25 | 6.8333 | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Qld
S>BRTW_BWPA_HUWT | 50055.746 | 54697.0613 | 4.0833 | 15.6667 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_T+NIL_MG_RECL_R60 | 49954.7652 | 8457.19 | 1115.5833 | 395.9167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
N_BOCORWF1_ZERO | 48678.3036 | 0 | 3.8333 | 0 | Boco Rock WF upper limit of 0 MW | Outage | NSW
V_MACARTHUR_ZERO | 48275.9721 | 70597.0954 | 20.5833 | 39.1667 | Macarthur upper limit of 0 MW | Outage | Vic
F_MAIN+TASCAP_RREG | 43900.8675 | 0 | 469.5 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS
T>T_LIPM_110_2A | 43399.3996 | 1659.1974 | 89.8333 | 0.91667 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
F_S++HYSE_L6_1 | 42768.6004 | 287598.3024 | 62.3333 | 53 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA lower 6 sec Requirement for risk of islanding, segment1 | Outage | FCAS
F_T++NIL_WF_TG_R6 | 41924.75 | 27910.0853 | 124 | 61 | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS Out= Nil, Tasmania raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
NRM_QLD1_NSW1 | 41200.1779 | 21735.9328 | 11.9167 | 6.9167 | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
S>BGTX_BGBR_HUWT | 40751.024 | 0 | 5.5 | 0 | Out= Bungama 275/132kV TX, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap windfarm), Feedback | Outage | SA
N^N_KKLS_1 | 39788.3875 | 12.5561 | 232.0833 | 2.3333 | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. | Outage | NSW
S_HDWF1_0 | 38668.9569 | 0 | 1.8333 | 0 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | SA
N_TARALGAWF_ZERO | 36518.3546 | 0 | 2.75 | 0 | Taralga WF upper limit of 0 MW | Outage | NSW
N_X_MBTE_3A & N_X_MBTE_3B | 36347.5025 | 36410.7064 | 223.25 | 863.5833 | Out = all three Directlink cables | Outage | NSW
VTBL_ROC | 36023.1273 | 16543.7249 | 12.5833 | 4.3333 | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL | Vic
F_MAIN+TASCAP_LREG | 33240.2368 | 0 | 677.75 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS
N_GUNNING1_ZERO | 31639.3144 | 5421.8481 | 0.41667 | 5.0833 | Discretionary upper limit for Gunning generation of 0 MW | Outage | NSW
SVML_ROC_80 | 31448.1887 | 12554.2346 | 21.3333 | 33.75 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
S:VS_650_HY_TEST_DYN | 30646.6613 | 0 | 22.5 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
VSML_220 | 29626.0483 | 890028.9034 | 22.3333 | 468.0833 | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL | Vic
Q_BRBRA_8839 | 29506.0909 | 0 | 0.25 | 0 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 | Outage | Qld
N>>N-NIL__H_15M | 28464.8889 | 0 | 0.33333 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | NSW
V_S_ROCOF | 28362.1649 | 19987.6435 | 1.1667 | 31.8333 | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage | Vic
T_T_FASH_3_N-2 | 28000 | 0 | 0.16667 | 0 | Out = Nil, loss of both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, Hampshire link open, constrain Reece Unit 1 to 0 MW as per Transend advice | Outage | Tas
T:T_LIPM_1 | 27896.8393 | 311.9552 | 63.1667 | 0.33333 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Tas
N>LSDU_LSDU | 27705.4928 | 33988.0942 | 32.5833 | 109.75 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | NSW
V_S_NIL_ROCOF | 27221.0258 | 303197.4223 | 134.1667 | 393 | Out = Nil, limit Victoria to SA on Heywood flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL | Vic
N_MOREESF1_ZERO | 26255.2245 | 34774.9581 | 2 | 2.4167 | Moree Solar Farm upper limit of 0 MW | Outage | NSW
N^^V_DDMSX5_1 | 25994.0287 | 0 | 29.4167 | 0 | Out = Dederang - Murray (67 or 68) and Darlington Pt - Buronga (X5) lines, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
F_T+NIL_MG_RECL_R5 | 25853.159 | 6349.9438 | 718.0833 | 469.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_T+NIL_WF_TG_R5 | 25315.2583 | 12086.5323 | 865.75 | 561.5833 | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
SVML_ZERO | 25260.0273 | 168997.6636 | 83.25 | 173.75 | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage | SA
V>V_ROYP6_1AR | 24281.5542 | 0 | 4.8333 | 0 | Out = Rowville to Yallourn No. 6 220 kV line, radial mode, prevent O/L of the Rowville to Yallourn No. 7 or No. 8 220 kV line for trip of the parallel No. 8 or No. 7 220 kV line, Yallourn W1 on 220 kV, feedback | Outage | Vic
V>>SML_NIL_1 | 24081.251 | 38.3158 | 2.6667 | 0.16667 | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
S_BRBG_CMWF_0 | 23279.5391 | 0 | 1.6667 | 0 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | SA
N>N-NIL_LSDU | 23087.3702 | 915.3355 | 7.8333 | 14.8333 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line This constraint equation binds for high exports from NSW to Qld. | NIL | NSW
V>>DDSH_DDGN_N-2 | 23047.5284 | 110400 | 1.3333 | 0.66667 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage | Vic
F_Q++ARDM_L60 | 22269.8846 | 0.43 | 108.1667 | 0.083333 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 60 second requirement | Outage | FCAS
N>>N-NIL_01N | 21901.7897 | 135243.2581 | 0.16667 | 3.5833 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | NSW
V::N_HWSM_xxx | 21877.1245 | 11195.9376 | 48.9167 | 33.5833 | Out = Hazelwood to South Morang 500 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
F_Q++ARDM_L5 | 21202.5228 | 0.26 | 92.1667 | 0.083333 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
F_Q++ARDM_L6 | 20974.4629 | 1.1078 | 107.25 | 0.083333 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
T_ROCOF_1 | 20678.1419 | 0 | 49.25 | 0 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL | Tas
S_HPRG1_E | 20077.2032 | 0 | 2.5 | 0 | Out= Nil, Hornsdale Battery generation energy target <= 30 MW | NIL | SA
F_T+NIL_MG_R5 | 19725.5517 | 20267.2505 | 757.4167 | 900.25 | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL | FCAS
I_CTRL_ISSUE_TE | 19419.3377 | 2447.7293 | 310.8333 | 44.25 | DC Link Control Issue Constraint for Terranora | Outage | Other
F_V_APD01_R6 | 18386.7038 | 1736.4899 | 64.4167 | 27.1667 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage | FCAS
V_ML_TRMO | 18235.4314 | 0 | 20.6667 | 0 | Out = Moorabool to Mortlake or Moorabool to Tarrone 500 kV line, limit nett loading to < 50 MW on the remaining 500 kV line into Moorabool. | Outage | Vic
V:SS_820_HY_TEST_DYN | 17614.4335 | 3099.8101 | 6.5 | 15.9167 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
NRM_SA1_VIC1 | 17049.5687 | 68769.794 | 1.25 | 6.5 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue
F_Q++LDTW_L5 | 16734.9837 | 266.1552 | 20.0833 | 0.58333 | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
T::T_HA_GT_PM_5 | 16546.2604 | 0 | 4.6667 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT in service. | Outage | Tas
S>BRDV_BWPA_RHBR | 15877.6417 | 537.7662 | 1.5833 | 0.25 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_Q++LDTW_R6 | 15119.2689 | 1586.838 | 0.41667 | 2.1667 | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage | FCAS
F_Q++MUTW_L5 | 14914.1809 | 1569.4284 | 28.0833 | 6.1667 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage | FCAS
F_N_GUTHEGA_RREG | 14763.9494 | 0 | 43.75 | 0 | Out= NIL, Guthega RREG Requirement <= 0MW | Outage | FCAS
S>NIL_NIL_SETX12 | 14260.0691 | 18355.3363 | 3.3333 | 1.5 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
N^^V_LTUT_1 | 14000 | 0 | 0.083333 | 0 | Out = lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
T_T_FASH_2_N-2 | 13898.5657 | 0 | 4.6667 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh >= 90% of West Coast load | Outage | Tas
S>NIL_BWMP_HUWT | 13849.508 | 52164.5347 | 1.1667 | 13.4167 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
NQTE_ROC | 13766.606 | 5676.8182 | 16.6667 | 85 | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL | NSW
Q:N_NIL_BI_POT | 13598.1548 | 0 | 49 | 0 | Out = Nil, avoid transient instability for a trip of a Boyne Island potline (400 MW) For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_OSC or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
F_MAIN++NIL_RREG | 13297.2568 | 1168.7738 | 88.1667 | 11.5 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL | FCAS
N>>N-NIL__S | 13123.9777 | 50792.9551 | 0.58333 | 1.5833 | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL | NSW
S>>NIL_TBCG_TBTU_1 | 12909.6258 | 7362.177 | 2.3333 | 35.25 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | SA
S>>BLMK_CNRB_WEMWP4 | 12727.7201 | 0 | 12.3333 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV on trip of Canowi-Robertstown 275kV line(this trips Hallet wind farm and Hallet GT, and offloads Davenport-Canowie 275kV line), Feedback | Outage | SA
V>>V_SMTXF2_6 | 12603.5035 | 677.3439 | 29.5 | 2.0833 | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage | Vic
N^^V_SMTXH1_1 | 12426.9546 | 716.2561 | 14.1667 | 3.25 | Out = South Morang H1 or H2 500/330 kV txfmr, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
T>T_NIL_220_14_HM | 12042.4347 | 0 | 23.4167 | 0 | Out = Nil, West Coast 220/110 kV parallel closed, avoid overloading a Farrell to Sheffield line for loss of the parallel line, feedback | NIL | Tas
V>SML_NSWRB_10 | 11973.9187 | 0 | 3.1667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
V::S_SETB_TBSE_2 | 11968.8425 | 0 | 45.3333 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | SA
S>NWBCB6225_TX1 | 11853.0359 | 0 | 40.9167 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 66/132kV TX1 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage | SA
T^V_NIL_11 | 11817.9508 | 1768.8147 | 21.5 | 2 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
S:V_500_HY_TEST | 11198.3929 | 0 | 45.25 | 0 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
S>NIL_LKDV_CNRB | 11040.3751 | 0 | 0.91667 | 0 | Out= NIL, avoid O/L Canowi-Robertstown 275kV on trip of Mt Lock-Davenport 275kV line, Feedback | NIL | SA
V>V_HWA34_OP2_1 | 11037.2555 | 0 | 1.6667 | 0 | Out = Hazelwood A3 or A4 500/220 kV txfmr, avoid O/L Yallourn to Rowville No. 5 220 kV line on trip of Hazelwood A4 or A3 500/220 kV txfmr, 3/5 parallel mode, Jeeralang B connected to HWPS B3/4 side, feedback | Outage | Vic
F_N_GUTHEGA_LREG | 10866.903 | 0 | 44.25 | 0 | Out= NIL, Guthega LREG Requirement <= 0MW | Outage | FCAS
N^^V_DDWG | 10756.9677 | 0 | 14.75 | 0 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
QNTE_150 | 10469.2959 | 0 | 19.5833 | 0 | Qld to NSW on Terranora Interconnector upper transfer limit of 150 MW | Outage | Qld
T_FASH_MAXGEN_1 | 10413.0235 | 14605.1336 | 14.5833 | 9.25 | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Tas
V::N_BYPASS_HW_SY_xxx | 10157.7167 | 2120.4482 | 14.3333 | 5.8333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 10067.3352 | 112850.2441 | 39.25 | 97.25 | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies These constraint equations are dependent on the Terranora load as well as all 3 cables of Directlink being in service. In May 2011 the constraint equation Q>NIL_757+758_B was replaced with two constraint equations Q>NIL_MUTE_757 and Q>NIL_MUTE_758. The binding results for each have been combined. | NIL | Qld
S-SNWF_WPWF_120 | 9788.5932 | 0 | 0.75 | 0 | Discretionary upper limit for Snowtown WF + Wattle Pt WF generation <= 120 MW | Outage | SA
F_V_APD01_R5 | 9402.365 | 528.9097 | 64.4167 | 27.5 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage | FCAS
S>V_NWRB_RBMWP3 | 9381.9689 | 0 | 17.4167 | 0 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage | SA
T_T_FASH_1_N-2 | 9343.8766 | 0 | 7.5 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
F_T++LREG_0050 | 9322.0483 | 2344.2592 | 93.3333 | 47.9167 | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
S>RB_275KV_S_BUS_9 | 9068.1209 | 0 | 14 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage | SA
S-HDWF2_0 | 9011.0063 | 0 | 2.1667 | 0 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW | Outage | SA
S>NWCB6024+25_TX3 | 8877.5056 | 1808.0953 | 18.25 | 4.3333 | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | SA
V_OAKLANDSHILL_42 | 8746.8266 | 0 | 0.66667 | 0 | Oaklands Hill Windfarm upper limit of 42 MW | Outage | Vic
F_Q++ARDM_R60 | 8595.588 | 0 | 12.0833 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 60 sec Requirement | Outage | FCAS
T::T_NIL_4 | 8269.3914 | 3815.3021 | 15.25 | 9.25 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
V>>N-NIL_HA | 8228.0732 | 97516.8331 | 12.9167 | 367.9167 | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | NIL | Vic
F_Q++ARTW_L60 | 8172.1792 | 4057.9883 | 62.5 | 11.75 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS
T>T_TU_LE_WA12_2 | 8122.5693 | 0 | 3.1667 | 0 | Out = either Tungatinah to Waddamana 110kV line (direct or via Lake Echo tee), avoid O/L the remaining Tungatinah to Waddamana 110 kV line (flow to North) on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, feedback | Outage | Tas
S>NIL_NIL_SGBN | 8046.2079 | 0 | 1.0833 | 0 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | SA
V>>V_KTS_TX_A3_2A_R | 7949.2836 | 464.0157 | 24.25 | 7.0833 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
F_V_APD01_R60 | 7929.9714 | 1059.2364 | 64.4167 | 27.5 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage | FCAS
V>S_460_DYN | 7909.509 | 3121.8444 | 12.5833 | 18 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Vic
F_T++NIL_MG_RECL_R60 | 7751.1746 | 265.9111 | 269.9167 | 22.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
N>N-X_96H+9W2_1 | 7460.8123 | 0 | 5 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Kempsey-Raleigh (9W2) and 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD | Outage | NSW
N>>N-NIL_64 | 7425.9788 | 3265.1278 | 0.33333 | 1 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | NSW
S_V_NIL_ROCOF | 7275.1777 | 3096.371 | 9 | 5.6667 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL | SA
F_Q++ARDM_R6 | 7105.1652 | 0 | 11.6667 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 6 sec Requirement | Outage | FCAS
V::S_PP+TIPSB_MG_2 | 7042.3824 | 0 | 3.0833 | 0 | Out =Nil(Note: with both Black Range series capacitors O/S); Vic-SA Tran. Stab limit for loss of SA largest generator with loss of half of Pelican Point PS (GT1 + ST) and largest TIPS B unit declared as credible (South East Capacitor Available). | Outage | SA
F_I+NIL_APD_TL_L5 | 6551.1842 | 8419.47 | 3624.0833 | 3203.25 | NEM lower 5 min Service Requirement for the loss of APD potlines | NIL | FCAS
F_Q++LDTW_L60 | 6507.9833 | 73.7207 | 31 | 1.0833 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage | FCAS
T>>T_NIL_BL_EXP_7C | 6497.9679 | 60843.685 | 25.9167 | 82.5833 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
S^NIL_PL_MAX | 6367.4105 | 62683.0678 | 0.5 | 3.75 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
TVBL_ROC | 6348.9875 | 1352.1013 | 12.6667 | 3.4167 | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL | Tas
V>>V_NIL_2_TIE | 6173.1088 | 0 | 35.8333 | 0 | Out = Nil, avoid pre-contingent O/L of the South Morang F2 500/330 kV transformer, Yallourn unit 1 in 220kV mode, all 220kV buses tied at Hazelwood, feedback | NIL | Vic
V::N_LTWG_xxx | 6133.8058 | 0 | 5.1667 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T::T_HA_GT_PM_4 | 6033.9554 | 6445.3895 | 2.3333 | 0.16667 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Tas
NRM_VIC1_SA1 | 6030.8075 | 0 | 4.75 | 0 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
V>>V-JNWG_RADIAL_1A | 5911.72 | 24365.4994 | 5.4167 | 6.8333 | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage | Vic
N^^V_MSUT_1 | 5837.8511 | 0 | 20.0833 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
SV_250 | 5819.0757 | 0 | 29 | 0 | SA to Victoria on Heywood upper transfer limit of 250 MW | Outage | SA
F_I+ML_L5_0400 | 5804.0144 | 1049.2702 | 3036.9167 | 667.5833 | NEM lower 5 minute requirement for a NEM load event The largest single load in the NEM is 400 MW at Boyne Island in Queensland. | NIL | FCAS
F_Q++MUTW_L6 | 5758.9918 | 1627.1375 | 37.9167 | 7.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage | FCAS
N_BLOWERNG_ZERO | 5483.1462 | 0 | 0.41667 | 0 | Blowering generation upper limit of 0 MW | Outage | NSW
T>T_NIL_BL_IMP_7CC | 5350.5583 | 58707.1625 | 14.8333 | 86.5 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
S_HDWF3_0 | 5298.2794 | 0 | 1.25 | 0 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW | Outage | SA
N_NIL_TE_B | 5284.3925 | 888.5332 | 23.4167 | 1.5833 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
T>T_FASH_3_N-2 | 5262.7737 | 0 | 5.6667 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV line (flow to Burnie) for loss of both Farrell to Sheffield 220 kV lines | Outage | Tas
F_MAIN++APD_TL_L5 | 5167.5672 | 5883.9343 | 1248.1667 | 871.8333 | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL | FCAS
F_T++NIL_MG_RECL_R5 | 5063.5627 | 267.0942 | 86.6667 | 28.5 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
VS_250_DYN | 5055.532 | 123270.1321 | 10.3333 | 244.75 | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Vic
F_T++NIL_WF_TG_R60 | 5050.4615 | 1299.3389 | 144.5 | 60.3333 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
Q:N_TW330_CB5102_OSC | 4963.5235 | 0 | 8.4167 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage | Qld
Q>N-MUTE_758 | 4852.2021 | 0.26545 | 68.8333 | 0.083333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
V::N_X_HWSM_ROSM_xxx | 4740.7622 | 0 | 0.5 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_N_GUTHEGA_R5 | 4734.9422 | 0 | 42.25 | 0 | Out= NIL, Guthega R5 Requirement <= 0MW | Outage | FCAS
V>>V_KTS_TX_A2_2A_R | 4701.8228 | 6198.0101 | 9.0833 | 54.75 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
F_Q++ARTW_L5 | 4611.9201 | 1544.0452 | 42.5833 | 9.3333 | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
S_LB2WF_CONF | 4541.3898 | 63855.156 | 1.25 | 2.4167 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
F_Q++ARTW_L6 | 4527.9227 | 2268.4197 | 63.8333 | 11.75 | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
Q:N_AR_CP2_AR_2L-G | 4376.2156 | 1690.9416 | 26 | 6.5 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
S>>BLMK_BWPA_BRTW | 4339.5671 | 0 | 1 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T>T_SH_TX | 4185.6781 | 671.3143 | 1.9167 | 0.25 | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Tas
VSML_-100 | 3843.1456 | 0 | 1.6667 | 0 | Vic to SA on ML upper transfer limit of -100 MW | Outage | Vic
F_Q++LDTW_L6 | 3833.8968 | 154.4172 | 32.1667 | 1.0833 | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
T::T_NIL_3 | 3818.5061 | 0 | 8.5 | 0 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. Swamped if Tamar CCGT OOS. | NIL | Tas
V::N_SMF2_SD2 | 3703.0439 | 0 | 7.75 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage | Vic
Q:N_NIL_OSC | 3696.7798 | 0 | 19.4167 | 0 | Out = Nil, Queensland to NSW oscillatory stability limit This constraint equation sets the upper limit from Queensland to NSW to 1078 MW. For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
CA_MQS_47FE2B0C_01 | 3644.9312 | 0 | 3.25 | 0 | Constraint Automation, O/L FARRELL TRANSF T2 for CTG LTAL on trip of FARRELL_SHEFFIELD #2 220KV LINE. Generated by STNET[MANFL] Host MANEEMP1(MQ) | Outage | Constraint Automation
N::V_DDMS | 3611.6904 | 0 | 1.4167 | 0 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage | NSW
F_MAIN++ML_L5_0400 | 3534.2212 | 204.7598 | 1519.0833 | 86.0833 | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
V::N_DDSM_xxx | 3506.5355 | 3240.9756 | 4.9167 | 13.8333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_Q++MUTW_L60 | 3411.3854 | 1660.2807 | 36.5 | 8.25 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage | FCAS
NQ_000 | 3407.9853 | 0 | 0.91667 | 0 | NSW to Qld on QNI upper transfer limit of 0 MW | Outage | NSW
N^^V_DDSM1 | 3338.0314 | 1193.8996 | 12.5 | 4.25 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
F_Q_W/HOE#2_R5 | 3166.3114 | 0 | 18.5 | 0 | Out= NIL, W/HOE#2 R5 Requirement <= 0MW | Outage | FCAS
F_N_GUTHEGA_R60 | 3109.3463 | 0 | 42.25 | 0 | Out= NIL, Guthega R60 Requirement <= 0MW | Outage | FCAS
S>>NIL_TBTU_TBCG_1 | 3082.9883 | 0 | 4.6667 | 0 | Out=NIL, avoid O/L Tailem Bend-Cherry Gardens 275kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
N>>N-NIL__2_OPENED | 3019.8248 | 535.7474 | 3.4167 | 0.75 | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | NSW
S_SECB_LG-1 | 2999.9983 | 0 | 0.25 | 0 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
F_Q++LDMU_L60 | 2964.2402 | 0 | 5.25 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage | FCAS
VT_ZERO | 2881.8871 | 710463.284 | 2.4167 | 628.3333 | Victoria to Tasmania on Basslink upper transfer limit of 0 MW 0 | Outage | Vic
T>T_PMSH_IMP_4C | 2849.9901 | 0 | 4 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>V_HWYP1_3_TIE | 2801.9554 | 0 | 3.5833 | 0 | Out= Hazelwood to Yallourn No.1 220kV line, avoid O/L Yallourn to Hazelwood No.2 220kV line on trip of Yallourn to Rowville No.7 or No.8 220kV line, all 220kV buses tied at Hazelwood, Feedback | Outage | Vic
S:VS_650_HY_TEST | 2787.092 | 0 | 4 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
T>T_GTSH_IMP_4K | 2715.8572 | 78219.1538 | 3.6667 | 103.4167 | Out = Sheffield to Georgetown 220 kV line, avoid overloading Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action | Outage | Tas
NSA_Q_GSTONE34_xxx | 2674.7649 | 645921.0662 | 14.6667 | 13.5833 | Gladstone 3 + 4 >= various levels for Network Support Agreement The binding results from three constraint equations that set the minimum level of Gladstone 3 and 4 generation have been combined. | Outage | Qld
TV_525 | 2660.0214 | 0 | 18.25 | 0 | Tas to Vic on Basslink upper limit of 525 MW | Outage | Tas
V::N_KTSY_xxx | 2505.1017 | 735.4589 | 11 | 6.1667 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T_V_NIL_FCSPS | 2479.7877 | 407.5704 | 5.25 | 0.5 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
F_T+BB_N-2_TG_R6_1 | 2445.5653 | 3034.5275 | 5 | 58.1667 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
T_V_NIL_BL1 | 2385.0688 | 510.7281 | 5 | 1.8333 | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL | Tas
S>NIL_NIL_SGMYSE-T2 | 2372.9336 | 0 | 2.25 | 0 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on Nil trip (for Line component SECS assumed O/S or I/S), Feedback | NIL | SA
V:S_PA_SVC_600 | 2371.3826 | 19606.013 | 2.5833 | 38 | Out= one Para SVC (Note: both Black Range series caps I/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 600 MW | Outage | Vic
QNTE_ROC | 2264.2143 | 3605.9322 | 8.1667 | 82.1667 | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
V_OAKLANDSHILL_ZERO | 2218.7195 | 0 | 0.16667 | 0 | Oaklands Hill Windfarm upper limit of 0 MW | Outage | Vic
T>T_NIL_BL_5C | 2198.9509 | 0 | 1.8333 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
T^V_NIL_BL_6 | 2185.3392 | 2459.073 | 10.5 | 7.75 | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
F_T++NIL_MG_R60 | 2141.0275 | 1009.9209 | 59.3333 | 126 | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
V>V_HWA34_OP2_2 | 2127.8764 | 0 | 0.16667 | 0 | Out = Hazelwood A3 or A4 500/220 kV txfmr, avoid O/L Yallourn to Rowville No. 7 or No. 8 220 kV line on trip of Hazelwood A4 or A3 500/220 kV txfmr, 3/5 parallel mode, Jeeralang B connected to HWPS B3/4 side, feedback | Outage | Vic
V>>N-LTUT_B | 2122.4495 | 0 | 1.5833 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
N>>N-NIL__3_CLOSED | 2011.5246 | 3978.8691 | 2.6667 | 14.0833 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
VSML_ZERO | 2004.5359 | 640206.6978 | 20.6667 | 301.5833 | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
F_T+CSGO_TG_R6_1 | 1982.9024 | 6023.8573 | 1.3333 | 7.8333 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
S>>X_CNRB+CB_02 | 1941.7153 | 0 | 3.1667 | 0 | Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line(this offloads Robertstown #1 275/132kV TX and Trips Hallet Hill WF) | Outage | SA
N>N-NIL_MBDU | 1935.9208 | 0.0584 | 3.4167 | 0.083333 | Out = Nil, avoid overloading Mullumbimby to Dunoon (9U6 or 9U7) 132 kV line on trip of the other Mullumbimby to Dunoon (9U7 or 9U6) 132 kV line | NIL | NSW
S>>X_MKRB+6573+74_1 | 1894.4077 | 0 | 10.25 | 0 | Out= Mokota-Robertstown 275kV line AND Robertstown CB6573 and CB6574, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Robt 275/132kV TX1, and Dav-Can 275kV line and trips Hallet GT & WF), Feedback | Outage | SA
S>RB_275KV_N_BUS_1 | 1891.1007 | 0 | 7.75 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | SA
F_T++NIL_WF_TG_R5 | 1883.3246 | 1065.4741 | 54.75 | 77.5 | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS In Nov 2013 educe by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
V::N_X_HWSM_SMF2_xxx | 1845.5264 | 0 | 7.3333 | 0 | Out= Hazelwood-South Morang 500kV line & South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T>T_FASH_1_N-2 | 1802.9789 | 19766.7145 | 2 | 9.8333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
S>V_CB6033+6225_TX2 | 1745.3609 | 271.1817 | 10.4167 | 4.6667 | Out= North West Bend_CB6033 and CB6225; avoid O/L of North West Bend transformer 132/66kV #2 on trip of either Robertstown-NWB #2 132kV line or NWB-Monash #2 132kV line . | Outage | SA
F_MAIN++NIL_BL_R60 | 1718.119 | 49.4866 | 29.9167 | 3.1667 | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL | FCAS
V>>N-LTUT_2_30 | 1699.609 | 0 | 0.75 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L using 30 mins rating on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
F_MAIN++RREG_0400 | 1698.9648 | 0 | 0.83333 | 0 | Mainland Raise Regulation Requirement greater than 400 MW, Basslink able transfer FCAS | Other | FCAS
V>V_ROYP6_1BR | 1697.0182 | 0 | 1.1667 | 0 | Out = Rowville to Yallourn No. 6 220 kV line, radial mode, prevent O/L of the Rowville to Yallourn No. 7 or No. 8 220 kV line for trip of the Yallourn to Hazelwood No. 1 220 kV line (offloads HWPS-ROTS 1 & 2 220kV lines), Yallourn W1 on 500kV, feedback | Outage | Vic
V::S_KHKN_SETB_2-DS | 1660.2183 | 0 | 0.083333 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of South East - Tailem Bend 275kV line.(NOTE:DS RHS ONLY) | Outage | SA
Q>N-MUTE_757 | 1634.7018 | 39.0162 | 28.5833 | 2.5 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
S>>WTTP_WERB_STBG | 1629.2496 | 0 | 0.66667 | 0 | Out= Waterloo-Templers 132kV line, avoid O/L Snowtown-Bungama T 132kV line on trip of Waterloo East-MWP4-Robertstown 132kV line, Feedback | Outage | SA
NRM_VIC1_NSW1 | 1599.0155 | 27239.8894 | 0.58333 | 2 | Negative Residue Management constraint equation for VIC to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
S>>BLMK_NIL_WEMWP4 | 1572.348 | 0 | 0.58333 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on Nil trip, Feedback | NIL | SA
T>T_NIL_BL_IMP_5F | 1567.9177 | 0 | 2.0833 | 0 | Out = Nil, avoid overloading Hadspen to Georgetown No.1 220 kV line (flow to North) for trip of the Hadspen to Georgetown No.2 220 kV line with no SPS action This constraint only binds when the NCSPS control scheme is unavailable. | NIL | Tas
Q:N_ARSVC_AR_2L-G | 1559.6281 | 407.0405 | 6.1667 | 0.58333 | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
F_MAIN+APD_TL_L5 | 1550.557 | 34400.4146 | 219.4167 | 4086.8333 | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink unable to transfer FCAS | NIL | FCAS
F_T++FASH_N-2_TG_R6 | 1527.6622 | 14340.978 | 3.8333 | 7.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
V>>V_ROTS_TX_2A_R | 1518.4795 | 17193.3819 | 2.25 | 99.25 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
V_ARARAT_5 | 1466.3451 | 19936.5737 | 0.75 | 10.3333 | Ararat Wind Farm upper limit of 5 MW, limit to manage islanding risk | Outage | Vic
T>T_TUNN3_110_2 | 1442.5047 | 0 | 1.3333 | 0 | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Tas
F_MAIN++NIL_BL_L60 | 1430.0977 | 189.0326 | 1749.1667 | 228.4167 | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL | FCAS
V>S_460 | 1413.8665 | 545.0276 | 3.0833 | 3.5 | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | Outage | Vic
S>>NIL_SETB_SETB_1 | 1407.6268 | 2920.0227 | 3.8333 | 11 | Out= Nil, avoid O/L one South East-Tailem Bend 275kV on trip of other South East-Tailem Bend 275kV line, feedback | NIL | SA
F_T+FASH_N-2_RREG | 1398.238 | 6658.8878 | 10.25 | 21.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | FCAS
N^^Q_NIL_A | 1391.5017 | 0 | 8.5 | 0 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | NSW
VN_0850 | 1357.8951 | 47.1164 | 3.9167 | 0.25 | Discretionary Vic to NSW transfer upper limit of 850 MW | Outage | Vic
F_I+NIL_APD_TL_L60 | 1251.0838 | 1970.1492 | 3286.4167 | 3140.8333 | NEM lower 60 sec Service Requirement for the loss of APD potlines | NIL | FCAS
S>NIL_NIL_MYSG-T | 1251.0804 | 0 | 0.91667 | 0 | Out = Nil, avoid overloading Mayura to Snuggery 132 kV line on no line trips | NIL | SA
Q:N_BI_POT_WIV_N-2 | 1203.7049 | 0 | 8.1667 | 0 | Out= Nil, limit Qld to NSW on QNI to avoid transient instability on trip of both Wivenhoe pumps | Outage | Qld
T>T_LIPM_110_2B | 1202.1219 | 0 | 2.1667 | 0 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
N>N-BAMB_132_OPEN_B | 1182.752 | 0 | 3.75 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage | NSW
T^V_NIL_9 | 1151.6346 | 10067.1774 | 1.1667 | 23.6667 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
T^T_LIPM_1_DS | 1144.7173 | 0 | 1.0833 | 0 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line, dispatch only | Outage | Tas
S:V_420 | 1108.7278 | 0 | 1.4167 | 0 | South Australia to Victoria on both Heywood and Murraylink maximum transfer limit to avoid oscillatory instability This constraint equation was added, in January 2011, to a number of outage constraint sets across the NEM (except for Tasmania). The 420 MW value is the previous system normal limit. Throughout 2011 AEMO conducted studies as to whether the 420 MW limit was appropriate for various outages. In some cases the limit was increased. This work will continue in 2012. | Outage | SA
S-SNWF_WPWF_140 | 1092.5938 | 0 | 0.083333 | 0 | Discretionary upper limit for Snowtown WF + Wattle Pt WF generation <= 140 MW | Outage | SA
N^^V_EPMB_1 | 1089.5706 | 94.4054 | 3.1667 | 0.91667 | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
V:SS_820_HY_TEST | 1079.6816 | 779.7771 | 2.8333 | 3.1667 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
N>N-96H+96R_TE_1 | 1075.2923 | 5.614 | 18.1667 | 0.25 | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage | NSW
V:S_ARDM_560 | 1074.1397 | 146.4952 | 5.4167 | 1.0833 | Maintain maximum transfer limit of 560 MW on Heywood IC from VIC to SA to avoid oscillatory instability | Outage | Vic
V::N_X_HWSM_HWRO_xxx | 1067.2803 | 0 | 2.75 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_PP+TIPSB_MG | 1051.0176 | 0 | 3.25 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of half of Pelican Point PS(GT11 + ST18) + largest TIPS B unit declared as credible (South East Capacitor Available). | Outage | SA
V>>V_KTS_TX_A3_2_P | 1038.624 | 0 | 4.5 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, all HWPS 220kV bus tied, feedback | Outage | Vic
CA_MQS_47B62C84_01 | 1037.4674 | 0 | 0.083333 | 0 | Constraint Automation, O/L SNWHUM_T @BUNGAM for CTG LS5R on trip of MINTAR-W_LOO 132KV LINE. Generated by STNET[MANFR] Host MANEEMP1(MQ) | Outage | Constraint Automation
T^V_NIL_8 | 1035.9341 | 437.6987 | 2.25 | 1 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
T>T_NIL_LIPM_N-2_2B | 1026.1792 | 4568.9542 | 1.3333 | 1.5833 | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to South) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
S>NIL_BWMP_RHBR-T | 1021.455 | 21296.17 | 0.083333 | 8 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | SA
F_Q++LDTW_R60 | 1013.238 | 1130.7619 | 0.75 | 2.5833 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage | FCAS
F_S_TIPSA1_R6 | 994.8423 | 0 | 4.0833 | 0 | Out= NIL, Torrens Island A Unit 1 R6 Requirement <= 0MW | Outage | FCAS
F_Q++LDMU_L6 | 975.8259 | 0 | 5.1667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage | FCAS
F_MAIN+ML_L5_0400 | 965.4232 | 134.2903 | 332.1667 | 57.3333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
S>>CNLK_MKRB_WEMWP4 | 965.3377 | 0 | 1.25 | 0 | Out= Canowie-Mt Lock 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV on trip of Mokota-Robertstown 275kV line( this offloads Belalie-Mokota 275kV line and trips Hallet Hill WF), Feedback | Outage | SA
F_I+ML_L6_0400 | 953.7252 | 784.4772 | 4520.5 | 2899.5833 | NEM lower 6 second requirement for a NEM load event | NIL | FCAS
S>>DVBL_LKDV_WEWT | 936.2839 | 0 | 0.75 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East- Waterloo 132kV on trip of Mt Lock-Davenport 275kV line, Feedback | Outage | SA
F_Q++LDMU_L5 | 908.2682 | 0 | 2.9167 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage | FCAS
F_T++CSGO_TG_R6 | 900.9901 | 0 | 2 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS
V_ARARAT_ZERO | 896.8 | 652.252 | 0.5 | 0.5 | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
N^^Q_TW_330_BUS3_B1 | 885.8167 | 0 | 1 | 0 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | NSW
V>SML_BUDP_2 | 880.0711 | 14707.1645 | 3.4167 | 25.1667 | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage | Vic
F_T+NIL_ML_L60 | 856.78 | 425.7 | 481.9167 | 197.0833 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
CA_SPS_482F72C7_01 | 850.0574 | 0 | 0.91667 | 0 | Constraint Automation, O/L HWPS_YPS1_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
V::N_KTSY_MLSM_ET_xxx | 849.1686 | 666.7087 | 3 | 2 | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>N-NIL_HG | 735.6078 | 1558.6623 | 0.75 | 3.5 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
F_T++NIL_MG_R5 | 733.3027 | 2282.8121 | 20.0833 | 273.0833 | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
CA_MQS_48D013FF_01 | 732.8378 | 0 | 0.41667 | 0 | Constraint Automation, O/L ROBMW4_2 @MW_4 for CTG LSII on trip of BELALI-MOKOTA 275KV LINE. Generated by STNET[MANBL] Host MANEEMP1(MQ) | Outage | Constraint Automation
QNTE_ZERO | 680.0922 | 601.4909 | 0.91667 | 3 | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW | Outage | Qld
V::S_NIL_MAXG_xxx | 670.3092 | 116389.918 | 3.75 | 397.5 | Out = Nil, avoid transient instability for trip of the largest generation unit in South Australia There are two constraint equations that make up the transient stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
N^N-X_96H_LS_SVC | 643.3709 | 44.46 | 3.9167 | 3.1667 | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Coffs Harbour to Lismore (89) trip; TG formulation only | Outage | NSW
N>N-X_96H+9W2+96L_1 | 608.1443 | 0 | 12.0833 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Kempsey-Raleigh (9W2) and Lismore-Tenterfield (96L) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD | Outage | NSW
F_V+NIL_APD01_R6 | 598.9901 | 41.76 | 3.9167 | 1.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
F_T++FARE_N-2_TG_R6 | 581.9718 | 802.0234 | 3.0833 | 1.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_T+NIL_ML_L6 | 578.7891 | 280.8107 | 483.3333 | 194.9167 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN++ML_L6_0400 | 555.8295 | 132.1165 | 2051.9167 | 354.8333 | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
F_I+RREG_0400 | 545.6207 | 444.9067 | 1 | 0.5 | NEM Raise Regulation Requirement greater than 400 MW | Other | FCAS
N^^V_LTWG | 511.5383 | 0 | 2.4167 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse in Southern NSW for either loss of the largest VIC generating unit or Basslink, or loss of a Murray to Dederang 330 kV line | Outage | NSW
F_I+TG_R5_0850 | 508.7071 | 0 | 2.5 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 850 | Outage | FCAS
T^T_LFWA_1_DS | 501.719 | 0 | 0.33333 | 0 | Out = Lindisfarne to Waddamana 220 kV line, avoid voltage instability or violations for loss of the other Lindisfarne to Waddamana 220 kV line line, dispatch only | Outage | Tas
QNTE_OSCILLATE | 490.3384 | 0 | 9.4167 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Qld
F_S_TIPSA1_R60 | 485.4968 | 0 | 4.0833 | 0 | Out= NIL, Torrens Island A Unit 1 R60 Requirement <= 0MW | Outage | FCAS
V::N_SMF2_SD1 | 478.6344 | 0 | 0.5 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage | Vic
F_T+FASH_N-2_TG_R6_1 | 472.9925 | 3722.6533 | 2.0833 | 6.3333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
F_I+TG_R60_1300 | 472.8513 | 0 | 0.75 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1300 | Outage | FCAS
T>T_TUMBNN2_110_3 | 468.9747 | 0 | 1.0833 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.2 110kV lines, avoid O/L Tungatinah to New Norfolk No.3 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV line, Feedback | Outage | Tas
N^^Q_LS_VC_B1 | 462.507 | 19294.8873 | 0.83333 | 4.4167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
F_Q_TARONG#2_R60 | 459.1328 | 0 | 2.3333 | 0 | Out= NIL, Tarong 2 R60 Requirement <= 0MW | Outage | FCAS
T_T_BA_JB_RC2_250 | 450.668 | 9282.3753 | 0.66667 | 3.25 | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
V^^S_SETB_TBSE_2 | 449.7565 | 0 | 2.0833 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | SA
T>T_BWLF_110_4 | 448.8179 | 0 | 0.25 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana 110 kV line, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Tas
F_S_TIPSA4_R6 | 448.0923 | 0 | 1.8333 | 0 | Out= NIL, Torrens Island A Unit 4 R6 Requirement <= 0MW | Outage | FCAS
F_MAIN++APD_TL_L60 | 443.1486 | 513.5417 | 805.8333 | 317.6667 | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL | FCAS
V::N_X_MLSM_EMTT_xxx | 433.7927 | 1579.0269 | 2.8333 | 5.4167 | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T_MA_WESTCOAST_2 | 430.4176 | 0 | 1.0833 | 0 | Limit Mackintosh to 90% of West Coast load | Outage | Tas
F_Q_W/HOE_R5 | 428.1946 | 0 | 1.75 | 0 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage | FCAS
F_I+TG_R60_0850 | 420.74 | 0 | 2.5 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 850 | Outage | FCAS
N^N-967_LS_SVC | 412.9251 | 0 | 6.8333 | 0 | Out= Koolkhan to Lismore (967) and Lismore SVC, avoid Voltage collapse on CoffsHarbour to Lismore(89) trip; TG formulation only | Outage | NSW
F_Q_TARONG#1_R60 | 404.1328 | 0 | 1.9167 | 0 | Out= NIL, Tarong 1 R60 Requirement <= 0MW | Outage | FCAS
T>T_PMSH_IMP_4D | 404.0928 | 0 | 0.5 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
F_I+ML_L60_0400 | 386.2774 | 115.7374 | 1534.9167 | 354.75 | NEM lower 60 second requirement for a NEM load event | NIL | FCAS
F_T++NIL_ML_L60 | 384.8854 | 220.2447 | 206.4167 | 121.0833 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
T::T_NIL_2 | 379.876 | 4888.7425 | 2.6667 | 13.4167 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL | Tas
S>X_NWCB6225+6021_T1 | 367.0126 | 0 | 3.5833 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225 (which also causes an outage of North West Bend to Monash #1 132 kV line), avoid overloading North West Bend 132/66 kV #1 transformer on trip of North West Bend to Morgan Whyalla pump 1 132 kV line | Outage | SA
SVML_233 | 364.2511 | 0 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 233 MW | NIL | SA
V::N_EPMB_xxx | 352.9106 | 525.3903 | 0.66667 | 7 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_BLKRG_TBSE_2 | 342.6106 | 107045.5395 | 0.5 | 54.1667 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
F_S++HYSE_L60 | 333.1473 | 243872.7495 | 45.8333 | 26.5 | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage | FCAS
V>>V_LTMS_1 | 328.6459 | 0 | 0.16667 | 0 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage | Vic
T::T_HA_GT_PM_3 | 328.4471 | 0 | 1.4167 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. | Outage | Tas
N^^V_LTMS | 326.1636 | 0 | 1.8333 | 0 | Out = Lower Tumut to Murray 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
TV_560 | 318.7625 | 0 | 0.16667 | 0 | Tas to Vic on Basslink upper limit of 560 MW | Outage | Tas
T>>T_GTHA_EXP_3H | 317.4709 | 0 | 0.25 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
TV_575 | 313.6279 | 0 | 0.16667 | 0 | Tas to Vic on Basslink upper limit of 575 MW | Outage | Tas
F_I+TG_R5_1300 | 306.5405 | 0 | 0.75 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1300 | Outage | FCAS
T>T_PMSH_2A | 298.5442 | 0 | 1.0833 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow to George Town) for trip of the other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
V>>SML_BESH_2 | 292.6202 | 0 | 0.66667 | 0 | Out = Bendigo to Shepparton 220 kV line, avoid O/L Darlington Pt to Balranald to Buronga (X5/1 & X5/3) 220kV line on loss of Ballarat to Bendigo 220kV line, feedback | Outage | Vic
VS_500 | 290.4354 | 0 | 0.41667 | 0 | VIC to SA on Heywood upper transfer limit of 500 MW | Outage | Vic
F_V+NIL_APD01_R5 | 278.2833 | 17.69 | 3.9167 | 1.3333 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
V::S_NIL_SETB_SECP_1 | 274.9595 | 378.8694 | 0.5 | 1.25 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
F_V+NIL_APD01_R60 | 273.2801 | 28.57 | 4.0833 | 1.1667 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
F_T+NIL_ML_L5 | 272.95 | 0.17 | 183.9167 | 0.083333 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
F_QNV+MO_TG_R60 | 270.6545 | 0 | 3.75 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 60 sec requirement for Mortlake generation loss on trip of other line, Basslink unable to transfer FCAS | Outage | FCAS
V>V_NIL_RADIAL_10 | 264.1526 | 10017.1044 | 0.16667 | 1.8333 | Out = Nil, avoid O/L of Yallourn to Rowville No. 7 or No. 8 220 kV line for trip of the Yallourn to Rowville No. 8 or No. 7 220 kV line. Yallourn W1 on 220 kV side. Feedback | NIL | Vic
V>V_HWYP2_1_R | 262.5967 | 0 | 0.25 | 0 | Out = Hazelwood to Yallourn No. 2 220 kV line, avoid O/L Yallourn to Hazelwood PS No.1 220kV line on trip of Yallourn to Rowville No.5 220kV line, Radial mode, YWG1 on 220kV, Feedback | Outage | Vic
N>N-KKLS_TE_2 | 255.2845 | 0 | 1 | 0 | Out = Koolkhan to Lismore (967) 132 kV line, avoid overloading the Armidale to Glen Innes (96T) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects that this constraint equation will continue to bind for a reasonable portion of any future outage times. | Outage | NSW
VN_0700 | 245.5513 | 64.3038 | 1.8333 | 0.41667 | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage | Vic
V::N_HYMO_xxx | 243.6509 | 192.6525 | 0.33333 | 0.58333 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S>>CNRB_MKRB_WEMWP4 | 242.3061 | 1010.4904 | 1.0833 | 13.75 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | SA
T>T_NIL_BL_3C | 241.2419 | 0 | 0.16667 | 0 | Out = Nil, avoid overloading a Hadspen to Palmerston 220 kV line for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action | NIL | Tas
F_MAIN+LREG_0400 | 240.9 | 0 | 0.083333 | 0 | Mainland Lower Regulation Requirement greater than 350 MW, Basslink unable to transfer FCAS | Other | FCAS
V::N_HWCB_xxx | 238.5462 | 0 | 1.5 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
VSML_-080 | 236.4422 | 0 | 0.25 | 0 | Vic to SA on ML upper transfer limit of -80 MW | Outage | Vic
VS_250 | 229.0772 | 0 | 3.5833 | 0 | Victoria to South Australia on Heywood upper transfer limit of 250 MW This constraint equation is included in a number of constraint sets which are used for outages of the 500 kV lines in from Sydenham to Heywood and the 275 kV lines from Heywood to South East. | Outage | Vic
F_T++BB_N-2_TG_R6 | 220.6514 | 0 | 1.6667 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
V::S_NIL_TBSE_1 | 220.2367 | 857.1829 | 2.1667 | 2.75 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
VSML_-050 | 218.3188 | 0 | 0.5 | 0 | Vic to SA on ML upper transfer limit of -50 MW | Outage | Vic
F_S_TIPSA4_R60 | 216.5768 | 0 | 1.8333 | 0 | Out= NIL, Torrens Island A Unit 4 R60 Requirement <= 0MW | Outage | FCAS
V>>V_NIL_8 | 209.9594 | 2308.7927 | 0.83333 | 1.4167 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL | Vic
F_T++FASH_N-2_TG_R60 | 208.1177 | 29.8882 | 4.9167 | 3.4167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_T+NIL_BB_TG_R6 | 200.6161 | 4539.2913 | 0.91667 | 377.1667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
T_FATI | 198.4677 | 0 | 0.16667 | 0 | Out=Farrell-Tribute 220KV line. Energy <= 0MW | Outage | Tas
V>>V_DDSM_1 | 196.0694 | 10895.3054 | 0.16667 | 20.8333 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Vic
F_I+TG_R6_1300 | 190.9431 | 0 | 0.75 | 0 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1300 | Outage | FCAS
VSML_-040 | 185.7213 | 0 | 0.33333 | 0 | Vic to SA on ML upper transfer limit of -40 MW | Outage | Vic
F_V_APD01_L5 | 184.61 | 46.2304 | 60 | 26.1667 | Out= NIL, APD Potline 1 L5 Requirement <= 0MW | Outage | FCAS
F_MAIN+APD_TL_L60 | 180.77 | 5319.8196 | 218.8333 | 4078.8333 | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink unable to transfer FCAS | NIL | FCAS
S::V_TBSE_TBSE_1 | 173.5603 | 1656.3775 | 2.1667 | 2.4167 | Out = one Tailembend-South East 275kV line (NOTE: with both Black Range series capacitors I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines | Outage | SA
N^^V_DDSM2 | 172.5555 | 2767.9964 | 1 | 3.4167 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse for loss of remaining Dederang to South Morang 330 kV line | Outage | NSW
V>>V_NIL_1A | 164.8365 | 1108.3426 | 0.33333 | 1.25 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
S>V_NIL_SETX_SETX1 | 162.2227 | 14311.8392 | 0.083333 | 1.4167 | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL | SA
F_MAIN+ML_L6_0400 | 160.69 | 1307.9778 | 515.6667 | 3590.75 | Out = Nil, lower 6 sec requirement for a Mainland load event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
T>T_NIL_110_26_HM | 157.4426 | 0 | 0.083333 | 0 | Out = Nil, West Coast 220/110 kV parallel closed, avoid overloading Waratah Tee to Hampshire 110 kV line for loss of a Farrell to Sheffield 220 kV line, feedback | NIL | Tas
N>N-BAMB_132_OPEN_A | 155.1191 | 68547.0798 | 0.58333 | 68.4167 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | NSW
N^^Q_LS_VC_B4 | 154.2712 | 0 | 1.9167 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage | NSW
N^^Q_AR_VC_B4 | 153.9643 | 0 | 1 | 0 | Out= Armidale SVC, avoid Voltage Collapse on loss of Tarong North | Outage | NSW
F_T+FARE_N-2_TG_R6_1 | 153.6346 | 24520.349 | 0.66667 | 17 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage | FCAS
V:S_MSUT_560 | 145.6303 | 37.0322 | 1.8333 | 0.66667 | Out = Murray - Upper Tumut (65) 330kV line, VIC to SA on Heywood upper transfer limit of 560 MW based on oscillatory stability. | Outage | Vic
F_I+TG_R60_1200 | 145.0815 | 0 | 0.25 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1200 | Outage | FCAS
F_Q++NIL_R5 | 143.0909 | 0.03 | 1.0833 | 0.25 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL | FCAS
S_TIPSB2+B1_270 | 142.6272 | 0 | 0.66667 | 0 | Discretionary upper limit for TIPS B2 + B1 <= 270 MW | Outage | SA
V^^S_NIL_TBSE_1 | 140.8212 | 0 | 0.083333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
F_MAIN+ML_L60_0400 | 132.2634 | 27.99 | 275.8333 | 51.25 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_T+NIL_BB_TG_R60 | 131.45 | 3488 | 4.5833 | 363.3333 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
V>>V_NIL_1B | 129.5768 | 25679.7423 | 1.0833 | 1.75 | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL | Vic
F_N_GUTHEGA_L5 | 125.3325 | 0 | 43 | 0 | Out= NIL, Guthega L5 Requirement <= 0MW | Outage | FCAS
T>T_PMSH_2B | 125.1676 | 0 | 0.41667 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
V>>N-LTUT_A | 123.6897 | 0 | 0.083333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
F_T++NIL_ML_L6 | 122.8562 | 2399.9838 | 119.0833 | 92.25 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
S>>NIL_TBTU_TBMO_1 | 122.1295 | 1021.208 | 0.5 | 4.5 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
N::Q_LDNC_TNT | 120.8119 | 0 | 0.083333 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage | NSW
V::S_NIL_SETB_SECP_2 | 118.6979 | 78.8836 | 0.16667 | 0.75 | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
N^^N_NIL_1 | 110.7605 | 3378.3493 | 0.083333 | 1.4167 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
T>T_NIL_BL_110_8 | 109.6455 | 0 | 0.16667 | 0 | Out = Nil, avoid overloading the New Norfolk to Creek Road 110 kV line (flow to south) for loss of the New Norfolk to Chapel St 110 kV line | NIL | Tas
T>T_NIL_BL_IMP_3F | 100.3034 | 0 | 0.41667 | 0 | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220 kV line with no SPS action, feedback | NIL | Tas
S>V_NWRB2_RBNW1 | 95.9095 | 5336.7889 | 0.16667 | 34.9167 | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage | SA
V>NWCB6024+25_TX1 | 93.9495 | 0 | 0.41667 | 0 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #1 132/66kV TX on trip of Monash-North West Bend #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | SA
TV_550 | 91.9778 | 0 | 1.0833 | 0 | Tas to Vic on Basslink upper limit of 550 MW | Outage | Tas
T^V_NIL_BLCAP | 89.5063 | 539.499 | 0.083333 | 1.8333 | Outage = Nil, Basslink HF7 98 MVAr cap bank unavailable, limit Basslink to 460 MW at George Town under conditions of low George Town 220 kV voltage. | NIL | Tas
VN_0800 | 88.941 | 591.4915 | 0.25 | 3.6667 | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage | Vic
F_MAIN++LREG_0400 | 84.3379 | 1827.794 | 0.16667 | 5.0833 | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Other | FCAS
F_I+TG_R5_1200 | 83.2842 | 0 | 0.25 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1200 | Outage | FCAS
S>V_460_DYN | 82.5406 | 0 | 0.75 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | SA
V::N_KGRC_xxx | 80.8235 | 1448.0159 | 0.41667 | 9.6667 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>V_NIL_RADIAL_3-4_7 | 80.0233 | 0 | 0.083333 | 0 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split) | NIL | Vic
V^SML_BAWB_3 | 75.7824 | 0 | 1.75 | 0 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
V>>N-LTWG_RADIAL_1 | 75.5309 | 0 | 0.33333 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
T>T_PMSH_IMP_4B | 72.3181 | 0 | 0.083333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
V^^S_NIL_MAXG_xxx | 71.4015 | 0 | 0.75 | 0 | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off There are two constraint equations that make up the voltage stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
F_T+NIL_BB_TG_R5 | 71.4 | 0.3 | 2.8333 | 0.083333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN++ML_L60_0400 | 71.1855 | 6.63 | 281.6667 | 16.9167 | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
V::N_MLTR_xxx | 66.5529 | 224.9851 | 0.5 | 0.91667 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T>T_NIL_BL_IMP_5FF | 66.4561 | 13661.1961 | 0.083333 | 0.083333 | Out = Nil, avoid overloading Hadspen to Georgetown No.2 220 kV line for trip of the Hadspen to Georgetown No.1 220 kV line with no SPS action | NIL | Tas
V::N_HORC_xxx | 64.702 | 227.8982 | 0.58333 | 2 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_I+TG_R6_1200 | 61.68 | 0 | 0.25 | 0 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1200 | Outage | FCAS
V^^S_NIL_SETB_SECP_1 | 60.3392 | 0 | 0.16667 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Long Term Voltage Stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
F_T+CSGO_TG_R5 | 60 | 225.3149 | 0.33333 | 3.6667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
N>>V-X_BUDP_DDMS_A | 58.186 | 0 | 0.16667 | 0 | Out= Dederang to Murray (67 or 68) and Darlington Point to Buronga (X5) line, avoid the other Murray to Dederang (68 or 67) O/L on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback, Feedback | Outage | NSW
T_T_X_FASH_A | 57.9213 | 0 | 0.083333 | 0 | Out = both Farrell to Sheffield lines, limit West Coast gen <= 110% of West Coast load | Outage | Tas
V^^S_BLKRG_TBSE_2 | 56.8375 | 7988.9344 | 1.5 | 9.75 | Out = both or one Black Range series capacitors O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
F_T++FARE_N-2_TG_R60 | 56.2412 | 2.1729 | 1.25 | 0.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
V>>V_MLSY_KTSBP_1AR | 55.6364 | 6107.8374 | 1.8333 | 28.5 | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage | Vic
F_T+BB_N-2_TG_R5 | 54.6 | 0 | 2.1667 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS
Q>>BCRG_CLWU_BCCP | 50.5861 | 0 | 0.25 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
F_MAIN++ML_L5_APD | 49.2025 | 0 | 9.9167 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
S>>KHKN_SETB_SETB | 47.5221 | 0 | 0.66667 | 0 | Out= Keith-Kincraig 132 kV line (Note: with both Black Range series caps I/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage | SA
F_I+TG_R60_1000 | 42.342 | 0 | 0.16667 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage | FCAS
F_I+ML_L5_APD | 41.4581 | 0 | 21 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage | FCAS
S:V_580 | 38.9752 | 0 | 0.33333 | 0 | Out = One Heywood 500/275 kV txfmr (two remain in service), maintain maximum SA to VIC transfer limit of 580 MW on Heywood and Murraylink combined to avoid oscillatory instability | Outage | SA
F_I+TG_R5_1000 | 37.98 | 0 | 0.16667 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1000 | Outage | FCAS
F_I+ML_L6_APD | 37.3973 | 12.43 | 142 | 41.75 | NEM lower 6 second requirement for loss of APD potlines | Outage | FCAS
F_I+LREG_0400 | 37.14 | 1182.0032 | 0.16667 | 6.3333 | NEM Lower Regulation Requirement greater than 400 MW | Other | FCAS
F_V_APD01_L60 | 36.6015 | 9.44 | 53.0833 | 22.5 | Out= NIL, APD Potline 1 L60 Requirement <= 0MW | Outage | FCAS
S>>PARB_RBTU_WEWT | 36.4015 | 0 | 0.75 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
F_T+CSGO_TG_R60 | 36 | 449.6454 | 0.33333 | 2.1667 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
V::N_SMSC_xxx | 34.939 | 6034.7944 | 0.25 | 19.0833 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_Q_MEWV_824_R5 | 27.094 | 0 | 0.25 | 0 | Out= Mt England to Wivenhoe (824) line, Raise 5 min requirement of zero for Wivenhoe #2 | Outage | FCAS
N>N-X_96H+9W2+9W5_1 | 26.9741 | 0 | 0.25 | 0 | Out= Coffs Harbour-Koolkhan (96H) & Raleigh-Kempsey(9W2) & Macksville-Kempsey(9W5), avoid O/L Armidale-Coffs Harbour (96C) on trip of Armidale-Coffs Harbour (87), Swamp out when all 3 directlink cable O/S,Feedback, TG formulation in PD/ST | Outage | NSW
F_T++BB_N-2_TG_R60 | 25.04 | 0 | 1.5833 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_T++FASH_N-2_TG_R5 | 24.6036 | 863.5501 | 1.75 | 5.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_Q_TARONG#1_R6 | 23.2 | 0 | 0.33333 | 0 | Out= NIL, Tarong 1 R6 Requirement <= 0MW | Outage | FCAS
F_Q_TARONG#2_R6 | 23.2 | 0 | 0.33333 | 0 | Out= NIL, Tarong 2 R6 Requirement <= 0MW | Outage | FCAS
I_CTRL_ISSUE_ML | 22.2175 | 32997.9005 | 0.41667 | 6.3333 | DC Link Control Issue Constraint for Murraylink | Outage | Other
F_I+WIP_N-2_ML_L6 | 22.2151 | 0 | 15.6667 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 6 sec requirement | Outage | FCAS
CA_MQS_4780983C_01 | 21.7204 | 0 | 0.083333 | 0 | Constraint Automation, O/L TABSES_2 @S_EAST for CTG LSIC on trip of T_BEND-S_EAST 275KV 1 LINE. Generated by STNET[MANBL] Host MANEEMP2(MQ) | Outage | Constraint Automation
N^^V_MSUTLT_2 | 21.7001 | 0 | 0.16667 | 0 | Out = Murray to Upper Tumut or Murray to Lower Tumut 330 kV line, avoid voltage collapse in Southern NSW for loss of Murray to Lower Tumut or Murray to Upper Tumut 330 kV line | Outage | NSW
F_T+FARE_N-2_RREG | 17.4584 | 4196.1517 | 1.25 | 7.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | FCAS
F_V+NIL_APD01_L5 | 17.41 | 2.9203 | 3.8333 | 1.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
F_Q_TARONG#1_RREG | 17.1005 | 0 | 0.16667 | 0 | Out= NIL, Tarong 1 RREG Requirement <= 0MW | Outage | FCAS
F_Q_TARONG#2_RREG | 17.1005 | 0 | 0.16667 | 0 | Out= NIL, Tarong 2 RREG Requirement <= 0MW | Outage | FCAS
F_V_APD01_L6 | 16.6298 | 6.66 | 50.1667 | 22.5 | Out= NIL, APD Potline 1 L6 Requirement <= 0MW | Outage | FCAS
F_T+FASH_N-2_TG_R60 | 15.93 | 144.8039 | 0.58333 | 5.3333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
F_T++BB_N-2_TG_R5 | 14.6447 | 0 | 1.0833 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_T+BB_N-2_TG_R60 | 14.34 | 892.8538 | 0.5 | 92.8333 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
T^^V_GTSH_1 | 13.5535 | 2006.2784 | 0.083333 | 2.5 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
F_ESTN++MLMO_L60 | 13.26 | 19.75 | 8.5 | 13.4167 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
VSML_VFRB_OFF | 11.6181 | 0 | 0.083333 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL | Vic
V>>V_BAEL_1 | 11.4656 | 0 | 0.16667 | 0 | Out = Ballarat to Elaine 220 kV line section, avoid O/L Moorabool to Ballarat No. 1 220 kV line on trip of Moorabool to Terang 220 kV line, feedback | Outage | Vic
F_MAIN+ML_L5_APD | 11.16 | 167.9561 | 0.33333 | 27.5833 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_N_GUTHEGA_L60 | 10.57 | 0 | 40.75 | 0 | Out= NIL, Guthega L60 Requirement <= 0MW | Outage | FCAS
Q:N_AR_CP2_BI_POT | 9.8992 | 0 | 0.16667 | 0 | Out = Armidale capacitor bank (120MVAr), Qld to NSW on QNI Transient Stability Limit, Loss of Boyne Island 375MW potline, 1 or 2 Millmerran units I/S | Outage | Qld
V^^S_KHKN_SETB | 9.1318 | 0 | 0.16667 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
F_T++NIL_ML_L5 | 8.6363 | 49.0515 | 21.5 | 34.6667 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
V>>N-LTUT_G | 8.2389 | 0 | 0.16667 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage | Vic
V>NWBCB6225_TX1 | 8.158 | 0 | 1 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 132/66kV TX1 on trip of Monash-North West Bend #2 132kV line, Feedback | Outage | SA
V>>N-DPWG_X5_A | 8.1398 | 0 | 0.16667 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Buronga (X5), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
F_V+NIL_APD01_L60 | 5.61 | 0.86 | 3.1667 | 1.4167 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
F_T+FARE_N-2_TG_R5 | 5.147 | 47.3876 | 0.083333 | 3.3333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_Q++ARDM_R5 | 4.96 | 0 | 0.083333 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 5 min Requirement | Outage | FCAS
F_I+ML_L60_APD | 4.3942 | 0 | 20.25 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
F_MAIN++ML_L6_APD | 3.96 | 0.33 | 17.6667 | 1.3333 | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | Outage | FCAS
F_T++COGT_TL_L6 | 3.9123 | 364.3387 | 2.8333 | 5.3333 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
V^SML_HORC_3 | 3.7568 | 0 | 0.33333 | 0 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
V>S_NIL_HYSE | 3.3501 | 14000 | 0.083333 | 0.083333 | Out = NIL, avoid O/L either Heywood to South East 275 kV line on trip of parallel circuit, flow VIC to SA, feedback | NIL | Vic
F_MAIN++ML_L60_APD | 2.12 | 0 | 5.8333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
F_V+NIL_APD01_L6 | 1.98 | 0.3 | 3.25 | 1.1667 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
F_MAIN+ML_L6_APD | 1.24 | 231.3 | 2.1667 | 427.75 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_T+FASH_N-2_TG_R5 | 1.2 | 52.72 | 0.083333 | 3.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
T>>T_NIL_BL_EXP_6E | 0.76262 | 115905.6153 | 0.083333 | 79.5833 | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL | Tas
F_MAIN+ML_L60_APD | 0.65 | 24.72 | 0.33333 | 26.5 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
N_MBTE1_A | 0.38375 | 24.4589 | 0.16667 | 3.1667 | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
F_T++FARE_N-2_TG_R5 | 0.3 | 0.01 | 0.5 | 0.083333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_T++NIL_BLSPS_L60_1 | 0.18 | 0 | 0.083333 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS
F_T++NIL_BLSPS_L5 | 0.17 | 0 | 0.083333 | 0 | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL | FCAS
V>X_NWCB6225+6021_T1 | 0.1639 | 0 | 0.083333 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225, avoid overloading North West Bend 132/66 kV #1 transformer on trip of North West Bend to Morgan Whyalla pump 1 132 kV line | Outage | SA
F_T++COGT_TL_L60 | 0.16 | 9.3647 | 0.083333 | 4.9167 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
F_ESTN++HYMO_L60 | 0.14 | 104.779 | 0.58333 | 52.75 | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage | FCAS
F_T++NIL_BLSPS_L6_1 | 0.12 | 0 | 0.083333 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS
F_T++CSGO_TG_R5 | 0.1 | 0 | 0.16667 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS
F_MAIN++APD_TL_L6 | 0.02 | 0 | 0.083333 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS

## Summary By Region
Binding Hours
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Ad-Hoc | 45.6667 | 0.16667
Constraint Automation | 39.5833 | 13.3333 | 12.25 | 5.5 | 24.9167 | 4.75
FCAS
NSW | 1639.5 | 5095.5833 | 3586.0833 | 3112.1667 | 2768.5 | 4260.0833
Negative Residue | 25.8333 | 38 | 12.25 | 13.0833 | 46.8333 | 25.75
Non-Conformance | 602.9167 | 479.6667 | 358.5 | 228.6667 | 156.6667 | 97.3333
Other |  | 11.5 | 35.5833 | 142.6667 | 50.5833 | 311.8333
Outage Ramping | 297.5833 | 197.5 | 162.5833 | 236.8333 | 251.8333 | 142.25
Qld | 1685.25 | 1265.1667 | 2850.25 | 913.75 | 1756.6667 | 996.6667
Quick | 109.5 | 1149.8333 | 132.3333 | 281.5 | 1018.4167 | 3070.3333
SA | 2769.1667 | 2568.1667 | 2144.9167 | 3383.5833 | 3995.1667 | 2013.25
Tas | 1887.0833 | 3387.9167 | 1247.1667 | 354.5833 | 895.9167 | 923.1667
Vic | 1782.75 | 2605.25 | 3277.5833 | 5660.4167 | 6854 | 2618
Binding Impact
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Ad-Hoc | 169022.6006
Constraint Automation | 71318.6756 | 118018.5319 | 72630.7349 | 61543.4159 | 64122.5584 | 6287.0142
FCAS | 1545398.0698 | 2025902.8396 | 2312077.1775 | 11967737.2201 | 27702893.4048 | 24018595.0767
NSW | 703170.4773 | 2061311.3279 | 2666446.6314 | 3008201.0876 | 2981579.7124 | 3811263.7887
Negative Residue | 76369.2876 | 346084.2837 | 193679.0393 | 133618.843 | 159141.1919 | 65879.5695
Other |  | 162.4387 | 1327.1417 | 5944.8762 | 35445.6298 | 19441.5552
Qld | 20515669.2251 | 8241677.7744 | 3351642.8339 | 17832407.3191 | 3412397.6405 | 1557960.0849
SA | 5291489.0596 | 4307596.7546 | 7308788.4534 | 7975370.452 | 19175976.6502 | 19603528.2545
Tas | 523692.0838 | 15879751.959 | 7917341.1843 | 2498349.5552 | 3312667.8479 | 4771966.3751
Vic | 1407859.0887 | 4550348.9087 | 6717447.0811 | 3149671.2278 | 6498415.4069 | 3681628.8597
Total | 30303988.5681 | 37530854.8184 | 30541380.2775 | 46632843.9969 | 63342640.0428 | 57536550.5786
Note on A5: FCAS excluded as it will swamp the graph

## NIL vs Outage
Binding Hours
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Commissioning | 0 | 1849.75 | 36.3333 | 166.5 | 71.1667 | 453
FCAS - NIL | 72832.6667 | 67438.5 | 71339 | 78805.6667 | 98153.9167 | 83335.5
FCAS - Outage | 5527.1667 | 6939.25 | 5271.75 | 2785.8333 | 6213.6667 | 5623.9167
System Normal | 5333 | 7521.0833 | 8116.3333 | 7848.6667 | 9089.5 | 6047.6667
Network Support | 391.4167 | 339.6667 | 155.8333 | 204.5 | 128.3333 | 55.6667
Negative Residues | 25.8333 | 38 | 12.25 | 13.0833 | 46.8333 | 25.75
Outage | 4727.5 | 6841.0833 | 5240.1667 | 5748.1667 | 7284.5833 | 5121.75
Total (non-FCAS) | 10477.75 | 16589.5833 | 13560.9167 | 13980.9167 | 16620.4167 | 11703.8333
Binding Impact
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Commissioning | 0 | 11072953.0178 | 23582.5681 | 1122946.4259 | 123874.3701 | 695791.4608
FCAS - NIL | 1018103.8043 | 1330596.4579 | 1920731.4196 | 1523297.0635 | 4284769.1816 | 9691374.8176
FCAS - Outage | 527294.2655 | 695306.3817 | 391353.9579 | 10444462.1066 | 23418124.2233 | 14327220.2591
System Normal | 4759558.4085 | 17466013.2732 | 20601341.3495 | 7628472.3458 | 13101240.0894 | 16979263.4586
Network Support | 13604633.6237 | 5680587.956 | 4678541.5594 | 22261395.2873 | 8878912.2779 | 965379.2057
Negative Residues | 76369.2876 | 346084.2837 | 193679.0393 | 134581.6187 | 159141.1919 | 65879.5695
Outage | 10318029.1786 | 2940926.3226 | 2769291.9038 | 4643343.5874 | 13500453.0789 | 15507433.2681
Total | 30303988.5681 | 39532467.6929 | 30578521.7976 | 47758498.4352 | 63466514.413 | 58232342.0394

## Interconnector Binding
Interconnector Direction | Constraint Equation ID | 2017 Hours | 2016 Hours | Description | Type
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 308.25 | 43.0833 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | N^N_KKLS_1 | 229.6667 | 2.3333 | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. | Outage
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 77.5 | 340.1667 | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator | NIL
N-Q-MNSP1 Export | N>N-CHKK_TE_1 | 71.9167 | 12.6667 | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | N_X_MBTE2_A | 45.4167 | 137 | Out = two Directlink cables, NSW to Queensland limit | Outage
N-Q-MNSP1 Export | N_X_MBTE_3A | 34.75 | 211.1667 | Out = all three Directlink cables, NSW to Queensland limit | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_I_E | 31.6667 | 40 | Quick constraint equation applied to Terranora Interconnector at various levels | Other
N-Q-MNSP1 Export | N^Q_NIL_A | 21 | 72.25 | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL
N-Q-MNSP1 Export | NQTE_ROC | 18.4167 | 82.8333 | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL
N-Q-MNSP1 Export | N>N-96H+96R_TE_1 | 18.1667 | 0.58333 | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage
N-Q-MNSP1 Export | N>LSDU_LSDU | 18.0833 | 59.4167 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | N>N-X_96H+9W2+96L_1 | 12.0833 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Kempsey-Raleigh (9W2) and Lismore-Tenterfield (96L) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD | Outage
N-Q-MNSP1 Export | N^^Q_NIL_A | 10.5 | 0 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
N-Q-MNSP1 Export | QNTE_OSCILLATE | 7.3333 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage
N-Q-MNSP1 Export | N^N-967_LS_SVC | 6.8333 | 0 | Out= Koolkhan to Lismore (967) and Lismore SVC, avoid Voltage collapse on CoffsHarbour to Lismore(89) trip; TG formulation only | Outage
N-Q-MNSP1 Export | N>>Q_LDMU_B | 5.5833 | 0 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage
N-Q-MNSP1 Export | N>N-X_96H+9W2_1 | 5 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Kempsey-Raleigh (9W2) and 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD | Outage
N-Q-MNSP1 Export | N^N-X_96H_LS_SVC | 3.9167 | 3.1667 | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Coffs Harbour to Lismore (89) trip; TG formulation only | Outage
N-Q-MNSP1 Export | N>N-NIL_LSDU | 3.5 | 10.5833 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line | NIL
N-Q-MNSP1 Export | N^^Q_LS_VC_B4 | 2.25 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage
N-Q-MNSP1 Export | N>>N-NIL__3_OPENED | 1.75 | 40.1667 | Out = Nil, avoid overloading Liddell to Muswellbrook (83) 330kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL
N-Q-MNSP1 Export | #R015535_001_RAMP_F | 1.25 | 0 | Hard Ramping constraint for constraint N>N-96H+96R_TE_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | N^^Q_TW_330_BUS3_B1 | 1 | 0 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | #R015576_001_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint N>N-96H+96R_TE_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R015105_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R015831_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R015956_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016632_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R015114_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R015630_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N>N-X_96H+9W2+96L_1, Effective Date: 27/01/2017, Version: 1 | Other
N-Q-MNSP1 Export | #R015630_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N>N-X_96H+9W2+96L_1, Effective Date: 27/01/2017, Version: 1 | Other
N-Q-MNSP1 Export | #R016260_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R015621_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>N-X_96H+9W2+96L_1, Effective Date: 27/01/2017, Version: 1 | Other
N-Q-MNSP1 Export | #R015621_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N>N-X_96H+9W2+96L_1, Effective Date: 27/01/2017, Version: 1 | Other
N-Q-MNSP1 Export | #R016345_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^N-967_LS_SVC, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | F_Q++LDTW_R6 | 0.33333 | 1.5 | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
N-Q-MNSP1 Export | N>N-BAMB_132_OPEN_A | 0.33333 | 39.6667 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage
N-Q-MNSP1 Export | N^^Q_AR_VC_B4 | 0.33333 | 0 | Out= Armidale SVC, avoid Voltage Collapse on loss of Tarong North | Outage
N-Q-MNSP1 Export | #R015114_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016288_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B4, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | N>N-X_96H+9W2+9W5_1 | 0.25 | 0 | Out= Coffs Harbour-Koolkhan (96H) & Raleigh-Kempsey(9W2) & Macksville-Kempsey(9W5), avoid O/L Armidale-Coffs Harbour (96C) on trip of Armidale-Coffs Harbour (87), Swamp out when all 3 directlink cable O/S,Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | #R015761_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>N-X_96H+9W2+96L_1, Effective Date: 27/01/2017, Version: 1 | Other
N-Q-MNSP1 Export | #R016260_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | N>N-KKLS_TE_2 | 0.16667 | 0 | Out = Koolkhan to Lismore (967) 132 kV line, avoid overloading the Armidale to Glen Innes (96T) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B1 | 0.16667 | 0.083333 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | #R015523_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R015567_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>N-96H+96R_TE_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016303_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B2, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016303_007_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B6, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | N>>N-NIL__3_CLOSED | 0.083333 | 12.9167 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL
N-Q-MNSP1 Export | N_MBTE1_A | 0.083333 | 3.1667 | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 1157.9167 | 431.6667 | Out = two Directlink cables, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | N_MBTE1_B | 206 | 10 | Out = one Directlink cable, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | N_X_MBTE_3B | 189.25 | 653.5 | Out = all three Directlink cables, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | Q>N-MUTE_758 | 68.9167 | 0.083333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 45.0833 | 6.75 | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
N-Q-MNSP1 Import | Q>N-MUTE_757 | 30.3333 | 2.5 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L6 | 24.4167 | 5 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N_NIL_TE_B | 23.4167 | 1.6667 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL
N-Q-MNSP1 Import | QNTE_150 | 19.4167 | 0 | Qld to NSW on Terranora Interconnector upper transfer limit of 150 MW | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 18.3333 | 4.8333 | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 17.25 | 6.8333 | Negative Residue Management constraint equation for QLD to NSW flow | NIL
N-Q-MNSP1 Import | QNTE_ROC | 15.8333 | 84.75 | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | F_Q++LDTW_L6 | 13.4167 | 0.91667 | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L5 | 9.9167 | 2.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 9.1667 | 22.8333 | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies | NIL
N-Q-MNSP1 Import | F_Q++LDTW_L5 | 8 | 0.16667 | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
N-Q-MNSP1 Import | N>N-BAMB_132_OPEN_B | 3.75 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage
N-Q-MNSP1 Import | N>N-NIL_MBDU | 3.4167 | 0.083333 | Out = Nil, avoid overloading Mullumbimby to Dunoon (9U6 or 9U7) 132 kV line on trip of the other Mullumbimby to Dunoon (9U7 or 9U6) 132 kV line | NIL
N-Q-MNSP1 Import | I_CTRL_ISSUE_TE | 3.1667 | 1.1667 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Import | #N-Q-MNSP1_I_E | 1.75 | 0 | Quick constraint equation applied to Terranora Interconnector at various levels | Other
N-Q-MNSP1 Import | #N-Q-MNSP1_RAMP_I_F | 1.75 | 0.25 | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Other
N-Q-MNSP1 Import | F_Q++LDMU_L6 | 1.1667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N>>N-NIL__S | 1.1667 | 0.83333 | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL
N-Q-MNSP1 Import | QNTE_ZERO | 0.91667 | 3 | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW | Outage
N-Q-MNSP1 Import | F_Q++LDMU_L5 | 0.58333 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | #R015365_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R015831_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R015839_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 15/06/2017, Version: 1 | Other
N-Q-MNSP1 Import | #R015956_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016632_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016642_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | N>>N-NIL_64 | 0.33333 | 0.58333 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
N-Q-MNSP1 Import | #R015839_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 15/06/2017, Version: 1 | Other
N-Q-MNSP1 Import | #R016642_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R015365_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R015105_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R015831_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R015956_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016358_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_ARDM_A, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016383_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_ARDM_A, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016573_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_ARDM_A, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 148.0833 | 572 | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator | NIL
NSW1-QLD1 Export | N^Q_NIL_A | 30 | 79.25 | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL
NSW1-QLD1 Export | N>>N-NIL__3_OPENED | 21.1667 | 60 | Out = Nil, avoid overloading Liddell to Muswellbrook (83) 330kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL
NSW1-QLD1 Export | N>>Q_LDMU_B | 13.1667 | 0 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage
NSW1-QLD1 Export | F_Q++ARDM_R6 | 11.5833 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_NIL_A | 11.25 | 0 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
NSW1-QLD1 Export | N^^Q_LS_VC_B4 | 3.5833 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage
NSW1-QLD1 Export | N>>N-NIL__3_CLOSED | 2.6667 | 14.0833 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL
NSW1-QLD1 Export | N^^Q_AR_VC_B4 | 1 | 0 | Out= Armidale SVC, avoid Voltage Collapse on loss of Tarong North | Outage
NSW1-QLD1 Export | N^^Q_TW_330_BUS3_B1 | 1 | 0 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | NQ_000 | 0.91667 | 0 | NSW to Qld on QNI upper transfer limit of 0 MW | Outage
NSW1-QLD1 Export | N>>N-NIL__2_OPENED | 0.83333 | 0.75 | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
NSW1-QLD1 Export | N^^Q_LS_VC_B1 | 0.83333 | 4.4167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | #R015618_003_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint Q>>BCCP_CLWU_LCCP_2, Effective Date: 11/05/2017, Version: 1 | Other
NSW1-QLD1 Export | #R015742_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q>>BCCP_CLWU_LCCP_2, Effective Date: 11/05/2017, Version: 1 | Other
NSW1-QLD1 Export | #R015743_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q>>BCCP_CLWU_LCCP_2, Effective Date: 11/05/2017, Version: 1 | Other
NSW1-QLD1 Export | F_Q++LDTW_R6 | 0.41667 | 1.5833 | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
NSW1-QLD1 Export | #NSW1-QLD1_RAMP_E_F | 0.33333 | 0 | NSW1-QLD1 <= MAX(190, InitialFlow - 200) (Wt=35) | Other
NSW1-QLD1 Export | #R015743_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint Q>>BCCP_CLWU_LCCP_2, Effective Date: 11/05/2017, Version: 1 | Other
NSW1-QLD1 Export | #R016248_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^Q_AR_VC_B5, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Export | #R016288_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B4, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Export | Q>>BCRG_CLWU_BCCP | 0.25 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | #NSW1-QLD1_I_E | 0.16667 | 0 | NSW1-QLD1.ENERGY * -1 >= 100 (Wt = 0.0001) | Other
NSW1-QLD1 Export | #R015612_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q>>BCCP_CLWU_LCCP_2, Effective Date: 11/05/2017, Version: 1 | Other
NSW1-QLD1 Export | #R015523_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R016303_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B2, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Export | #R016303_007_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B6, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Export | F_Q++ARDM_R5 | 0.083333 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | F_Q++ARDM_R60 | 0.083333 | 0 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N::Q_LDNC_TNT | 0.083333 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage
NSW1-QLD1 Import | Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 516.3333 | 0 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL
NSW1-QLD1 Import | F_Q++ARDM_L6 | 62 | 0.083333 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage
NSW1-QLD1 Import | Q:N_NIL_BI_POT | 48.9167 | 0 | Out = Nil, avoid transient instability for a trip of a Boyne Island potline (400 MW) For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_OSC or Q:N_NIL_BCK2L-G will bind. | NIL
NSW1-QLD1 Import | F_Q++ARTW_L6 | 45.9167 | 6.75 | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
NSW1-QLD1 Import | F_Q++ARDM_L5 | 44.9167 | 0 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage
NSW1-QLD1 Import | F_Q++MUTW_L6 | 27 | 5 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | Q:N_AR_CP2_AR_2L-G | 26 | 6.5 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++LDTW_L6 | 23 | 0.91667 | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
NSW1-QLD1 Import | Q:N_NIL_OSC | 19.4167 | 0 | Out = Nil, Queensland to NSW oscillatory stability limit | NIL
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 18.8333 | 7 | Negative Residue Management constraint equation for QLD to NSW flow | NIL
NSW1-QLD1 Import | F_Q++ARTW_L5 | 16.8333 | 4.9167 | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 11.5 | 0.83333 | NSW1-QLD1 >= MIN(-207, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Import | F_Q++MUTW_L5 | 11 | 2.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++LDTW_L5 | 9.1667 | 0.16667 | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
NSW1-QLD1 Import | Q:N_BI_POT_WIV_N-2 | 8.1667 | 0 | Out= Nil, limit Qld to NSW on QNI to avoid transient instability on trip of both Wivenhoe pumps | Outage
NSW1-QLD1 Import | Q:N_TW330_CB5102_OSC | 8 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage
NSW1-QLD1 Import | Q:N_ARSVC_AR_2L-G | 6.1667 | 0.58333 | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++LDMU_L6 | 3.3333 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++LDMU_L5 | 1.4167 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | N>>N-NIL__S | 1.1667 | 1.0833 | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL
NSW1-QLD1 Import | #R015465_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q:N_TW330_CB5102_OSC, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R015704_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint QN_850, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | #R016386_013_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint Q:N_ARSVC_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | #R016386_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q:N_ARSVC_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | #R015383_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint Q:N_LDTW_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | #R015704_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint QN_850, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | F_Q++ARDM_L60 | 0.33333 | 0 | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 60 second requirement | Outage
NSW1-QLD1 Import | N>>N-NIL_64 | 0.33333 | 0.66667 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
NSW1-QLD1 Import | #R015345_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q:N_MUTW_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | #R015368_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q:N_LDTW_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | #R015465_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint Q:N_TW330_CB5102_OSC, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R016003_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q:N_LDMU_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | F_Q++NIL_R5 | 0.16667 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | Q:N_AR_CP2_BI_POT | 0.16667 | 0 | Out = Armidale capacitor bank (120MVAr), Qld to NSW on QNI Transient Stability Limit, Loss of Boyne Island 375MW potline, 1 or 2 Millmerran units I/S | Outage
NSW1-QLD1 Import | #R015072_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_Q4, Effective Date: 08/04/2016, Version: 2 | Other
NSW1-QLD1 Import | #R015078_017_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_LTWG_Q4, Effective Date: 24/11/2016, Version: 1 | Other
NSW1-QLD1 Import | #R015329_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_MUTW_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Other
NSW1-QLD1 Import | #R016101_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_ARTW_BI_POT, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R016358_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_ARDM_A, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R016383_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_ARDM_A, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R016573_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_ARDM_A, Effective Date: 21/08/2013, Version: 1 | Other
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 625.9167 | 148.8333 | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 575 | 59.3333 | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 470.3333 | 173.5 | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 287.5833 | 814 | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 45.6667 | 26.9167 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | V>>V_NIL_2_TIE | 41.8333 | 0 | Out = Nil, avoid pre-contingent O/L of the South Morang F2 500/330 kV transformer, Yallourn unit 1 in 220kV mode, all 220kV buses tied at Hazelwood, feedback | NIL
T-V-MNSP1 Export | V>>V_KTS_TX_A3_2A_R | 23 | 3.25 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 22.1667 | 14.75 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_MAIN++NIL_BL_R60 | 19.1667 | 0.5 | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL
T-V-MNSP1 Export | T^V_NIL_11 | 18.6667 | 1.4167 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL
T-V-MNSP1 Export | TV_525 | 18.0833 | 0 | Tas to Vic on Basslink upper limit of 525 MW | Outage
T-V-MNSP1 Export | TVBL_ROC | 12.4167 | 3.0833 | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL
T-V-MNSP1 Export | F_T++LREG_0050 | 10.8333 | 5 | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_RREG | 10.4167 | 0.75 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | T^V_NIL_BL_6 | 9.3333 | 4.5 | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 9 | 49.1667 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A3_2_P | 4.5 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, all HWPS 220kV bus tied, feedback | Outage
T-V-MNSP1 Export | T_V_NIL_FCSPS | 4.4167 | 0.33333 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL
T-V-MNSP1 Export | T::T_HA_GT_PM_5 | 3.9167 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT in service. | Outage
T-V-MNSP1 Export | F_T++NIL_ML_L5 | 3.25 | 4.5 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | T_V_NIL_BL1 | 3.25 | 1.6667 | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL
T-V-MNSP1 Export | F_T++COGT_TL_L6 | 2.75 | 2.25 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | T^V_NIL_8 | 2.1667 | 0.83333 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | V>>V_ROTS_TX_2A_R | 2.0833 | 47 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | V>>V_MLSY_KTSBP_1AR | 1.8333 | 27.3333 | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage
T-V-MNSP1 Export | TV_550 | 0.91667 | 0 | Tas to Vic on Basslink upper limit of 550 MW | Outage
T-V-MNSP1 Export | #R015307_001_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
T-V-MNSP1 Export | T^V_NIL_9 | 0.75 | 21.0833 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | F_MAIN++RREG_0400 | 0.58333 | 0 | Mainland Raise Regulation Requirement greater than 400 MW, Basslink able transfer FCAS | Other
T-V-MNSP1 Export | #R015110_010_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Other
T-V-MNSP1 Export | #R015300_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
T-V-MNSP1 Export | #R015300_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
T-V-MNSP1 Export | TV_560 | 0.16667 | 0 | Tas to Vic on Basslink upper limit of 560 MW | Outage
T-V-MNSP1 Export | TV_575 | 0.16667 | 0 | Tas to Vic on Basslink upper limit of 575 MW | Outage
T-V-MNSP1 Export | #R015099_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
T-V-MNSP1 Export | #R015123_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 22/08/2016, Version: 1 | Other
T-V-MNSP1 Export | #R015141_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 11/10/2016, Version: 1 | Other
T-V-MNSP1 Export | #R016252_051_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 31/10/2016, Version: 1 | Other
T-V-MNSP1 Export | F_T++COGT_TL_L60 | 0.083333 | 2.25 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_T++NIL_BLSPS_L5 | 0.083333 | 0 | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
T-V-MNSP1 Export | T^^V_GTSH_1 | 0.083333 | 2.5 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 638.5833 | 458.0833 | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 328.5833 | 63 | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_NILxxx | 279.3333 | 618.5 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 276.6667 | 43.4167 | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 265.75 | 18.0833 | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 262.0833 | 56 | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V_T_NIL_FCSPS | 171.0833 | 43.4167 | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) | NIL
T-V-MNSP1 Import | V::N_SMF2_V2 | 170.8333 | 1.1667 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++LREG_0120 | 131.8333 | 3.0833 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V_T_NIL_BL1 | 118.1667 | 11.9167 | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 97.5833 | 3.0833 | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R60 | 90.0833 | 6.8333 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++RREG_0050 | 86.1667 | 17.6667 | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R6 | 72.0833 | 6.0833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 46.0833 | 13.9167 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 37.0833 | 12.8333 | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | T_ROCOF_1 | 33.4167 | 0 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 23.4167 | 66.5 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R5 | 23.25 | 5.8333 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 20.75 | 30.5833 | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 13.8333 | 34.6667 | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 12.8333 | 18.8333 | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | VTBL_ROC | 12.5833 | 4.3333 | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL
T-V-MNSP1 Import | T::T_NIL_4 | 12.1667 | 7.75 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL
T-V-MNSP1 Import | V::N_HWSM_S1 | 9.25 | 5.25 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
T-V-MNSP1 Import | T::T_NIL_3 | 8.75 | 0 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. Swamped if Tamar CCGT OOS. | NIL
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_V4 | 7.9167 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_SMF2_SD2 | 7.5833 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L5_APD | 6.5 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 4.5833 | 68.4167 | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_HWSM_V2 | 4.5 | 19.5 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_SMF2_S1 | 4.4167 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_LTWG_V4 | 3.6667 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V>>V_HWYP1_3_TIE | 3.1667 | 0 | Out= Hazelwood to Yallourn No.1 220kV line, avoid O/L Yallourn to Hazelwood No.2 220kV line on trip of Yallourn to Rowville No.7 or No.8 220kV line, all 220kV buses tied at Hazelwood, Feedback | Outage
T-V-MNSP1 Import | V::N_DDSM_V2 | 3 | 12.5833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | T::T_NIL_2 | 2.5 | 11.75 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL
T-V-MNSP1 Import | F_MAIN++ML_L60_APD | 2.4167 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | T::T_HA_GT_PM_4 | 2.3333 | 0.16667 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Import | VT_ZERO | 2.25 | 628 | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 2.0833 | 0.16667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R6 | 2 | 2.9167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_HWSM_SD | 2 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 1.75 | 1.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 1.5833 | 0.083333 | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T::T_HA_GT_PM_3 | 1.4167 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. | Outage
T-V-MNSP1 Import | V::N_X_MLSM_EMTT_V2 | 1.4167 | 0.5 | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_KTSY_MLSM_ET_V2 | 1.3333 | 1.75 | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_KTSY_V2 | 1.0833 | 1.5 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++BB_N-2_TG_R60 | 0.91667 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_X_HWSM_SMF2_S1 | 0.83333 | 0 | Out= Hazelwood-South Morang 500kV line & South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
T-V-MNSP1 Import | V::N_SMF2_S2 | 0.66667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HORC_V2 | 0.58333 | 0.25 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HWSM_Q2 | 0.58333 | 0.083333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for trip HWTS-SMTS 500kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
T-V-MNSP1 Import | #R015063_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015074_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015078_025_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_LTWG_V4, Effective Date: 24/11/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015250_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Other
T-V-MNSP1 Import | #R016273_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R60 | 0.41667 | 0.16667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_HWCB_S2 | 0.41667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_KGRC_V2 | 0.41667 | 1.9167 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R015072_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015174_006_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SMF2_S1, Effective Date: 10/02/2017, Version: 1 | Other
T-V-MNSP1 Import | #R015217_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
T-V-MNSP1 Import | #R015247_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015295_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 07/03/2017, Version: 1 | Other
T-V-MNSP1 Import | #R015311_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 22/02/2017, Version: 1 | Other
T-V-MNSP1 Import | #R015943_008_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #T-V-MNSP1_RAMP_E_F | 0.33333 | 0 | T-V-MNSP1 >= MIN(0, InitialFlow + 200) (Wt=35) | Other
T-V-MNSP1 Import | V::N_EPMB_V4 | 0.33333 | 6.8333 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | #R015110_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
T-V-MNSP1 Import | #R015248_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015943_008_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R015972_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | T>>T_GTHA_EXP_3H | 0.25 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
T-V-MNSP1 Import | V::N_DDSM_S2 | 0.25 | 0.083333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_SMF2_SD1 | 0.25 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | #R015106_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V4, Effective Date: 24/11/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015174_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SMF2_S1, Effective Date: 10/02/2017, Version: 1 | Other
T-V-MNSP1 Import | #R015311_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 22/02/2017, Version: 1 | Other
T-V-MNSP1 Import | #R016123_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BAWB_S2, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R016273_008_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++LREG_0400 | 0.16667 | 2.3333 | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Other
T-V-MNSP1 Import | F_T++BB_N-2_TG_R6 | 0.16667 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R6 | 0.16667 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R5 | 0.16667 | 1.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_SMSC_S2 | 0.16667 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_X_HWSM_ROSM_V2 | 0.16667 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R015066_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015160_007_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 10/01/2017, Version: 1 | Other
T-V-MNSP1 Import | #R015247_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
T-V-MNSP1 Import | #R015562_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++APD_TL_L6 | 0.083333 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R5 | 0.083333 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_6E | 0.083333 | 65.75 | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL
T-V-MNSP1 Import | V::N_KTSY_SD | 0.083333 | 1.0833 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | N^^V_NIL_1 | 1342.5 | 68.8333 | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL
V-S-MNSP1 Export | V::N_NILxxx | 560.25 | 807.8333 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 272.1667 | 879.0833 | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
V-S-MNSP1 Export | V::N_SMF2_V2 | 174 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V^SML_NSWRB_2 | 53 | 153.9167 | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line | NIL
V-S-MNSP1 Export | V>>V_NIL_2_TIE | 42.0833 | 0 | Out = Nil, avoid pre-contingent O/L of the South Morang F2 500/330 kV transformer, Yallourn unit 1 in 220kV mode, all 220kV buses tied at Hazelwood, feedback | NIL
V-S-MNSP1 Export | N^^V_DDMSX5_1 | 29.4167 | 0 | Out = Dederang - Murray (67 or 68) and Darlington Pt - Buronga (X5) lines, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
V-S-MNSP1 Export | V>>V_SMTXF2_6 | 27.5833 | 1.75 | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage
V-S-MNSP1 Export | V::N_HWSM_S1 | 26 | 6.0833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-S-MNSP1 Export | VSML_220 | 22.1667 | 467.4167 | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL
V-S-MNSP1 Export | V>>V_NIL_5 | 21.5 | 0.083333 | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL
V-S-MNSP1 Export | VSML_ZERO | 20.4167 | 299.9167 | Victoria to South Australia on Murraylink upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | VSML_ROC_80 | 20.1667 | 27.1667 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Export | N^^V_MSUT_1 | 20.0833 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage
V-S-MNSP1 Export | V::N_HWSM_V2 | 18.5 | 18.0833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | N^^V_DDWG | 14.75 | 0 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V4 | 14.25 | 1.0833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | N^^V_SMTXH1_1 | 14.1667 | 0 | Out = South Morang H1 or H2 500/330 kV txfmr, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
V-S-MNSP1 Export | N^^V_DDSM1 | 12.5 | 3.5 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Export | V>>N-NIL_HA | 11.3333 | 280.3333 | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | NIL
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 8 | 50.0833 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-S-MNSP1 Export | V::N_SMF2_SD2 | 7.75 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_SMF2_S1 | 7.3333 | 0 | Out= Hazelwood-South Morang 500kV line & South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-S-MNSP1 Export | V::N_KTSY_V2 | 6.4167 | 0.83333 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_SMF2_S1 | 6.4167 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_LTWG_V4 | 5.0833 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_DDSM_V2 | 4.5833 | 10.5833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HWSM_SD | 3.25 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | N^^V_EPMB_1 | 3.1667 | 0.91667 | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
V-S-MNSP1 Export | V>SML_BUDP_2 | 3.0833 | 25.1667 | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage
V-S-MNSP1 Export | V::N_KTSY_MLSM_ET_V2 | 3 | 0.25 | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_HWRO_V2 | 3 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>BLMK_BWPA_BRTW | 2.9167 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_X_MLSM_EMTT_V2 | 2.8333 | 0.5 | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | N^^V_LTWG | 2.4167 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse in Southern NSW for either loss of the largest VIC generating unit or Basslink, or loss of a Murray to Dederang 330 kV line | Outage
V-S-MNSP1 Export | V>SML_NSWRB_10 | 2.3333 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL
V-S-MNSP1 Export | NRM_VIC1_SA1 | 2.0833 | 26.75 | Negative Residue Management constraint for VIC to SA flow | NIL
V-S-MNSP1 Export | V>>SML_NIL_8 | 1.9167 | 0.25 | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line | NIL
V-S-MNSP1 Export | N^^V_LTMS | 1.8333 | 0 | Out = Lower Tumut to Murray 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
V-S-MNSP1 Export | V:SS_820_HY_TEST_DYN | 1.75 | 5.8333 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-S-MNSP1 Export | V^SML_BAWB_3 | 1.75 | 0 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | VSML_-100 | 1.6667 | 0 | Vic to SA on ML upper transfer limit of -100 MW | Outage
V-S-MNSP1 Export | V::N_HWCB_S2 | 1.5 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-LTUT_B | 1.5 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage
V-S-MNSP1 Export | V>>DDSH_DDGN_N-2 | 1.3333 | 0.66667 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
V-S-MNSP1 Export | V>>SML_NIL_1 | 1.3333 | 0.16667 | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line | NIL
V-S-MNSP1 Export | V::N_KTSY_S2 | 1.1667 | 2.6667 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>NWBCB6225_TX1 | 1 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 132/66kV TX1 on trip of Monash-North West Bend #2 132kV line, Feedback | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WEWT | 0.75 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>N-LTUT_2_30 | 0.75 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L using 30 mins rating on Murray to Upper Tumut(65) trip; Feedback | Outage
V-S-MNSP1 Export | #R015063_012_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015074_012_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | V::N_KTSY_SD | 0.66667 | 1.0833 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V::N_SMF2_S2 | 0.66667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | #R015072_012_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R016565_003_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | V::N_EPMB_V4 | 0.58333 | 6.8333 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HORC_V2 | 0.58333 | 0.083333 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HWSM_Q2 | 0.58333 | 0.083333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for trip HWTS-SMTS 500kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
V-S-MNSP1 Export | V::N_MLTR_V2 | 0.5 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_ROSM_V2 | 0.5 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-NIL_HG | 0.5 | 1.5 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | V>>V_NIL_8 | 0.5 | 1.4167 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL
V-S-MNSP1 Export | VSML_-050 | 0.5 | 0 | Vic to SA on ML upper transfer limit of -50 MW | Outage
V-S-MNSP1 Export | #R015063_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015074_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015078_025_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_LTWG_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015247_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015250_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015355_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015386_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015553_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R015782_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016125_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_BAWB_3, Effective Date: 20/07/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016128_013_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_LTWG, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016273_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016579_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016600_011_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016639_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | V::N_KGRC_V2 | 0.41667 | 1.6667 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>SML_BESH_2 | 0.41667 | 0 | Out = Bendigo to Shepparton 220 kV line, avoid O/L Darlington Pt to Balranald to Buronga (X5/1 & X5/3) 220kV line on loss of Ballarat to Bendigo 220kV line, feedback | Outage
V-S-MNSP1 Export | V>NWCB6024+25_TX1 | 0.41667 | 0 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #1 132/66kV TX on trip of Monash-North West Bend #1 132kV line (this splits NWB 132kV bus), Feedback | Outage
V-S-MNSP1 Export | #R015066_012_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015066_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015072_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015160_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015174_006_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SMF2_S1, Effective Date: 10/02/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015185_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V2_R, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015217_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015247_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015295_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 07/03/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015311_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 22/02/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015348_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015590_013_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R015770_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R015870_018_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R015943_008_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015972_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016097_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R016273_008_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016472_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016609_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 0.33333 | 5.0833 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | VSML_-040 | 0.33333 | 0 | Vic to SA on ML upper transfer limit of -40 MW | Outage
V-S-MNSP1 Export | V^SML_HORC_3 | 0.33333 | 0 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | #R015078_025_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_LTWG_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015110_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015160_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015217_005_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015248_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015553_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R015870_018_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R015943_008_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016097_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R016123_013_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_BAWB_3, Effective Date: 20/07/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016518_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016600_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016609_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | V::N_DDSM_S2 | 0.25 | 0.083333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_SMF2_SD1 | 0.25 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | VSML_-080 | 0.25 | 0 | Vic to SA on ML upper transfer limit of -80 MW | Outage
V-S-MNSP1 Export | #R015106_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015110_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015174_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SMF2_S1, Effective Date: 10/02/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015185_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_V2_R, Effective Date: 24/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015250_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015311_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 22/02/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015386_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015562_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015770_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016123_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BAWB_S2, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016125_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_BAWB_3, Effective Date: 20/07/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016472_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016579_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016639_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | S>>DVBL_LKDV_WEWT | 0.16667 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East- Waterloo 132kV on trip of Mt Lock-Davenport 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_SMSC_S2 | 0.16667 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-LTUT_G | 0.16667 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage
V-S-MNSP1 Export | V>>V_DDSM_1 | 0.16667 | 17.9167 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
V-S-MNSP1 Export | V>>V_LTMS_1 | 0.16667 | 0 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage
V-S-MNSP1 Export | #R015141_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 11/10/2016, Version: 1 | Other
V-S-MNSP1 Export | #R015348_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
V-S-MNSP1 Export | #R015562_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016525_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | #R016525_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 07/08/2015, Version: 1 | Other
V-S-MNSP1 Export | V::N_HYMO_V2 | 0.083333 | 0.5 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-LTUT_A | 0.083333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage
V-S-MNSP1 Export | V>>V_BAEL_1 | 0.083333 | 0 | Out = Ballarat to Elaine 220 kV line section, avoid O/L Moorabool to Ballarat No. 1 220 kV line on trip of Moorabool to Terang 220 kV line, feedback | Outage
V-S-MNSP1 Export | V>X_NWCB6225+6021_T1 | 0.083333 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225, avoid overloading North West Bend 132/66 kV #1 transformer on trip of North West Bend to Morgan Whyalla pump 1 132 kV line | Outage
V-S-MNSP1 Export | VSML_VFRB_OFF | 0.083333 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL
V-S-MNSP1 Import | S>V_NIL_NIL_RBNW | 282.4167 | 585.8333 | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips | NIL
V-S-MNSP1 Import | SVML_ZERO | 80.3333 | 159.0833 | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage
V-S-MNSP1 Import | S>NWBCB6225_TX1 | 40.8333 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 66/132kV TX1 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage
V-S-MNSP1 Import | S>NIL_NIL_NWMH2 | 37 | 36 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL
V-S-MNSP1 Import | SVML_ROC_80 | 21.6667 | 33.9167 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Import | S>NWCB6024+25_TX3 | 18.25 | 4.3333 | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage
V-S-MNSP1 Import | S>V_NWRB_RBMWP3 | 17.4167 | 0 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage
V-S-MNSP1 Import | S>>BLMK_CNRB_WEMWP4 | 16.5 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV on trip of Canowi-Robertstown 275kV line(this trips Hallet wind farm and Hallet GT, and offloads Davenport-Canowie 275kV line), Feedback | Outage
V-S-MNSP1 Import | S>RB_275KV_S_BUS_9 | 14 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage
V-S-MNSP1 Import | S>V_CB6033+6225_TX2 | 10.4167 | 4.6667 | Out= North West Bend_CB6033 and CB6225; avoid O/L of North West Bend transformer 132/66kV #2 on trip of either Robertstown-NWB #2 132kV line or NWB-Monash #2 132kV line . | Outage
V-S-MNSP1 Import | S>>X_MKRB+6573+74_1 | 10.25 | 0 | Out= Mokota-Robertstown 275kV line AND Robertstown CB6573 and CB6574, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Robt 275/132kV TX1, and Dav-Can 275kV line and trips Hallet GT & WF), Feedback | Outage
V-S-MNSP1 Import | S>RB_275KV_N_BUS_1 | 7.75 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage
V-S-MNSP1 Import | S:VS_650_HY_TEST_DYN | 6.9167 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-S-MNSP1 Import | S:VS_650_HY_TEST | 4.0833 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-S-MNSP1 Import | S>X_NWCB6225+6021_T1 | 3.5833 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225 (which also causes an outage of North West Bend to Monash #1 132 kV line), avoid overloading North West Bend 132/66 kV #1 transformer on trip of North West Bend to Morgan Whyalla pump 1 132 kV line | Outage
V-S-MNSP1 Import | S>>X_CNRB+CB_02 | 3.0833 | 0 | Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line(this offloads Robertstown #1 275/132kV TX and Trips Hallet Hill WF) | Outage
V-S-MNSP1 Import | V>>V_MLSY_KTSBP_1AR | 1.8333 | 27 | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage
V-S-MNSP1 Import | S:V_420 | 1.4167 | 0 | South Australia to Victoria on both Heywood and Murraylink maximum transfer limit to avoid oscillatory instability This constraint equation was added, in January 2011, to a number of outage constraint sets across the NEM (except for Tasmania). The 420 MW value is the previous system normal limit. Throughout 2011 AEMO conducted studies as to whether the 420 MW limit was appropriate for various outages. In some cases the limit was increased. This work will continue in 2012. | Outage
V-S-MNSP1 Import | S>>CNLK_MKRB_WEMWP4 | 1.25 | 0 | Out= Canowie-Mt Lock 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV on trip of Mokota-Robertstown 275kV line( this offloads Belalie-Mokota 275kV line and trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | NRM_SA1_VIC1 | 1.1667 | 7.3333 | Negative Residue Management constraint for SA to VIC flow | NIL
V-S-MNSP1 Import | S>>CNRB_MKRB_WEMWP4 | 1.0833 | 13.6667 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | V>>V_NIL_1B | 1.0833 | 1.4167 | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL
V-S-MNSP1 Import | S>>BLMK_NIL_WEMWP4 | 0.5 | 0 | Out= Belalie-Mokota 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on Nil trip, Feedback | NIL
V-S-MNSP1 Import | #R015110_010_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Other
V-S-MNSP1 Import | #R015330_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R015662_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R015662_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016029_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016215_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>V_CB6033+6225_TX2, Effective Date: 21/07/2015, Version: 1 | Other
V-S-MNSP1 Import | #R016216_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>V_CB6033+6225_TX2, Effective Date: 21/07/2015, Version: 1 | Other
V-S-MNSP1 Import | #R016228_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>V_CB6033+6225_TX2, Effective Date: 21/07/2015, Version: 1 | Other
V-S-MNSP1 Import | #R016456_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016587_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | CA_MQS_48D013FF_01 | 0.41667 | 0 | Constraint Automation, O/L ROBMW4_2 @MW_4 for CTG LSII on trip of BELALI-MOKOTA 275KV LINE. Generated by STNET[MANBL] Host MANEEMP1(MQ) | Outage
V-S-MNSP1 Import | #R016119_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016225_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint S>X_NWCB6225+6021_T1, Effective Date: 13/07/2015, Version: 1 | Other
V-S-MNSP1 Import | S:V_580 | 0.33333 | 0 | Out = One Heywood 500/275 kV txfmr (two remain in service), maintain maximum SA to VIC transfer limit of 580 MW on Heywood and Murraylink combined to avoid oscillatory instability | Outage
V-S-MNSP1 Import | V>>V_NIL_1A | 0.33333 | 1 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL
V-S-MNSP1 Import | #R015863_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016029_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016214_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S>NWBCB6225_TX1, Effective Date: 02/08/2017, Version: 1 | Other
V-S-MNSP1 Import | #R015789_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016119_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016214_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>NWBCB6225_TX1, Effective Date: 02/08/2017, Version: 1 | Other
V-S-MNSP1 Import | #R016228_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>V_CB6033+6225_TX2, Effective Date: 21/07/2015, Version: 1 | Other
V-S-MNSP1 Import | #R016456_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016587_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | S>V_NWRB2_RBNW1 | 0.16667 | 35 | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage
V-S-MNSP1 Import | #R015789_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016216_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>V_CB6033+6225_TX2, Effective Date: 21/07/2015, Version: 1 | Other
V-S-MNSP1 Import | #R016502_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S:V_580, Effective Date: 25/11/2016, Version: 1 | Other
V-S-MNSP1 Import | I_CTRL_ISSUE_ML | 0.083333 | 1.0833 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Import | S>>NIL_CNRB_WEMWP4 | 0.083333 | 0 | Out= Nil, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line (this offloads Mt Lock-Canowie 275kV line and trips Hallet WF and GTs), Feedback | NIL
V-SA Export | V::N_NILxxx | 453.4167 | 574.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-SA Export | V::N_SMF2_V2 | 175.6667 | 1.25 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V_S_NIL_ROCOF | 133.3333 | 391.9167 | Out = Nil, limit Victoria to SA on Heywood flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL
V-SA Export | V:S_600_HY_TEST_DYN | 97.5833 | 76.25 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-SA Export | V:S_600_HY_TEST | 75.3333 | 47.75 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL
V-SA Export | VS_050 | 57.5833 | 0 | Victoria to South Australia on Heywood upper transfer limit of 50 MW | Outage
V-SA Export | V::S_SETB_TBSE_2 | 44.5833 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V::N_HWSM_V2 | 18.5 | 8.4167 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_HWSM_S1 | 14.8333 | 0.083333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-SA Export | VS_250_DYN | 10.25 | 232.25 | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Export | V::N_BYPASS_HW_SY_V4 | 9.4167 | 1.0833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_SMF2_S1 | 5.9167 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V:S_ARDM_560 | 5.4167 | 0.91667 | Maintain maximum transfer limit of 560 MW on Heywood IC from VIC to SA to avoid oscillatory instability | Outage
V-SA Export | V::N_LTWG_V4 | 5 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | NRM_VIC1_SA1 | 4.75 | 26.75 | Negative Residue Management constraint for VIC to SA flow | NIL
V-SA Export | S>>NIL_TBTU_TBCG_1 | 4.6667 | 0 | Out=NIL, avoid O/L Tailem Bend-Cherry Gardens 275kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL
V-SA Export | V>S_460_DYN | 4.5833 | 5.8333 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Export | V::N_KTSY_V2 | 3.9167 | 1.0833 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | S>>NIL_SETB_SETB_1 | 3.6667 | 11 | Out= Nil, avoid O/L one South East-Tailem Bend 275kV on trip of other South East-Tailem Bend 275kV line, feedback | NIL
V-SA Export | V::N_HWSM_SD | 3.5833 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V>>V_HWYP1_3_TIE | 3.5833 | 0 | Out= Hazelwood to Yallourn No.1 220kV line, avoid O/L Yallourn to Hazelwood No.2 220kV line on trip of Yallourn to Rowville No.7 or No.8 220kV line, all 220kV buses tied at Hazelwood, Feedback | Outage
V-SA Export | V>S_460 | 3.0833 | 3.3333 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage
V-SA Export | V::S_NIL_MAXG_xxx | 3.0833 | 366.25 | Out = Nil, avoid transient instability for trip of the largest generation unit in South Australia | NIL
V-SA Export | V::S_PP+TIPSB_MG | 3.0833 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of half of Pelican Point PS(GT11 + ST18) + largest TIPS B unit declared as credible (South East Capacitor Available). | Outage
V-SA Export | V::S_PP+TIPSB_MG_2 | 3.0833 | 0 | Out =Nil(Note: with both Black Range series capacitors O/S); Vic-SA Tran. Stab limit for loss of SA largest generator with loss of half of Pelican Point PS (GT1 + ST) and largest TIPS B unit declared as credible (South East Capacitor Available). | Outage
V-SA Export | V::N_KTSY_MLSM_ET_V2 | 3 | 0.33333 | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_X_HWSM_HWRO_V2 | 3 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | S>>NIL_TBCG_TBTU_1 | 2.25 | 34.6667 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL
V-SA Export | V::N_X_HWSM_SMF2_S1 | 2.25 | 0 | Out= Hazelwood-South Morang 500kV line & South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-SA Export | V^^S_SETB_TBSE_2 | 2.0833 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V::N_X_MLSM_EMTT_V2 | 2 | 0.33333 | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_NIL_TBSE_1 | 1.6667 | 2.75 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Export | V::N_HWCB_S2 | 1.5 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V:S_MSUT_560 | 1.5 | 0.66667 | Out = Murray - Upper Tumut (65) 330kV line, VIC to SA on Heywood upper transfer limit of 560 MW based on oscillatory stability. | Outage
V-SA Export | V^^S_BLKRG_TBSE_2 | 1.5 | 8.75 | Out = both or one Black Range series capacitors O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | V>>DDSH_DDGN_N-2 | 1.3333 | 0.66667 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
V-SA Export | V::N_KTSY_S2 | 0.91667 | 2.5833 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V_S_ROCOF | 0.75 | 31.75 | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage
V-SA Export | S>>KHKN_SETB_SETB | 0.66667 | 0 | Out= Keith-Kincraig 132 kV line (Note: with both Black Range series caps I/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage
V-SA Export | V::N_SMF2_S2 | 0.66667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_HORC_V2 | 0.58333 | 0.083333 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_HWSM_Q2 | 0.58333 | 0.083333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for trip HWTS-SMTS 500kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
V-SA Export | V::N_KTSY_SD | 0.58333 | 1 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | #R015074_012_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | S>>NIL_TBTU_TBMO_1 | 0.5 | 4.1667 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL
V-SA Export | V::N_MLTR_V2 | 0.5 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_X_HWSM_ROSM_V2 | 0.5 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_BLKRG_TBSE_2 | 0.5 | 44.9167 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | #R015063_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015074_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015078_025_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_LTWG_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015118_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Export | #R015212_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 14/02/2017, Version: 1 | Other
V-SA Export | #R015247_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
V-SA Export | #R015250_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Other
V-SA Export | #R015318_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R016085_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R016273_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R016298_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | V::N_KGRC_V2 | 0.41667 | 0.25 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_NIL_SETB_SECP_1 | 0.41667 | 0.33333 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | VS_500 | 0.41667 | 0 | VIC to SA on Heywood upper transfer limit of 500 MW | Outage
V-SA Export | V^^S_NIL_MAXG_xxx | 0.41667 | 0 | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off | NIL
V-SA Export | #R015066_012_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015066_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015072_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015160_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-SA Export | #R015174_006_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SMF2_S1, Effective Date: 10/02/2017, Version: 1 | Other
V-SA Export | #R015185_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V2_R, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015217_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-SA Export | #R015247_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
V-SA Export | #R015286_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015295_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 07/03/2017, Version: 1 | Other
V-SA Export | #R015311_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 22/02/2017, Version: 1 | Other
V-SA Export | #R015318_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015374_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015374_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015943_008_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R015972_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R016085_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R016273_008_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R015078_025_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_LTWG_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015110_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-SA Export | #R015160_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-SA Export | #R015248_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
V-SA Export | #R015943_008_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #V-SA_RAMP_E_F | 0.25 | 0 | V-SA <= MAX(50, InitialFlow - 30) (Wt=35) | Other
V-SA Export | F_ESTN++MLMO_L60 | 0.25 | 2.1667 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::N_SMSC_S2 | 0.25 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | #R015106_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015110_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-SA Export | #R015174_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SMF2_S1, Effective Date: 10/02/2017, Version: 1 | Other
V-SA Export | #R015217_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
V-SA Export | #R015282_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015286_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015298_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015562_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R015770_020_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V:S_MSUT_560, Effective Date: 06/09/2016, Version: 1 | Other
V-SA Export | #R016123_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BAWB_S2, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | V::S_NIL_SETB_SECP_2 | 0.16667 | 0.75 | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | V^^S_KHKN_SETB | 0.16667 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage
V-SA Export | V^^S_NIL_SETB_SECP_1 | 0.16667 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Long Term Voltage Stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | #R015063_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
V-SA Export | #R015118_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Export | #R015236_013_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V:S_ARDM_560, Effective Date: 03/02/2016, Version: 1 | Other
V-SA Export | #R015298_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015313_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015313_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R015562_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | CA_MQS_4780983C_01 | 0.083333 | 0 | Constraint Automation, O/L TABSES_2 @S_EAST for CTG LSIC on trip of T_BEND-S_EAST 275KV 1 LINE. Generated by STNET[MANBL] Host MANEEMP2(MQ) | Outage
V-SA Export | V::N_HYMO_V2 | 0.083333 | 0.33333 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V^^S_NIL_TBSE_1 | 0.083333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 294.0833 | 945.25 | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
V-SA Import | S:V_500_HY_TEST_DYN | 64.5 | 0.16667 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | S:V_500_HY_TEST | 48.0833 | 0 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | V>>V_NIL_2_TIE | 40.5 | 0 | Out = Nil, avoid pre-contingent O/L of the South Morang F2 500/330 kV transformer, Yallourn unit 1 in 220kV mode, all 220kV buses tied at Hazelwood, feedback | NIL
V-SA Import | F_S++HYSE_L6_1 | 38.5 | 23.6667 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA lower 6 sec Requirement for risk of islanding, segment1 | Outage
V-SA Import | SV_250 | 28.75 | 0 | SA to Victoria on Heywood upper transfer limit of 250 MW | Outage
V-SA Import | V>>V_KTS_TX_A3_2A_R | 24.25 | 7.0833 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | F_S++HYSE_L60 | 23.0833 | 10.75 | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage
V-SA Import | V_ML_TRMO | 20.6667 | 0 | Out = Moorabool to Mortlake or Moorabool to Tarrone 500 kV line, limit nett loading to < 50 MW on the remaining 500 kV line into Moorabool. | Outage
V-SA Import | S_V_NIL_ROCOF | 9.5 | 3.25 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL
V-SA Import | V>>V_KTS_TX_A2_2A_R | 9.0833 | 54 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | V::N_DDSM_V2 | 4.6667 | 10.25 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Import | V>>V_KTS_TX_A3_2_P | 3.3333 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, all HWPS 220kV bus tied, feedback | Outage
V-SA Import | S:VS_650_HY_TEST_DYN | 2.9167 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | V>>V_ROTS_TX_2A_R | 2.25 | 98 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
V-SA Import | S::V_TBSE_TBSE_1 | 2.1667 | 2.3333 | Out = one Tailembend-South East 275kV line (NOTE: with both Black Range series capacitors I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines | Outage
V-SA Import | V>>V_MLSY_KTSBP_1AR | 1.8333 | 28.0833 | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage
V-SA Import | S:V_420 | 1.4167 | 0 | South Australia to Victoria on both Heywood and Murraylink maximum transfer limit to avoid oscillatory instability | Outage
V-SA Import | NRM_SA1_VIC1 | 1.1667 | 6.0833 | Negative Residue Management constraint for SA to VIC flow | NIL
V-SA Import | S:VS_650_HY_TEST | 1.0833 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | #R015307_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
V-SA Import | #V-SA_RAMP_I_F | 0.58333 | 0.25 | V-SA >= MIN(-52, InitialFlow + 50) (Wt=35) | Other
V-SA Import | #R015110_010_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Other
V-SA Import | #R015300_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
V-SA Import | #R015323_006_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V_ML_TRMO, Effective Date: 20/03/2017, Version: 1 | Other
V-SA Import | #R015123_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 22/08/2016, Version: 1 | Other
V-SA Import | #R016315_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint SV_250_DYN, Effective Date: 17/08/2016, Version: 1 | Other
V-SA Import | #R016502_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>V_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Import | S>V_460_DYN | 0.25 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Import | #R015123_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 22/08/2016, Version: 1 | Other
V-SA Import | #R015300_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
V-SA Import | #R016502_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>V_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Import | #R015099_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
V-SA Import | #R015141_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 11/10/2016, Version: 1 | Other
VIC1-NSW1 Export | V::N_NILxxx | 581.4167 | 941.6667 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 285.75 | 957.0833 | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
VIC1-NSW1 Export | V::N_SMF2_V2 | 169.3333 | 1.9167 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_NIL_2_TIE | 42.0833 | 0 | Out = Nil, avoid pre-contingent O/L of the South Morang F2 500/330 kV transformer, Yallourn unit 1 in 220kV mode, all 220kV buses tied at Hazelwood, feedback | NIL
VIC1-NSW1 Export | V>>V_SMTXF2_6 | 27.9167 | 1.75 | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage
VIC1-NSW1 Export | V>>V_NIL_5 | 26.5833 | 0.41667 | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL
VIC1-NSW1 Export | V::N_HWSM_S1 | 26.5 | 8 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A3_2A_R | 24.0833 | 7 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | V::N_HWSM_V2 | 18.5 | 19.3333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V4 | 14.3333 | 1.0833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HA | 11.0833 | 312.75 | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | NIL
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2A_R | 8.25 | 54.3333 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | V::N_KTSY_V2 | 8.0833 | 1.5 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_SD2 | 7.75 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_X_HWSM_SMF2_S1 | 7.3333 | 0 | Out= Hazelwood-South Morang 500kV line & South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
VIC1-NSW1 Export | V::N_SMF2_S1 | 6.3333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_LTWG_V4 | 5.0833 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_DDSM_V2 | 4.6667 | 11.75 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A3_2_P | 4.5 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, all HWPS 220kV bus tied, feedback | Outage
VIC1-NSW1 Export | N>>N-NIL__B_15M | 4.1667 | 0.16667 | Out= Nil, avoid O/L Upper Tumut to Canberra (01) using 15 mins rating on trip of Lower Tumut to Canberra (07) line, Feedback | NIL
VIC1-NSW1 Export | VN_0850 | 3.9167 | 0.25 | Discretionary Vic to NSW transfer upper limit of 850 MW | Outage
VIC1-NSW1 Export | V::N_HWSM_SD | 3.25 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_X_HWSM_HWRO_V2 | 3 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_KTSY_MLSM_ET_V2 | 2.9167 | 1.75 | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_X_MLSM_EMTT_V2 | 2.75 | 0.5 | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_ROTS_TX_2A_R | 2.25 | 98.3333 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V>>V_MLSY_KTSBP_1AR | 1.8333 | 26.9167 | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage
VIC1-NSW1 Export | VN_0700 | 1.8333 | 0.41667 | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage
VIC1-NSW1 Export | V>>SML_NIL_8 | 1.75 | 0.25 | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line | NIL
VIC1-NSW1 Export | V::N_HWCB_S2 | 1.5 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-LTUT_B | 1.5 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage
VIC1-NSW1 Export | V>>SML_NIL_1 | 1.4167 | 0.16667 | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line | NIL
VIC1-NSW1 Export | V::N_KTSY_S2 | 1.0833 | 2.8333 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | NRM_VIC1_NSW1 | 0.91667 | 1.9167 | Negative Residue Management constraint equation for VIC to NSW flow | NIL
VIC1-NSW1 Export | #R015307_001_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL__S | 0.83333 | 0.5 | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL
VIC1-NSW1 Export | V::N_KTSY_SD | 0.83333 | 1 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V>>N-LTUT_2_30 | 0.75 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L using 30 mins rating on Murray to Upper Tumut(65) trip; Feedback | Outage
VIC1-NSW1 Export | #R015063_012_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015074_012_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | V::N_EPMB_V4 | 0.66667 | 6.75 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_S2 | 0.66667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | #R015072_012_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | V::N_HORC_V2 | 0.58333 | 0.25 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HG | 0.58333 | 2.8333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | V::N_HWSM_Q2 | 0.5 | 0.083333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for trip HWTS-SMTS 500kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_MLTR_V2 | 0.5 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_X_HWSM_ROSM_V2 | 0.5 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | #R015063_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015074_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015078_025_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_LTWG_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015247_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015250_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015300_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
VIC1-NSW1 Export | #R016273_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | V::N_KGRC_V2 | 0.41667 | 1.6667 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | #R015066_012_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015066_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015072_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015110_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015123_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 22/08/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015160_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 10/01/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015174_006_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SMF2_S1, Effective Date: 10/02/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015185_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V2_R, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015217_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015247_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015295_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 07/03/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015311_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 22/02/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015943_008_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015972_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R016273_008_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | V::N_HYMO_V2 | 0.33333 | 0.5 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_SD1 | 0.33333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | #R015078_025_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_LTWG_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015110_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015160_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 10/01/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015217_005_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015248_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HWCB_S2, Effective Date: 20/12/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015943_008_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | V::N_DDSM_S2 | 0.25 | 0.083333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | VN_0800 | 0.25 | 3.6667 | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage
VIC1-NSW1 Export | #R015106_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V4, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015110_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 10/01/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015123_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 22/08/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015174_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SMF2_S1, Effective Date: 10/02/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015185_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_V2_R, Effective Date: 24/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015250_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015300_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015311_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 22/02/2017, Version: 1 | Other
VIC1-NSW1 Export | #R015562_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R016123_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BAWB_S2, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_64 | 0.16667 | 0.33333 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
VIC1-NSW1 Export | V::N_SMSC_S2 | 0.16667 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-DPWG_X5_A | 0.16667 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Buronga (X5), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage
VIC1-NSW1 Export | V>>N-LTUT_G | 0.16667 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage
VIC1-NSW1 Export | V>>V_BAEL_1 | 0.16667 | 0 | Out = Ballarat to Elaine 220 kV line section, avoid O/L Moorabool to Ballarat No. 1 220 kV line on trip of Moorabool to Terang 220 kV line, feedback | Outage
VIC1-NSW1 Export | V>>V_DDSM_1 | 0.16667 | 20.1667 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
VIC1-NSW1 Export | V>>V_LTMS_1 | 0.16667 | 0 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage
VIC1-NSW1 Export | #R015099_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 07/12/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015141_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 11/10/2016, Version: 1 | Other
VIC1-NSW1 Export | #R015562_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_01N | 0.083333 | 3.4167 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL
VIC1-NSW1 Export | V>>N-LTUT_A | 0.083333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage
VIC1-NSW1 Export | V>>N-LTWG_RADIAL_1 | 0.083333 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Import | N^^V_NIL_1 | 1805.6667 | 81.8333 | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL
VIC1-NSW1 Import | N^^V_DDMSX5_1 | 29.25 | 0 | Out = Dederang - Murray (67 or 68) and Darlington Pt - Buronga (X5) lines, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_MSUT_1 | 20 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_DDWG | 14.5 | 0 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_SMTXH1_1 | 14.1667 | 3.25 | Out = South Morang H1 or H2 500/330 kV txfmr, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_DDSM1 | 11.9167 | 3.9167 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V-JNWG_RADIAL_1A | 5.25 | 6.8333 | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage
VIC1-NSW1 Import | N^^V_EPMB_1 | 3.1667 | 0.91667 | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_LTWG | 2.4167 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse in Southern NSW for either loss of the largest VIC generating unit or Basslink, or loss of a Murray to Dederang 330 kV line | Outage
VIC1-NSW1 Import | N^^V_LTMS | 1.8333 | 0 | Out = Lower Tumut to Murray 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | N::V_DDMS | 1.5 | 0 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage
VIC1-NSW1 Import | V>>DDSH_DDGN_N-2 | 1.25 | 0.66667 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
VIC1-NSW1 Import | #R015597_030_RAMP_F | 1.1667 | 0 | Hard Ramping constraint for constraint V>>V-JNWG_RADIAL_1A, Effective Date: 01/07/2016, Version: 1 | Other
VIC1-NSW1 Import | V>>V_NIL_1B | 1 | 1.75 | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line | NIL
VIC1-NSW1 Import | N^^V_DDSM2 | 0.75 | 3.25 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse for loss of remaining Dederang to South Morang 330 kV line | Outage
VIC1-NSW1 Import | #R015782_012_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^V_DDSM2, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016565_003_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R015355_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
VIC1-NSW1 Import | #R015386_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
VIC1-NSW1 Import | #R015553_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R015782_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016128_013_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_LTWG, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016579_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016600_011_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016639_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R015348_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
VIC1-NSW1 Import | #R015590_013_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R015770_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R015870_018_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016472_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016609_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R015553_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R015870_018_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016518_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016600_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016609_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | V>>SML_BESH_2 | 0.25 | 0 | Out = Bendigo to Shepparton 220 kV line, avoid O/L Darlington Pt to Balranald to Buronga (X5/1 & X5/3) 220kV line on loss of Ballarat to Bendigo 220kV line, feedback | Outage
VIC1-NSW1 Import | V>>V_NIL_1A | 0.25 | 1.1667 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL
VIC1-NSW1 Import | #R015386_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
VIC1-NSW1 Import | #R015770_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016472_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016579_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DDWG, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016639_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | N^^V_MSUTLT_2 | 0.16667 | 0 | Out = Murray to Upper Tumut or Murray to Lower Tumut 330 kV line, avoid voltage collapse in Southern NSW for loss of Murray to Lower Tumut or Murray to Upper Tumut 330 kV line | Outage
VIC1-NSW1 Import | #R015348_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_DDMSX5_1, Effective Date: 13/01/2017, Version: 1 | Other
VIC1-NSW1 Import | #R016525_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 07/08/2015, Version: 1 | Other
VIC1-NSW1 Import | #R016525_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 07/08/2015, Version: 1 | Other

## Outages
Constraint Set ID | 2017 Days | 2016 Days | Description
N-MBTE_1 | 278.1528 | 258.0729 | One Directlink cable
N-CHKK_96H | 137.0764 | 69.0972 | Coffs Harbour to Koolkhan (96H) 132 kV line
N-X_MBTE_2 | 115.3889 | 122.2604 | Two Directlink cables
N-X_96H_9W2 | 75.8924 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Kempsey-Raleigh (9W2) and 132kV line
N-KKLS_967 | 66.7847 | 0.31944 | Koolkhan to Lismore (967) 132 kV line
T-TUNN3 | 30.6875 | 18.1389 | Out = Tungatinah to New Norfolk No.3 110kV line
T-FATI | 30.1667 | 0.010417 | Out=Farrell-Tribute 220KV line
S-BRDV | 25.6354 | 74.5139 | Out = Brinkworth - Davenport 275 kV line
N-X_96H+9W2+9W5 | 25.2465 | 0 | Out= Coffs Harbour-Koolkhan (96H) & Raleigh-Kempsey(9W2) & Macksville-Kempsey(9W5) 132kV lines
S-BLMK | 24.0035 | 2.0972 | Out = Belalie - Mokota 275kV line
N-LTUT_64_15M | 22.3021 | 0.29514 | Lower Tumut to Upper Tumut (64) 330 kV line
S-BRTW | 21.3438 | 21.0347 | Out= Brinkworth- Templers West 275kV line
Q-STBS | 19.8194 | 0 | Out= 856 or 8831 H29 Stanwell to H20 Broadsound 275 kV line
N-BAMB_132_OPEN | 18.7292 | 54.8785 | Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path.
V-HWSM | 18.6111 | 3.4236 | Hazelwood to South Morang 500 kV line
V-KTTX_A3_R | 18.566 | 2.7639 | Keilor 500/220 kV (A3) transformer, Victorian radial mode
V-ROYP6_R | 16.5729 | 11.441 | Out = Rowville to Yallourn No. 6 220 kV line, Radial mode
T-TU_MB_NN2 | 15.2812 | 15.2569 | Out= Tungatinah to Meadowbank to New Norfolk No.2 110kV lines
I-CTRL_ISSUE_TE | 12.9167 | 1.7986 | DC Link Control Issue Constraint for Terranora
N-AR_CP2 | 12.8646 | 7.9201 | Out = Armidale Capacitor Bank (120 MVAr)
N-LDNC_81 | 12.7465 | 1.5382 | Out= Liddell to Newcastle (81)
N-BUDP | 12.6597 | 10.8854 | Buronga to Darlington Point (X5) 220 kV line
N-LS_VC1 | 11.566 | 1.7431 | Out= Lismore SVC
S-DVLK | 11.5382 | 0 | Out = Davenport-Mt Lock 275kV line (Note:both Black Range series capacitors I/S)
S-X_BC_CP | 10.1701 | 39.6007 | Out = both Black Range series capacitors bypassed
V-KTTX_A2_OR_A4_R | 9.8403 | 6.7986 | Outage = Keilor 500/220kV A2 or A4 transformer, Radial
S-DVBL | 9.7361 | 8.4688 | Out = Davenport - Belalie 275kV line (Note: with both Black Range series caps I/S)
T-LIPM | 9.684 | 0.14236 | Out = Liapootah to Waddamana to Palmerston 220kV line
N-X_MBTE_3 | 9.4062 | 36.9722 | All three Directlink cables
F-N_GUTHEGA_ZERO | 8.7465 | 0 | Guthega FCAS <= 0MW
I-MUTE_758 | 8.4896 | 2.3403 | Mudgeeraba to Terranora (758) 110 kV line
F-I_ML_APD | 8.2674 | 23.1354 | Out=Nil, Dymanic FCAS for APD Load Event
V-SMSC | 7.5799 | 1.2917 | One or both South Morang 330 kV series capacitors
V-HYTX_M12 | 6.9653 | 18.9028 | Out = Heywood (HYTS) M1 or M2 500/275 kV txfmr
V-HWYP2 | 6.9028 | 4.4236 | Out = Hazelwood to Yallourn No. 2 220 kV line, radial mode
F-T-BBGT | 6.6424 | 27.5972 | One Bell Bay - Georgetown 110 kV line, all four Bell Bay GTs on remaining 110 kV line, FCAS requirements
N-BLOWERNG_ZERO | 6.6076 | 0 | Blowering generation upper limit of 0 MW
S-X_CNRB+CB | 6.3438 | 0 | Out = Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S(Note:both Black Range series capacitors I/S)
S-NWRB | 6.3368 | 0.020833 | Out = North West Bend to Robertstown
V-HYTX_M3 | 6.2882 | 0.20833 | Out = Heywood (HYTS) M3 500/275 kV txfmr
S-NWBCB6024+6025 | 6.2465 | 0.25 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2)
S-CNRB | 6.2396 | 2.0625 | Out = Canowie-Robertstown 275kV line (i.e. Line ONLY O/S, with associated line CBs I/S), (Note: both Black Range series capacitors I/S)
S-RB_275KV_N_BUS | 6.2257 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, CBs 6616, 6573, 6005 and 6188 O/S) (Note:with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S)
F-N-ARDM_ONE | 5.8333 | 0.15625 | One Armidale to Dumaresq (8C or 8E) 330 kV line
N-ARDM_ONE | 5.8333 | 0.15625 | One Armidale to Dumaresq (8C or 8E) line
S-RB_275KV_S_BUS | 5.7535 | 0 | Out= Robertstown 275kV South Bus (i.e. CBs 6572, 6575, 6148 & 6149 OPEN and Robertstown 275/132 TX2 O/S).
S-KHKN | 5.5312 | 4.4479 | Keith to Kincraig 132 kV line
I-VS_050 | 5.4201 | 0 | Victoria to SA on VicSA upper transfer limit of 50 MW
V-HWYP1_TIE | 5.3472 | 0 | Out= Hazelwood to Yallourn No.1 220kV line, all 220kV buses tied at Hazelwood (i.e. HWPS 1-2-3-4-5-6 tied)
S-HDWF2_0 | 5.0382 | 0 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW
S_HDWF1_0 | 5.0382 | 0 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW
I-MUTE_757 | 4.9097 | 0.65278 | Mudgeeraba to Terranora (757) 110 kV line
I-ML_ZERO | 4.5938 | 20.3264 | Limit Murraylink to zero in either direction
S-X_MKRB+6573+74 | 4.3438 | 0 | Out= Mokota-Robertstown 275kV line AND Robertstown CB6573 and CB6574 (Note: with both Black Range series caps I/S)
S_HDWF3_0 | 3.4167 | 0 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW
S-RBPA | 3.3924 | 0 | Out= Robertstown - Para 275 kV line
T-SH_TX_WCP_OPEN | 3.3472 | 1.1146 | Out = one Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open
I-SV_250 | 3.0139 | 0 | SA to Victoria on VicSA upper transfer limit of 250 MW
V-HWCB4 | 2.6424 | 0.86111 | Hazelwood to Cranbourne No.4 500 kV line
S-NWB_CB6225 | 2.6319 | 0 | Out= North West Bend 132kV CB6225
S-BGTX | 2.4306 | 0 | Out = Bungama 275/132kV transformer O/S
S-X_CGTB+CB | 2.3611 | 0 | Out= Cherry Gardens-Tailembend 275kV line + associated 275kV line CBs O/S (Note: i.e. also Tailembend CBs 6535 & 6536 O/S); (Note: with both Black Range series caps I/S)
V-EPMB | 2.3403 | 13.0625 | One Eildon to Mt Beauty 220 kV line
V-HWTS_TX3_35PR_OPT2 | 2.3333 | 0 | Outage = Hazelwood A3 or A4 500/220 kV transformer, 3-5 Parallel mode, Jeeralang split with JLGS B units connected to Hazelwood 3-4-6 220kV bus group (option 2)
S-CNHL_HAL | 2.3125 | 3.5486 | Canowie to Hallett 275 kV line
V-MTMERCER_ZERO | 2.2951 | 2.184 | Mt Mercer Windfarm upper limit of 0 MW
N-X_96H_96R | 2.2604 | 0.069444 | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line
T-GTHA | 2.2118 | 0.23264 | Out = One George Town to Hadspen 220kV line
N-DPWG_63_X5 | 2.0312 | 0.055556 | Out = Darlington Point to Wagga (63) 330kV line + line X5 opened
N-LTWG_RADIAL | 2.0139 | 0.065972 | Lower Tumut to Wagga line
S-SA_WIND_1200 | 1.9306 | 0 | Discretionary upper limit for South Australian wind generation of 1200 MW.
F-N-MUTW_88 | 1.9271 | 1.3958 | Muswellbrook to Tamworth (88) 330 kV line
V-KTSY_R | 1.8507 | 39.9306 | Keilor to Sydenham 500 kV line
N-AR_VC1 | 1.8472 | 2.0729 | Armidale SVC
V-SMTS_HTX_R | 1.8299 | 14.3611 | Outage = South Morang H 330/220 kV transformer, only one SMTS H txfmr in service, Radial
I-MSUT | 1.7951 | 1.0764 | Murray to Upper Tumut (65) 330 kV line
Q-BCRG_811 | 1.7812 | 0 | Bouldercombe to Raglan (811) 275 kV line
V-MLMO | 1.7743 | 1.0451 | Moorabool to Mortlake 500 kV line
V-ROTX_R | 1.6562 | 14.7257 | Rowville 500/220kV (A) transformer, Radial
I-X_DDMSX5 | 1.6076 | 0 | Out=Dederang - Murray (67or68) and DarlingtonPt - Buronga (X5)
V-SMTS_BYPASS_HW_SY | 1.4757 | 7.2465 | Outage = SMTS 500kV bus or CB outages or SMTS bus bypass that creates risk of HWTS-SMTS and SMTS-SYTS combined line trip, Radial or Parallel
S-HUBG | 1.434 | 0 | Out= Hummocks-Bungama 132kV line (Note: this offloads Snowtown WF)
V-DDSM | 1.4028 | 3.7431 | One Dederang to South Morang 330 kV line
S-BRBG | 1.3993 | 0 | Out = Brinkworth to Redhill to Bungama 132kV lines (Note: outage also takes out Clements Gap Windfarm).
T-GTSH | 1.3854 | 14.8299 | One George Town to Sheffield 220kV line
V-HORC | 1.2708 | 1.4097 | Out = Horsham to Redcliffs 220kV line
S-PA_VC1 | 1.2014 | 42.3194 | One Para SVC, with both Black Range Series caps I/S
T-BUSH_220_WCP_OPEN | 1.1424 | 0 | Out = Burnie to Sheffield No.1 220kV line O/S, West Coast 110/220KV parallel open, either 110 kV CB at Hampshire open or parallel opened at Farrell, Burnie 110 kV bus NOT split
T-PMSH | 1.1354 | 0.18403 | Out = Palmerston to Sheffield 220kV line
F-T-CSGO | 1.1042 | 1.1076 | Out = one Chapel St to Gordon 220kV line, FCAS Requirements
V-BAEL | 1.0938 | 0 | Outage = Ballarat to Elaine 220kV line
V-X_MLSM_EMTT_KTS_R | 1.0799 | 3.6146 | Out = One Moorabool to Sydenham to South Morang 500kV line, EMTT scheme O/S, KTS 220kV bus #1 & #2 tied with both KTS-TTS lines bypass KTS to WMTS, Radial
S-X_PLN_02 | 1.0694 | 0.34028 | Yadnarie to Port Lincoln line
N-LDMU_83 | 0.96528 | 0 | Liddell to Muswellbrook (83) 330 kV line
F-N-LDMU_83 | 0.96528 | 0 | Liddell to Muswellbrook (83) 330 kV line
N-TW_330_CB5102 | 0.93403 | 0 | Out= Tamworth 330kV CB 5102
S-NWRB2 | 0.93056 | 17.5556 | North West Bend to Robertstown No.2 132 kV line
N-X_96H+9W2+96L | 0.91667 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Kempsey-Raleigh (9W2) and Lismore-Tenterfield (96L) 132kV line
V-MACARTHUR_ZERO | 0.89931 | 2.1007 | Macarthur Wind Farm upper limit of 0 MW
V-BESH | 0.89236 | 0 | Outage = Bendigo to Shepparton 220kV line
V-MLTR | 0.88889 | 2.1007 | Moorabool to Tarrone No.1 500 kV line
I-LTMS | 0.88542 | 0 | Lower Tumut to Murray (66) 330 kV line
V-KGRC | 0.87847 | 0.40278 | Outage = Kerang to Wemen or Red Cliffs to Wemen 220 kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line
S-HALWF2_0 | 0.82986 | 0 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW
V-X_HWSM_SMF2_STAB | 0.73611 | 0 | Out= Hazelwood - South Morang 500kV line & South Morang F2 500/330kV txfmr, Stability equations only
N-BOCORWF1_ZERO | 0.71875 | 0 | Boco Rock WF upper limit of 0 MW
S-SE_132KV_BUS | 0.71528 | 1.5 | Out = ONLY One South East 132 kV bus (i.e. either East or West 132kV bus WITH/WITHOUT associated CBs)
V-BAWB | 0.71181 | 0 | Out = Ballarat to Waubra 220kV line section, limit Ararat to 5 MW to manage islanding risk
N-JNWG_RADIAL | 0.70486 | 3.7778 | Jindera to Wagga (62) 330 kV line, Wagga to Yass 132 kV network split, X5 opened and with two 2 Yass transformer in service
V-X_HWSM_HWRO3 | 0.64931 | 0 | Out = One Hazelwood to South Morang and Hazelwood to Rowville 500kV lines
T-TU_WA2 | 0.61458 | 9.7778 | Out = Tungatinah to Waddamana No.2 110kV line
T-NWSD | 0.59028 | 0.13194 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752
Q-X_SMRS_A | 0.5625 | 0 | Two Strathmore to Ross 275 kV lines with parallel 132 kV network closed.
S-SNWWF_0 | 0.50347 | 1.3889 | Discretionary upper limit for Snowtown WF generation of 0 MW
N-LTUT_30M | 0.50347 | 0 | Out= LowerTumut to UpperTumut (64); line loading limits on 65, 66 lines imposed by 30 minute ratings
N-X_96H_LS_SVC | 0.48264 | 1 | Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode
T-BWLF | 0.47569 | 0.19097 | Out = Bridgewater to Lindisfarne OR Bridgewater to Waddamana 110kV line
S-NWCB6033+6225 | 0.46528 | 1.5104 | Out = North West Bend CBs 6033 and 6225 (this offloads North West Bend TX3)
S-BLNBH_0 | 0.46181 | 0.45833 | Out = Belalie - North Brown Hill 275kV line O/S (i.e. North Brown Hill WF <= 0 MW)
S-TBL_0 | 0.46181 | 0.39931 | Discretionary upper limit for The Bluff generation of 0 MW
S-STTX | 0.45833 | 8.8889 | Snowtown 132/33 kV transformer or Snowtown CB4593 or CB6265
N-BROKENH1_ZERO | 0.38889 | 1.8611 | Broken Hill Solar Farm upper limit of 0MW
S-NWCB6021+6225 | 0.36806 | 0 | North West Bend CBs 6021 and 6225
N-MOREESF1_ZERO | 0.35417 | 4.5972 | Moree Solar Farm upper limit of 0 MW
Q-MEWV_824 | 0.34722 | 0.0069444 | Out= Mt England to Wivenhoe (824) line
S-WTTP | 0.33681 | 0.58333 | Out= Waterloo-Templers 132kV line
T-LFWA | 0.33681 | 0.28819 | Out = One Lindisfarne to Waddamana 220 kV line
N-X_967_LS_SVC | 0.32639 | 0 | Koolkhan to Lismore (967) 132kV line and Lismore SVC
V-HYMO | 0.31597 | 2.7188 | Heywood to Mortlake No.2 500 kV line
S-CNLK | 0.30556 | 0 | Out= Canowie-Mt Lock 275kV line (Note: with both Black Range series caps I/S)
S-SE_CB6186_CB6187 | 0.27778 | 1.0972 | Out= South East 132kV CB 6186 Or CB 6187
V-DDWO_RADIAL | 0.26736 | 1.4271 | Dederang to Wodonga 330 kV line with Wagga area radial supply option
N-NYNGANSF_010 | 0.23264 | 1.2222 | Nyngan Solar Farm upper limit of 10 MW
N-TW_330_BUS3 | 0.20833 | 0.34722 | Out= Tamworth No.3 330kV bus
S-X_WTTP+CB | 0.19097 | 0 | Out = Templers - Waterloo 132kV line with associated critical line CBs O/S (i.e. Waterloo CB 7025 & CB7024 O/S)
V-ARARAT_ZERO | 0.15972 | 24.7812 | Ararat Wind Farm upper limit of 0 MW
V-OAKLANDSHILL_ZERO | 0.15625 | 0 | Oaklands Hill Windfarm upper limit of 0 MW
F-Q_TARONG#2_ZERO | 0.13542 | 1.3646 | Tarong 2 FCAS <= 0MW
F-Q_TARONG#1_ZERO | 0.13542 | 2.3576 | Tarong 1 FCAS <= 0MW
I-BL_ZERO | 0.125 | 100.8576 | Limit Basslink to zero in either direction
F-T-COGT | 0.125 | 1.9757 | Out = one Comalco to George Town 220kV line OR loss of both Comalco to Georgetown 220 kV lines or all Comalco potlines declared credible
N-TARALGAWF_ZERO | 0.11458 | 0 | Taralga WF upper limit of 0 MW
I-NQ_000 | 0.10417 | 0 | NSW to Qld on QNI upper transfer limit of 0 MW
T-MA_WESTCOAST | 0.041667 | 0 | Limit Mackintosh generation to 110% and 90% of West Coast load
I-TE_ZERO | 0.03125 | 0.12153 | Terranora Interconnector zero transfer limit in either direction
V-OAKLANDSHILL_42 | 0.027778 | 0 | Oaklands Hill Windfarm upper limit of 42 MW
V-X_HWSM_ROSM | 0.017361 | 0 | Out = One Hazelwood to South Morang and Rowville to South Morang 500kV lines
I-VS_500 | 0.013889 | 0 | Victoria to SA on VicSA upper transfer limit of 500 MW
N-GUNNING1_ZERO | 0.013889 | 0.67014 | Gunning unit upper limit of 0 MW
I-CTRL_ISSUE_ML | 0.010417 | 0.23264 | DC Link Control Issue Constraint for Murraylink
Q-BRBRA_8839 | 0.0069444 | 0 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839
T-X_FASH | 0 | 0 | Out = both Farrell to Sheffield lines

## Outage stats
Column1 | Unplanned | Short Notice | ≤ 30 days | > 30 days
APT 2013 | 10 | 9 | 0 | 1
2014 | 12 | 27 | 9 | 0
2015 | 27 | 60 | 8 | 2
2016 | 24 | 36 | 7 | 1
2017 | 20 | 33 | 5 | 4
ElectraNet 2013 | 305 | 691 | 1452 | 200
2014 | 93 | 311 | 571 | 108
2015 | 447 | 918 | 1003 | 231
2016 | 110 | 266 | 309 | 176
2017 | 281 | 687 | 907 | 426
Essential E 2013 | 21 | 52 | 98 | 0
2014 | 6 | 39 | 82 | 4
2015 | 0 | 17 | 59 | 0
2016 | 3 | 26 | 40 | 0
2017 | 4 | 28 | 61 | 0
Powerlink 2013 | 384 | 1111 | 1686 | 97
2014 | 350 | 1143 | 1993 | 15
2015 | 1076 | 3173 | 6415 | 100
2016 | 273 | 885 | 2265 | 17
2017 | 1796 | 5071 | 11266 | 195
AusNet 2013 | 221 | 1229 | 705 | 62
2014 | 134 | 636 | 991 | 614
2015 | 161 | 678 | 1290 | 764
2016 | 116 | 472 | 973 | 506
2017 | 316 | 1484 | 1208 | 80
TasNetworks 2013 | 123 | 775 | 596 | 480
2014 | 179 | 778 | 473 | 38
2015 | 197 | 1119 | 918 | 86
2016 | 170 | 876 | 695 | 97
2017 | 89 | 472 | 602 | 323
Transgrid 2013 | 309 | 665 | 1226 | 790
2014 | 33 | 125 | 130 | 73
2015 | 128 | 629 | 993 | 302
2016 | 19 | 88 | 166 | 32
2017 | 277 | 911 | 1365 | 856

## NEM Changes
PROJECT | DATE | REGION | NOTES
Hornsdale Wind Farm - Stage 2 | 21 February 2017 | SA | New Generator
Hazelwood Units 1-8 | 2017-04-01 | Victoria | Deregistered generator, units progressively shut down in late March 2017.
Mudgeeraba 275/110 kV (5T) transformer | 23 May 2017 | Qld
Ballarat to Moorabool No.2 220 kV line | 09 June 2017 | Victoria
White Rock Wind Farm | 06 July 2017 | NSW | New Generator
Hornsdale Wind Farm - Stage 3 | 14 August 2017 | SA | New Generator
Gullen Range Solar Farm | 15 August 2017 | NSW | New Generator
Deer Park Terminal Station | 11 September 2017 | Victoria | Cut into Geelong to Keilor #2 220 kV line
Temporary Generation South - Lonsdale | 20 October 2017 | SA | New Generator
Temporary Generation North - Edinburgh | 20 October 2017 | SA | New Generator
Kiata Wind Farm | 03 November 2017 | Victoria | New Generator
Hornsdale Battery Power Reserve | 14 November 2017 | SA | First large scale battery in the NEM connected at Hornsdale
Kidston Solar Farm | 23 November 2017 | Qld | New Generator
Sapphire Substation | 28 November 2017 | Victoria | New substation cut into the existing Armidale to Dumaresq (8E) 330 kV for the Sapphire wind farm. The 8E line is now the Armidale to Sapphire (8E) and Dumaresq to Sapphire (8J) 330 kV lines.
Sapphire Wind Farm | 7 December 2017 | NSW | New Generator
Parkes Solar Farm | 13 December 2017 | NSW | New Generator

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.