## Index
The National Electricity Market Constraint Report 2019
Electronic Material
This spreadsheet provides (for each calendar year):
* Constraint equation changes year on year comparison
* Binding constraint equations (energy and FCAS separately)
* Binding Impact of constraint equations
* Summary of binding/binding impact constraint equations by region
* Summary of binding/binding impact constraint equations for System Normal vs Outages
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
* Network and generation augmentations
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page
Binding constraints:
A constraint equation is a linear equation, with a left hand side (LHS) and a right hand side (RHS). A constraint is binding when LHS=RHS, which means it has reached its upper limit.
In some cases, the binding results for several constraint equation IDs have been combined. This is due to some limits being represented by several constraint equations, to either:
• Move each generator from a maximum calculation onto the LHS of separate constraint equations (such as the New South Wales to Queensland voltage stability limit).
• Manage the same limit under different network configurations (such as Yallourn W1 switched into 500 kV or 220 kV mode).
• Combine different values of network support for the same generator(s).
Binding Impact:
Binding Impact is used to distinguish between the severities of different binding constraint equations. It represents the financial pain associated with that binding constraint equation and can be a good way of picking up congestion issues. It is a relative term, not an absolute term.

## Constraint Changes
Constraint changes by region and year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019
Ad-Hoc | 0 | 0 | 0 | 1 | 1 | 0
Constraint Automation - Real Time | 24110 | 11484 | 22603 | 29805 | 37744 | 32817
Constraint Automation | 166 | 98 | 64 | 20 | 48 | 49
DATASNAP | 87 | 105 | 115 | 44 | 92 | 90
FCAS | 255 | 543 | 257 | 267 | 486 | 1192
NSW | 5272 | 6332 | 1973 | 2455 | 8206 | 5092
Negative Residue | 0 | 0 | 0 | 0 | 0 | 0
Non-Conformance | 3 | 5 | 5 | 52 | 35 | 29
Other | 0 | 2 | 0 | 0 | 3 | 1
Outage Ramping | 19888 | 21056 | 20484 | 16928 | 19368 | 25718
PASA | 12 | 0 | 0 | 0 | 0 | 0
Qld | 270 | 118 | 206 | 246 | 1716 | 582
Quick | 93 | 101 | 359 | 386 | 1032 | 865
SA | 600 | 1001 | 3197 | 1775 | 3239 | 7132
Tas | 726 | 121 | 1050 | 134 | 193 | 629
Vic | 637 | 3541 | 3251 | 1376 | 6280 | 5656
Total constraint eqns | 10303 | 11231 | 11660 | 11578 | 11467 | 12348
Total changes without outage ramping and CA-RT | 8121 | 11967 | 10477 | 6756 | 21331 | 21317
Total number of constraints
| 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
Constraint Equations | 7746 | 7697 | 8275 | 8902 | 9523 | 9745 | 9935 | 10303 | 11231 | 11660 | 11578 | 11467 | 12348
Constraint Sets | 3366 | 3369 | 3431 | 3559 | 3657 | 3597 | 3410 | 3424 | 3630 | 3778 | 3917 | 4036 | 4390
Constraint Functions |  |  | 347 | 382 | 390 | 401 | 366 | 359 | 364 | 373 | 387 | 505 | 585
Increase in Constraint Equations |  |  | 578 | 627 | 621 | 222 | 190 | 368 | 928 | 429 | -82 | -111 | 881

## Binding
Constraint Equation ID | 2019 Hours | 2018 Hours | Description | Type | Region
N^^V_NIL_1 | 2060.5833 | 1117.8333 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | NSW
#YENDWF1_E | 1080.3333 | 0 | VBAW1Y.ENERGY * 1 <= 103 (Wt = 360) | Other | Quick
#OAKEY2SF_E | 1015.5 | 0 | QTKS2O.ENERGY * 1 <= 43 (Wt = 360) | Other | Quick
V_T_NIL_FCSPS | 974.5833 | 114.5833 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Vic
#LILYSF1_E | 915.8333 | 0 | QBDR1L.ENERGY * 1 <= 100 (Wt = 360) | Other | Quick
#CHILDSF1_E | 907.0833 | 0 | QTBS1C.ENERGY * 1 <= 56 (Wt = 360) | Other | Quick
#BANN1_E | 839.25 | 674.8333 | VWES1B.ENERGY * 1 <= 32 (Wt = 360) | Other | Quick
#PPCCGT_P_E | 832.25 | 774.5833 | SPPT.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#PPCCGT_O_E | 830.25 | 762.9167 | SPPT.ENERGY * 1 = 202 (Wt = 755) | Other | Direction
Q^^NIL_QNI_SRAR | 773.8333 | 0 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Qld
#LGAPWF1_E | 676.4167 | 0 | SLGW1L.ENERGY * 1 <= 126 (Wt = 360) | Other | Quick
SVML_ZERO | 624.4167 | 289.6667 | SA to Vic on ML upper transfer limit of 0 MW | Outage | SA
S_WIND_1200_AUTO & S_NIL_STRENGTH_1 | 624.25 | 1063.0833 | Upper limit (1300 to 1750 MW) for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements. Automatically swamps out when required HIGH combination is online. | NIL | SA
#MUWAWF1_E | 601.75 | 0 | VMRT1M.ENERGY * 1 <= 148 (Wt = 360) | Other | Quick
#CLERMSF1_E | 562.0833 | 0 | QLLV3C.ENERGY * 1 <= 75 (Wt = 360) | Other | Quick
#DAYDSF1_E | 552.6667 | 1111.25 | QCCK1D.ENERGY * 1 <= 150 (Wt = 360) | Other | Quick
#BNGSF2_E | 537.8333 | 1691.5833 | SBEM2B.ENERGY * 1 <= 37 (Wt = 360) | Other | Quick
#SRSF1_E | 489.3333 | 0 | QTBS2S.ENERGY * 1 <= 35 (Wt = 360) | Other | Quick
N_MBTE1_B | 466.6667 | 130.3333 | Out= one Directlink cable, Qld to NSW limit | Outage | NSW
N>N-NIL_CLDP_1 | 448.3333 | 0 | Out= Nil, avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | NIL | NSW
S>V_NIL_NIL_RBNW | 406.5833 | 338.75 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL | SA
#HAMISF1_E | 330.5 | 831.1667 | QSLD1H.ENERGY * 1 <= 38 (Wt = 360) | Other | Quick
#WHITSF1_E | 327.75 | 1129.8333 | QSLS1W.ENERGY * 1 <= 38 (Wt = 360) | Other | Quick
V_MACARTHUR_ZERO | 310.9167 | 0.16667 | Macarthur upper limit of 0 MW | Outage | Vic
#CROWLWF1_E | 301.0833 | 0 | VCWL1C.ENERGY * 1 <= 72 (Wt = 360) | Other | Quick
V_KIATAWF_FLT_0 | 269.4167 | 0 | Limit Kiata Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
N_SILVERWF_MAX | 267.25 | 119.6667 | Limit MW output of Silverton wind farm to not exceed 131 MW with Broken Hill solar generating | Outage | NSW
S:V_500_HY_TEST_DYN | 266.3333 | 122.5833 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
T>T_NIL_110_1 | 251.5833 | 150.9167 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Tas
#CSPVPS1_E | 242.75 | 74.5833 | QCOS1C.ENERGY * 1 <= 32 (Wt = 360) | Other | Quick
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 234.5833 | 144.9167 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Qld
V_GANWRSF_FLT_25 | 230.8333 | 0 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | NIL | Vic
#TORRB4_P_E | 224.0833 | 123.25 | STSB4.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
S>V_NIL_SETX_SETX1 | 218.5833 | 0 | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL | SA
#TORRB2_P_E | 217.75 | 370.3333 | STSB2.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
N_X_MBTE2_A & N_X_MBTE2_B | 216.75 | 300.6667 | Out= two Directlink cables, NSW to Qld limit | Outage | NSW
Q_CS_1850 | 214.1667 | 0 | Qld Central to Qld South upper transfer limit of 1850MW (discretionary) | Outage | Qld
Q_CS_1100 | 211.5833 | 0 | Qld Central to Qld South upper transfer limit of 1100MW (discretionary) | Outage | Qld
S>>PARB_RBTU_WEWT | 210.25 | 26.25 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
#KSP1_E | 201 | 71.5833 | QROG1K.ENERGY * 1 <= 25 (Wt = 360) | Other | Quick
Q>>WOPW_WOSP_WOGP_2 | 192.6667 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
#HAYMSF1_E | 187.6667 | 2144.5 | QCCK2H.ENERGY * 1 <= 50 (Wt = 360) | Other | Quick
#DEVILS_G_E | 177.75 | 0 | TDG11.ENERGY * 1 <= 64 (Wt = 360) | Other | Quick
#TORRB1_P_E | 176.75 | 275.5833 | STSB1.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
N_X_MBTE_3A & N_X_MBTE_3B | 174 | 253.75 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | NSW
V_MURRAWRWF_MAX | 172.1667 | 0 | Limit MW output of Murra Warra wind farm to hold point levels during day/night | Outage | Vic
#TORRB4_O_E | 167.75 | 77.1667 | STSB4.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
V_GANWRSF_FLT_0 | 166.6667 | 0 | Limit Gannawarra solar farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V^^N_NIL_1 | 166.4167 | 74.8333 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Vic
#TORRA3_O_E | 165.75 | 535.75 | STSA3.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
#TORRA3_P_E | 165.4167 | 536.5 | STSA3.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
S:V_500_HY_TEST | 165.3333 | 25.6667 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
V_KARADSF_FLT_45 | 162.9167 | 0 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | NIL | Vic
#TORRB2_O_E | 155.5 | 195.9167 | STSB2.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
Q_LILYSF1_ZERO | 147.75 | 0 | Lilyvale Solar Farm upper limit of 0 MW | Outage | Qld
#QPS1_E | 146.8333 | 0 | SQPS1.ENERGY * 1 <= 20 (Wt = 360) | Other | Quick
V_KARADSF_FLT_0 | 141 | 0 | Limit Karadoc solar farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
Q>NIL_BI_xxx | 130.1667 | 91.25 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104 and 7105 (T022 Callide A to T152 Gladstone South) 132 kV lines open with 132 kV intact/split between T022 Callide A and H015 Lilyvale. | NIL | Qld
V_KIATA_ISL_0 | 127.1667 | 0 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
N_BROKENHSF_FLT_26 | 126.1667 | 0 | Limit Broken Hill Solar Farm upper limit to 26 MW to manage post contingent voltage oscillation | NIL | NSW
#TORRB1_O_E | 125.3333 | 176.0833 | STSB1.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
N_STWF1_ZERO | 118.8333 | 45.5833 | Silverton wind farm upper limit of 0 MW | Outage | NSW
T_LIPM_PMWA_1_N-3 | 115.9167 | 0 | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to <= southern load + 15 MW | Outage | Tas
V::N_HWSM_xxx | 113.8333 | 14 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#TORRA4_P_E | 113.5 | 512.25 | STSA4.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA4_O_E | 113.3333 | 512.0833 | STSA4.ENERGY * 1 >= 70 (Wt = 755) | Other | Direction
S>VMLMHNW1 | 104.4167 | 0.083333 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | SA
V_SV_MLMO_NETT | 104.25 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW. Swamp out when MOPS/DUNDWF not generating | Outage | Vic
#TORRA1_P_E | 103.6667 | 774.5833 | STSA1.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA1_O_E | 103.5 | 773 | STSA1.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
#HAUGHT11_E | 102.1667 | 0 | QHAR1H.ENERGY * 1 <= 100 (Wt = 360) | Other | Quick
T>T_LIPM_110_2A | 101.8333 | 1.4167 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 100.9167 | 82 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | NSW
V_WEMENSF_FLT_0 | 100.75 | 0 | Limit Wemen Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
#TORRA2_P_E | 97.9167 | 229.0833 | STSA2.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA2_O_E | 97.5833 | 228.5833 | STSA2.ENERGY * 1 >= 60 (Wt = 755) | Other | Direction
Q>X_CPWO_BI_INTACT | 95.6667 | 0 | Out= 813+815 or 814,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines,7104 and 7105(T022 Callide A to T152 Gladstone South) 132 kV lines open with 132 kV intact/split btw T022 Callide A and H015 Lilyvale, Feedback | Outage | Qld
V_WEMENSF_FLT_44 | 92.4167 | 0 | Limit Wemen Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | NIL | Vic
V_MTMERCER_ZERO | 88.9167 | 1.25 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
Q>NIL_COLNVSF1 | 87 | 0 | Out = Nil, Limit Collinsville Solar Farm to thermal rating of Powerlink's RMU | NIL | Qld
N_BROKENH1_ZERO | 85.0833 | 1.1667 | Broken Hill Solar Farm upper limit of 0 MW | Outage | NSW
QNTE_SUPPORT | 83 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Qld
Q>NIL_BI_CAGS_CALV_O | 82.9167 | 33.6667 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104/7105 (T022 Callide A to T152 Gladstone South) 132 kV lines closed with 132 kV split between T022 Callide A and H015 Lilyvale. | NIL | Qld
NQTE_-060 | 79.9167 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -60 MW | Outage | NSW
V_BANSF_BBD_60 | 79.9167 | 0 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Vic
#LYA2_E | 78.4167 | 0 | VLYP2.ENERGY * 1 <= 535 (Wt = 360) | Other | Quick
V^SML_HORC_3 | 78 | 17 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
S>NIL_NIL_NWMH2 | 77.3333 | 14.6667 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
V>>N-NIL_HA | 75.5 | 21.9167 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Vic
N>N-NIL_DC | 73.4167 | 81.1667 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL | NSW
S>>PARB_RBTU_WTTP | 72.9167 | 8.9167 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
#COOPGWF1_E | 72.5833 | 0 | QCPG1C.ENERGY * 1 <= 293 (Wt = 360) | Other | Quick
V_BANNERTSF_FLT_0 | 69.5833 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
Q>CPWO_B_CAGS_CALV_C | 67.25 | 0 | Out= 813+815 or 814+816,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines,7104 and/or 7105 (T022 Callide A to T152 Gladstone South)132 kV lines close with 132 kV intact btw T022 Callide A and H015 Lilyvale, Feedback | Outage | Qld
S_DVRB2_270 | 66.8333 | 27.5833 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | SA
#OSB-AG_O_E | 65.5833 | 353.3333 | SNBN1.ENERGY * 1 = 170 (Wt = 755) | Other | Direction
#OSB-AG_P_E | 65.5833 | 353.5833 | SNBN1.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
V_OWF_TGTSNRBHTN_30 | 65.0833 | 26.0833 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Vic
#TBSF1_E | 63.5833 | 0 | STBS1T.ENERGY * 1 <= 80 (Wt = 35) | Other | Quick
N>N-NIL_MBDU | 61.8333 | 0 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
V_T_NIL_BL1 | 61.75 | 24.4167 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL | Vic
S_HALWF_0 | 60.5833 | 0 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW | Outage | SA
S_HALWF2_0 | 59.1667 | 13 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | SA
V^^SML_NSWRB_2 | 59.1667 | 0 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Vic
Q:NIL_CS | 57.75 | 7.5 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW) | NIL | Qld
S:VS_650_HY_TEST_DYN | 57.4167 | 27.6667 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
#BARKIPS1_E | 55.6667 | 0 | SBPS1B.ENERGY * 1 <= 70 (Wt = 360) | Other | Quick
N_COLEASF1_ZERO | 55.25 | 7.4167 | Coleambally solar farm upper limit of 0 MW | Outage | NSW
V_MURRAWRWF_FLT_25 | 53.4167 | 0 | Limit Murra Warra Wind Farm upper limit to 25 MW to manage system stability on the next contingency due to voltage oscillation | Outage | Vic
T::T_NIL_2 | 52.3333 | 0 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL | Tas
V_BANSF_45_22INV | 52.0833 | 0 | Limit Bannerton Solar Farm upper limit to 45 MW with max 22 inverter available, upper limit set to 0 MW if number of inverter available exceed 22. This is to manage voltage oscillation | Outage | Vic
S_DVRB_270 | 51.75 | 0 | Out = DV-BL 275kV line Or MK-RB 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF + Hallet Hill WF (i.e. generation + load component) <= 270 MW | Outage | SA
T_MRWF_QLIM_xx | 51.5 | 4.0833 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Tas
Q_CLST_STRGTH_MEWF | 49.5833 | 0 | Out = 855 or 8873 or 8874 or 856 or 8831, limit Mt Emerald WF to 50% capacity (26 turbines) if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=3 + Gladstone >=3 + (Stan+Cal+Glad >=10) + Haughton >0 + Sun Metals >0. Zero otherwise. | Outage | Qld
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 49 | 208.25 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Vic
NSA_Q_BARCALDN | 48.9167 | 32.4167 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Qld
V_OAKHILL_TFB_42 | 48.4167 | 20.6667 | Out = Nil, Oaklands Hill Windfarm upper limit of 42.7 MW due to Oaklands Hill windfarm TFB mode operation, DS only. Swamp out if TFB mode is OFF | NIL | Vic
V>V_ELTS_TX_R2 | 46.75 | 0 | Out = Elaine R2 220/132kV transformer, limit Mt Mercer WF MW output to avoid overloading the remaining in service R1 220/132kV transformer. | Outage | Vic
Q:NIL_OAKEY2SF | 46.3333 | 0 | Limit Oakey 2 solar farm to 0MW when Oakey GT is online to prevent transient instability for 3 phase fault at Tangkam | NIL | Qld
#KPP_1_E | 44.75 | 0 | QBRA4K.ENERGY * 1 <= 745 (Wt = 360) | Other | Quick
#TORRB3_P_E | 44.5 | 240.5 | STSB3.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
VT_000 | 44.3333 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Vic
V_VS_LB_CAN_50 | 44.1667 | 0 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage | SA
V_KARSF_45_21INV | 43.6667 | 0 | Limit Karadoc Solar Farm upper limit to 45 MW with max 21 inverter available, upper limit set to 0 MW if number of inverter available exceed 21. This is to manage voltage oscillation | Outage | Vic
N_BROKENHSF_FLT_30 | 43.5833 | 0 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | NSW
V_KIATAWF_FLT_15 | 43.4167 | 0 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V^SML_BUDP_3 | 42.5833 | 5.5 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
Q_CS_1700 | 41 | 0 | Qld Central to Qld South upper transfer limit of 1700MW (discretionary) | Outage | Qld
T>T_NIL_BL_110_4 | 39.1667 | 0 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Tas
S>>X_CNRB+CB_01 | 37.9167 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
V_MURRAWRWF_FLT_50 | 37.5 | 0 | Limit Murra Warra Wind Farm upper limit to 50 MW to manage system stability on the next contingency due to voltage oscillation | Outage | Vic
V_MURRAWRWF_FLT_15 | 37.4167 | 0 | Limit Murra Warra Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
#NEVERSF1_E | 37 | 0 | NWLS3N.ENERGY * 1 <= 79 (Wt = 360) | Other | Quick
N_MOREESF1_ZERO | 36 | 0 | Moree Solar Farm upper limit of 0 MW | Outage | NSW
N^^V_BUDP_1 | 35.1667 | 1.5833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
I_QNI_ONE_PHASE_N-2 | 34.3333 | 1.4167 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage | Other
N_BROKENHSF_FLT_0 | 33.8333 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | NSW
VSML_ZERO | 33.4167 | 490.3333 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Vic
SV_100 | 33.25 | 0 | SA to Victoria on VicSA upper transfer limit of 100 MW | Outage | SA
N^^V_DDSM1 | 32.8333 | 6.25 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | NSW
Q_NIL_STRGTH_MEWF | 32.1667 | 0 | Out = Nil, limit Mt Emerald WF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to TOA 393 | NIL | Qld
T::T_NIL_4 | 32.0833 | 14.1667 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
Q>X_CPWO2_CPWU_CPWO1 | 32 | 0 | Out= Calliope River to Woolooga (814+816) line, avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (813+815) line, Feedback | Outage | Qld
VSML_ROC_80 | 31.75 | 43.1667 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
V_YENDWF_MAX | 31.6667 | 0 | Limit MW output of Yendon wind farm to hold point levels during day/night | Outage | Vic
N^N_CHLS_1 | 30.25 | 3.1667 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | NIL | NSW
N_SILVERTWF_FLT_0 | 30 | 0 | Limit Silverton Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | NSW
S>VMLMHNW2 | 29.6667 | 0 | Out=Monash-North West Bend #2 132kV line, SA-V on ML avoid overload on North West Bend-Monash #1 132kV line, feedback | Outage | SA
N>LSDU9U6_LSDU9U7 | 29.5833 | 6.0833 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
S:VS_650_HY_TEST | 29.1667 | 8.4167 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
V_MORTLAKE12_150 | 29.1667 | 0 | Mortlake unit 1 & 2 upper limit of 150 MW | Outage | Vic
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 28.9167 | 19.3333 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL | Qld
V_ARARATWF_FLT_0 | 28.5833 | 0 | Limit Ararat Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
SV_250 | 28.4167 | 0 | SA to Victoria on Heywood upper transfer limit of 250 MW | Outage | SA
V_WEMENSF_45_21INV | 28.0833 | 0 | Limit Wemen Solar Farm upper limit to 45 MW with max 21 inverter available, upper limit set to 0 MW if number of inverter available exceed 21. This is to manage voltage oscillation | Outage | Vic
VT_ZERO | 27.9167 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Vic
V_MURRAWRWF_FLT_0 | 27.9167 | 0 | Limit Murra Warra Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
N>N-NIL_LSDU | 27.8333 | 4.9167 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
S^SETX_GEN_CAP | 27.5 | 0 | Out= One South East 275/132kV transformer O/S, avoid local voltage collapse on trip of remaining South East transformer, | Outage | SA
SVML_ROC_80 | 27.25 | 49.9167 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
V_CWWF_FLT_50 | 27.0833 | 0 | Limit Crowlands Wind Farm upper limit to 50 MW to manage system stability on the next contingency | Outage | Vic
V^SML_BAWB_3 | 26.75 | 0 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
#TORRB4_D_E | 26.6667 | 0 | STSB4.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
Q>>CPPW_WOSP_WOGP_2 | 26.5 | 0 | Out= Calliope River to Palmwoods (813+815+810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
T:T_LIPM_1 | 26.0833 | 19.6667 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Tas
#PPCCGT_D_E | 26 | 0 | SPPT.ENERGY * 1 = 180 (Wt = 755) | Other | Direction
Q:N_1078 | 25.75 | 17.6667 | QNI oscillatory stability limit of 1078 MW | Outage | Qld
#TORRB3_O_E | 25.5833 | 138.25 | STSB3.ENERGY * 1 = 70 (Wt = 755) | Other | Direction
S>NIL_TINO3_TINO4 | 24.75 | 0 | Out = Nil, avoid O/L of TIPS-New Osborne #4 66kV line on trip of TIPS-New Osborne #3 66kV line (Note: Assumed CB 5536 at New Osborne is CLOSED). This constraint swamps out if New Osborne CB 5536 is OPEN. | NIL | Constraint Automation - RT
N^^Q_NIL_A | 24.6667 | 7 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | NSW
T>T_NIL_BL_110_18_1 | 24.5833 | 26.6667 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
S>V_460_DYN | 23.25 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | SA
Q_STR_233310_MEWF_26 | 23.0833 | 0 | Limit MT Emerald WF to 50% of max capacity (#26 turbine) if Kareeya > = 2 and Stanwell >= 3 and Callide >= 3 and Gladstone> = 3 and total of Stanwell, Callide and Gladstone >=10. Limit to zero otherwise. | Outage | Qld
N^N-LS_SVC | 22.3333 | 488 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage | NSW
S>NIL_SGBN_SGSE-T2 | 22.25 | 11.4167 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
N_BKHSF_44INV | 22 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 44. Constraint swamp out if number of inverter available not exceed 44. This is to manage voltage oscillation. DS only | Outage | NSW
T_TAMARCCGT_GCS | 21.9167 | 61.3333 | Tamar Valley 220 kV CCGT Generation Control Scheme (GCS) constraint to manage effective size of generation contingency for loss of Tamar CCGT. Limit output of Tamar CCGT based on load available and/or armed for shedding by Tamar GCS. | NIL | Tas
V::N_SMSC_xxx | 21.3333 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S_WATERLWF_RB | 21.25 | 16.8333 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | SA
TV_150 | 21.25 | 0 | Tas to Vic on Basslink upper limit of 150 MW | Outage | Tas
V:S_600_HY_TEST_DYN | 21 | 77 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
I_CTRL_ISSUE_TE | 20.9167 | 113.25 | DC Link Control Issue Constraint for Terranora | Outage | Other
N_BKHSF_30_44INV | 20.9167 | 0 | Limit Broken Hill Solar Farm upper limit to 30 MW with max 44 inverter available, upper limit set to 0 MW if number of inverter available exceed 44. This is to manage voltage oscillation | Outage | NSW
QNTE_OSCILLATE | 20.9167 | 4.8333 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Qld
T>T_NIL_BL_IMP_7CC | 20.6667 | 51.9167 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
N^^V_MSUT_1 | 20.3333 | 2.1667 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
Q^WOPW_CS_WOSP_O | 20.25 | 0 | Out= Any of the 275kV lines between Woolooga to South Pine (807,808 or 810),avoid voltage instability on CQSQ on trip of the remaining 275kV Parallel line lines between Woolooga to South Pine (807,808 or 810) (132kV and 110kV parallel network open) | Outage | Qld
V:S_600_HY_TEST | 20.0833 | 27.0833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
#V-SA_RAMP_I_F | 20 | 0.66667 | V-SA >= MIN(-110, InitialFlow + 50) (Wt=35) | Other | Quick
S>>PATW_BWPA_TPRS | 20 | 35.3333 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
#MACARTH1_E | 19.8333 | 0 | VTRT1M.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
S-TBTX4_TBSF1_80 | 19.6667 | 0 | Out =Tailem Bend 132/275 kV #4 Transformer O/S, constrain Tailem Bend (Coorong) Solar PV to 80 MW to manage voltage collapse for trip of Tailembend-Mobilong 132kV line | Outage | SA
T^V_NIL_9 | 19.5833 | 57.6667 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
Q_STR_233310_SMSF_38 | 19.4167 | 0 | Limit Sun Metal SF to 50% of max capacity (#38 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
#DARTM1_E | 19.25 | 0 | VDPS.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
Q_STR_233310_MEWF_39 | 19.0833 | 0 | Limit MT Emerald WF to 75% of max capacity (#39 turbine) if Kareeya > = 2 and Stanwell >= 3 and Callide >= 3 and Gladstone> = 3 and total of Stanwell, Callide and Gladstone >=10. Swamp during night. Limit to zero otherwise. | Outage | Qld
Q_CS_1600 | 19 | 0 | Qld Central to Qld South upper transfer limit of 1600MW (discretionary) | Outage | Qld
S>KNPW_SETX_SETX1 | 18.8333 | 0.25 | Out=Penola West-Kincraig 132kV line, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | Outage | SA
Q_STR_233310_HASF_40 | 18.75 | 0 | Limit Haughton SF to 50% of max capacity (#40 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
V_CWWF_GFT_5 | 18.5833 | 0 | Out= Crowlands WF associated fast tripping scheme (disabled), Limit Crowlands Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
Q_CLST_STRGTH_SMSF | 18.5 | 0 | Out = 855 or 8873 or 8874 or 856 or 8831, limit Sun Metals SF to 50% capacity (40 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=3 + Gladstone >=3 + (Stan+Cal+Glad >=10). Zero otherwise. | Outage | Qld
S>SE6161_SETX2_SGBL | 18.4167 | 66.9167 | Out= South East 132kV CB6161, avoid O/L Snuggery-Blanche 132kV line on trip of South East 132/275 TX2 ( this offloads Mayura-South East T 132kV line), Feedback | Outage | SA
QNTE_ROC | 18.25 | 71.1667 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
S>RB_275KV_N_BUS_1 | 18.25 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | SA
Q_CLST_STRGTH_HAUSF | 18.0833 | 0 | Out = 855 or 8873 or 8874 or 856 or 8831, limit Haughton SF to 50% capacity (40 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=3 + Gladstone >=3 + (Stan+Cal+Glad >=10). Zero otherwise. | Outage | Qld
V_MLMO_VS_LB_CAN_50 | 18.0833 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS/DUNDWF generating. | Outage | SA
Q_STR_43249_HASF_40 | 18 | 0 | Limit Haughton SF to 50% capacity (40 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=4 + (Stan+Cal+Glad >=9). Zero otherwise. | Outage | Qld
Q_STR_43249_SMSF_38 | 18 | 0 | Limit Sun Metals SF to 50% capacity (38 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=4 + (Stan+Cal+Glad >=9). Zero otherwise. | Outage | Qld
Q_STBS_STRGTH_MEWF | 17.8333 | 0 | Out = 856+822, limit Mt Emerald WF to 50% capacity (26 turbines) if Kareeya >=2 and Invicta is ON and Stanwell >=3 + Callide >=3 + Gladstone >=3 and Stan+Cal+Glad >=10 + Haughton >0 + Sun Metals >0. Zero otherwise. | Outage | Qld
V_KARSF_12INV | 17.6667 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out otherwise. This is to manage voltage oscillation. DS only | Outage | Vic
S>>MKRB_CNRB_WEMWP4 | 17.5833 | 14.1667 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage | SA
V_BANSF_22INV | 17.5833 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 22. Constraint swamp out if number of inverter available not exceed 22. This is to manage voltage oscillation. DS only | Outage | Vic
V_KARSF_20_8INV | 17.1667 | 0 | Limit Karadoc Solar Farm upper limit to 20 MW with max 8 inverter available, upper limit set to 0 MW if number of inverter available exceed 8. This is to manage voltage oscillation | Outage | Vic
V::N_NIL_xxx | 17.0833 | 269.6667 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL | Vic
#TORRA4_D_E | 17 | 0 | STSA4.ENERGY * 1 = 60 (Wt = 755) | Other | Direction
#GUTHEGA_E | 16.75 | 0 | NGUT8.ENERGY * 1 <= 22.5 (Wt = 360) | Other | Quick
V_CWWF_5 | 16.4167 | 0 | Crowlands Wind Farm total upper limit of 5 MW, limit to manage MW risk of islanding | Outage | Vic
V_GANWR_SF_BAT_50 | 16.4167 | 0 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Vic
N^^V_CNCW_1 | 16.3333 | 11.5833 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
S>NIL_NIL_SETX12 | 16.3333 | 5.6667 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
T::T_NIL_3 | 15.9167 | 2 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Tas
S>V_460 | 15.8333 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage | SA
V>>N-NIL_HG | 15.75 | 7.25 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
N_NIL_TE_B | 15.0833 | 12.5 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
S>>X_DVBR_BRTW_05 | 14.8333 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX), avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>NIL_HUWT_STBG2 | 14.8333 | 0.41667 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL | SA
V>>V_NIL_5 | 14.6667 | 2.25 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Vic
S>NWCB6024+25_TX3 | 14.3333 | 0 | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | SA
S>RB_275KV_S_BUS_9 | 14.3333 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage | SA
NC_Q_DAYDSF1 | 14.1667 | 0 | Non Conformance Constraint for DAYDREAM SOLAR FARM | Other | Non-Conformance
S_SECB_LG-2 | 13.6667 | 0 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 2 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
NSA_Q_GSTONE34_xxx | 13.5 | 0 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Qld
S>>X_CNRB+CB_04 | 13.3333 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 132/275kV TX2 on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
N_GUNNING1_ZERO | 12.8333 | 0 | Gunning unit upper limit of 0 MW | Outage | NSW
Q>EMBW_NIL_EMLV_DS | 12.5 | 0 | Out= 6056 or 6011 Emerald - Comet - Blackwater 66kV line ,limit Emerald SF to 40MW avoid overloading on Emerald - Lilyvale 66kV line, swap if Emerald CBs S612 or S610 or Blackwater CB S605 is closed (DS only) | NIL | Qld
Q>X_CPWO1_CPWU_CPWO2 | 12.5 | 0 | Out= Calliope River to Woolooga (813+815) line, avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (814) line, Feedback | Outage | Qld
#MORTLK12_E | 12.4167 | 0 | VM0P2O.ENERGY * 1 = 20 (Wt = 35) | Other | Quick
NQTE_ROC | 12.4167 | 74.25 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | NSW
Q_STR_43249_MEWF_26 | 12.3333 | 0 | Limit Mt Emerald WF to 50% capacity (26 turbines) if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=4 + (Stan+Cal+Glad >=9) + Haughton >0 + Sun Metals >0. Zero otherwise. | Outage | Qld
#DDSF1_E | 12.25 | 725.9167 | QBRS1D.ENERGY * 1 <= 87 (Wt = 360) | Other | Quick
#TORRB2_D_E | 12.25 | 0 | STSB2.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
N_WRWSF_055 | 12.0833 | 0 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | NSW
#NPS_P_E | 12 | 42.3333 | VNPS.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
V::N_KGRC_xxx | 12 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V_BANNERTSF_FLT_44 | 12 | 0 | Limit Bannerton Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | NIL | Vic
NRM_VIC1_NSW1 | 11.9167 | 0 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue
N>N-ARKS_TE_A1 | 11.75 | 0 | Out= Armidale to Kempsey (965), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
S>>PARB_RBTU_RBMWP4 | 11.75 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
V_WEMENSF_ZERO | 11.3333 | 0 | Wemen Solar Farm upper limit of 0 MW | Outage | Vic
N^^V_SMTXF2_1 | 11.1667 | 1.3333 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
V_ARARATWF_FLT_150 | 11.1667 | 0 | Limit Ararat Wind Farm upper limit to 150 MW to manage system stability on the next contingency | Outage | Vic
N_BKHSF_40INV | 11.0833 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 40. Constraint swamp out otherwise. DS only | Outage | NSW
T>>T_NIL_BL_EXP_7C | 11.0833 | 0.16667 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
#VIC1_E_20190303 | 10.75 | 0 | Multiple VIC1 LHS <= 680 (Wt = 35) | Other | Quick
T_LIPM1_SLOAD_1_N-2 | 10.75 | 0 | Out=Liapootah-Waddamana-Palmerston #1 220kV line and associated 220kV CBs at Waddamana I/S, loss of #2 parallel 220 kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Tas
V_GANWRSF_FLT_25 | 10.75 | 0 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | Vic
Q_STBS_STRGTH_HAUSF | 10.5 | 0 | Out = 856+822, limit Haughton SF to 50% of max capacity (40 inverters) if Kareeya >=2 and Invicta is ON and Stanwell >=3 + Callide >=3 + Gladstone >=3 and Stan+Cal+Glad >=10. Zero otherwise. | Outage | Qld
V^SML_ARWB_3 | 10.5 | 0 | Out = Ararat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
#LOYYB2_E | 10.4167 | 0 | VLYP6.ENERGY * 1 <= 580 (Wt = 360) | Other | Quick
V_MWWF_GFT_5 | 10.4167 | 0 | Out= Murra Warra WF associated fast tripping scheme (disabled), Limit Murra Warra Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
Q_STBS_STRGTH_SMSF | 10.3333 | 0 | Out = 856+822, limit Sun Metals SF to 50% of max capacity (38 inverters) if Kareeya >=2 and Invicta is ON and Stanwell >=3 + Callide >=3 + Gladstone >=3 and Stan+Cal+Glad >=10. Zero otherwise. | Outage | Qld
NQTE_-070 | 10.1667 | 1.25 | NSW to Qld on Terranora Interconnector upper transfer limit of -70 MW | Outage | NSW
V_GANNSF_30_12INV | 10 | 0 | Limit Gannawarra Solar Farm upper limit to 30 MW with max 12 inverter available, upper limit set to 0 MW if number of inverter available exceed 12. This is to manage voltage oscillation | Outage | Vic
#YWPS1_E | 9.9167 | 0 | VYP21.ENERGY * 1 <= 220 (Wt = 35) | Other | Quick
S>V_NWRB2_RBNW1 | 9.9167 | 0 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage | SA
V>V_NIL_7 | 9.9167 | 0 | Out = NIL, prevent overload of either MBTS-DDTS 220 kV line (flow north) for trip of the EPS-TTS 220 kV line, feedback. | NIL | Vic
#QPS5_P_E | 9.8333 | 70.75 | SQPS5Q.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
TVBL_ROC | 9.6667 | 7.4167 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Tas
VTBL_ROC | 9.6667 | 7.5833 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Vic
V_OWF_NRB_0 | 9.6667 | 4.8333 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Vic
#QPS5_O_E | 9.4167 | 70.5833 | SQPS5Q.ENERGY * 1 >= 74 (Wt = 755) | Other | Direction
V^SML_HORC_2 | 9.3333 | 0.25 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage | Vic
S>V_NWRB_RBMWP3 | 9.3333 | 0 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage | SA
V_KARADSF_FLT_25 | 9.3333 | 0 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | Vic
NRM_QLD1_NSW1 | 9.25 | 0 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue
Q_RRSF1_ZERO | 9.25 | 0 | Ross River solar farm upper limit of 0 MW | Outage | Qld
T>T_NIL_BL_IMP_7C | 9.25 | 11.9167 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Tas
V_HM_VIC_ZERO | 9.1667 | 0 | Hume VIC unit upper limit of 0 MW | Outage | Vic
I_CTRL_ISSUE_ML | 9.0833 | 0.58333 | DC Link Control Issue Constraint for Murraylink | Outage | Other
T_WIND_100 | 9.0833 | 0 | Limit output of TAS wind generation to less than 100 MW. Note, due to 144 MW rating of Non-Scheduled Woolnorth Wind Farm, directions may be required to reduce Woolnorth MW output if this constraint violates | Outage | Tas
V::N_HORC_xxx | 9 | 5.75 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#BW04_E | 8.9167 | 0 | NBAY4.ENERGY * 1 <= 450 (Wt = 360) | Other | Quick
T>T_NWSD_110_1 | 8.9167 | 0 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752, avoid O/L Scottsdale Tee to Norwood 110kV line on Nil trip, Feedback | Outage | Tas
S>NIL_BWMP_HUWT | 8.6667 | 1 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
N>Q_LSLS_9U8 | 8.5833 | 0 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 directlink cable O/S. | Outage | NSW
S>>X_RBTU+CB_2 | 8.4167 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) | Outage | SA
T_FASH_MAXGEN_1 | 8.3333 | 12.25 | Upper limit on Mackintosh + Bastyan + John Butters with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Tas
S>>X_RBPA+BGTX_04 | 8.25 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
Q_RGBYRSF1_ZERO | 8 | 0 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Qld
SVML_FLT_150 | 8 | 0 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | SA
NC_Q_SWAN_E | 7.9167 | 0.66667 | Non Conformance Constraint for Swanbank E Power Station | Other | Non-Conformance
S_PLN_ISL_01 | 7.9167 | 0 | Out = Cultana to Yadnarie (via Middleback Tee) 132kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
S_PLN_ISL_03 | 7.9167 | 0 | Out = Cultana to Yadnarie (via Middleback Tee) 132kV line, Port Lincoln unit #3 islanded | Outage | SA
N_WR_55_30WT-INV | 7.8333 | 0 | Limit White Rock wind/solar farm upper limit to 55 MW with max 30 wind turbine and inverter available, upper limit set to 0 MW if number of wind turbine + inverter available exceed 30. This is to manage low SCR. | Outage | NSW
T_T_FASH_7_N-2 | 7.8333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation <= 110% of West Coast load | Outage | Tas
T>T_BWLF_110_4 | 7.75 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana 110 kV line, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Tas
N>>N_65+66_N-2_2 | 7.5833 | 0 | Out= Nil, avoid O/L Dederang to Wodonga on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL | NSW
V>>V_NIL_3 | 7.4167 | 0.5 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL | Vic
NSA_V_BDL0xxx | 7.4167 | 4.25 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Vic
S_HPRG1_E | 7.3333 | 31.1667 | Out= Nil, Hornsdale Battery generation energy target <= 30 MW | NIL | SA
V_ARARATWF_ISL_0 | 7.3333 | 0 | Limit Ararat Wind Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Vic
N>N-LSTN_TE_C1 | 7.1667 | 0.16667 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
V::N_DDSM_xxx | 7.1667 | 1.5 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>V_NIL_8 | 7.1667 | 12 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL | Vic
V_CWWF_ISL_0 | 7.1667 | 0 | Crowlands Wind Farm total upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
NC_S_CLEMGPWF | 6.9167 | 0 | Non Conformance Constraint for Clements Gap Wind Farm | Other | Non-Conformance
Q_STR_43239_HASF_40 | 6.8333 | 0 | Limit Haughton SF to 50% capacity (40 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=3 + (Stan+Cal+Glad >=9). Zero otherwise. | Outage | Qld
T>T_FASH_1_N-2 | 6.6667 | 10.9167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, limit Bastyan, John Butters & Mackintosh to west coast load plus Hampshire link line rating | Outage | Tas
V^SML_NSWRB_2 | 6.5833 | 58.5 | Out = NSW Murraylink runback scheme, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | NIL | Vic
NQTE_-050 | 6.5 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -50 MW | Outage | NSW
N>N-NIL_TE_E1 | 6.3333 | 0 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST | NIL | NSW
S-SNWWF_0 | 6.25 | 0 | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
S>X_DV-BR-PA_08 | 6.25 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Hummocks-Waterloo 132kV lineon trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T_V_NIL_BL1 | 6.0833 | 5 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL | Tas
V:T_NIL_BL_1 | 6.0833 | 2.8333 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL | Vic
#KARSF1_E | 6 | 189.25 | VRCS1K.ENERGY * 1 <= 90 (Wt = 360) | Other | Quick
Q^^CS_-240 | 5.9167 | 0 | Nominated Offset -240MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage | Qld
S>>TBTU_CGTB_MOTB | 5.9167 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of Cherry Gardens-Tailem Bend 275kV line, Feedback | Outage | SA
S_CNLK_270 | 5.9167 | 0 | Out =Canowie-Mt Lock 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3 + Hornsdale battery (i.e. generation + load component)<= 270 MW | Outage | SA
V>>V_BUDP_6 | 5.9167 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Vic
T^V_NIL_8 | 5.8333 | 43 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
T_FASH_MAXGEN_2 | 5.75 | 0 | Upper limit on West Coast generation to maintain transient stability, West Coast 220/110 kV parallel closed, Farrell 220 kV bus NOT split, constraint swamped if only one machine on line | Outage | Tas
V_BANNERTON_ZERO | 5.75 | 16.3333 | Bannerton Solar Farm upper limit of 0 MW | Outage | Vic
N^^V_DDWG | 5.6667 | 3.6667 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
Q::N_ARSVC_AR_2L-G | 5.6667 | 14.5833 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
S:V_PA_SVC_420 | 5.6667 | 1.8333 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | SA
#HALLWF2_E | 5.5833 | 0 | SMOK1H.ENERGY * 1 <= 55 (Wt = 360) | Other | Quick
#WEMENSF1_E | 5.5833 | 108.5 | VWES2W.ENERGY * 1 <= 43 (Wt = 360) | Other | Quick
NC_Q_HAYMSF1 | 5.5833 | 0 | Non Conformance Constraint for HAYMAN SOLAR FARM | Other | Non-Conformance
N^^V_LTWG_1 | 5.5 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
N>N-ARKS_GITN_1 | 5.4167 | 0 | Out= Armidale to Kempsey (965) and Glen Innes to Tenterfield (96R) avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 Directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
T::T_HA_GT_PM_4 | 5.4167 | 9.1667 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Tas
V>SMLARHO1 | 5.4167 | 49 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
N^^V_GRYS_1 | 5.1667 | 0 | Out = Gullen Range to Yass (3J), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
T^V_NIL_11 | 5.1667 | 70.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
NC_N_GULLRSF1 | 5.0833 | 0 | Non Conformance Constraint for Gullen Range Solar Farm | Other | Non-Conformance
N_GULLRWF1_ZERO | 5.0833 | 0 | Gullen Range WF upper limit of 0 MW | Outage | NSW
T_ROCOF_1 | 5.0833 | 25.3333 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL | Tas
V>>V_KGWT_3 | 5.0833 | 0 | Out= Kerang to Wemen 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Balranald to Darlington Point (X5) 220kV line, Feedback | Outage | Vic
#LKBONNY2_E | 4.9167 | 0 | SMAY2.ENERGY * 1 <= 132 (Wt = 360) | Other | Quick
#MEWF1_E | 4.9167 | 271.1667 | QWKM1M.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
V^SML_KGRC_4 | 4.9167 | 1.5 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Vic
N_SILVERWF_WT | 4.8333 | 0.25 | Limit number of turbine online for Silverton wind farm to not exceed 38 with Broken Hill solar generating | Outage | NSW
SA_ISLE_STRENGTH_LB | 4.8333 | 0 | Maximum limit (0 MW) for Lake Bonney and Canunda Wind Farm for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
#OSB-AG_D_E | 4.75 | 0 | SNBN1.ENERGY * 1 = 155 (Wt = 755) | Other | Direction
S>>CNLK_MKRB_WEMWP4 | 4.75 | 0 | Out= Canowie-Mt Lock 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV on trip of Mokota-Robertstown 275kV line( this offloads Belalie-Mokota 275kV line and trips Hallet Hill WF), Feedback | Outage | SA
N_FINLYSF1_ZERO | 4.6667 | 0 | Finley solar farm upper limit of 0 MW | Outage | NSW
V::S_NIL_MAXG_xxx | 4.6667 | 15.6667 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
V_SALTCREEK_ZERO | 4.6667 | 0 | Salt Creek wind farm upper limit of 0 MW | Outage | Vic
V>SMLMHNW1 | 4.5833 | 0 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Vic
V_KARADSF_FLT_45 | 4.5833 | 0 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
NSA_V_NPSD_100 | 4.4167 | 0 | Newport unit >= 100 MW for Network Support Agreement | Outage | Vic
S>>X_MKRB+WTTP_14 | 4.4167 | 0 | Mokota - Robertstown 275kV line(i.e. Line ONLY O/S, line CBs I/S) + Waterloo-Templers 132kV line O/S, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kVline (this trips Hallet GT + WF), Feedback | Outage | SA
V_BANNERTSF_ISL_0 | 4.4167 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Vic
S_LB2WF_CONF | 4.3333 | 0.66667 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
S_NBH_0 | 4.3333 | 0 | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | SA
T>T_TU_LE_WA12_2 | 4.3333 | 0 | Out = either Tungatinah to Waddamana 110kV line (direct or via Lake Echo tee), avoid O/L the remaining Tungatinah to Waddamana 110 kV line (flow to North) on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, feedback | Outage | Tas
V>>V_KTS_TX_A2_2A_R | 4.3333 | 1.75 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
V>V_NIL_8 | 4.3333 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Vic
V>>V_KTS_TX_A3_2A_R | 4.25 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
N>>N-NIL_1G | 4.1667 | 0 | Out= Nil, avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22) line, Feedback | NIL | NSW
T>T_GTSH_IMP_4K | 4.1667 | 3.25 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
V_MURRAWRWF_30WT | 4.1667 | 0 | Limit Murra Warra Wind Farm upper limit to 0 MW if number of turbine ON exceed 30. Constraint swamp out if number of turbine ON not exceed 30. This is to manage voltage oscillation. DS only | Outage | Vic
S>NIL_LKDV_CNRB | 4.0833 | 0.083333 | Out= NIL, avoid O/L Canowi-Robertstown 275kV on trip of Mt Lock-Davenport 275kV line, Feedback | NIL | SA
V^^S_NIL_MAXG_xxx | 4.0833 | 9.4167 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
N>N-FLML_9R4 | 4 | 0 | Out= Finley to Mulwala (9R4) or Mulwala to Corowa(997/2) or Corowa to Albury (997/1), avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | Outage | NSW
S>NWBCB6025_TX2 | 4 | 0 | Out= North West Bend 132kV CB6025 , avoid O/L of North West Bend 132/66kV TX2 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage | SA
V::N_X_DDSM_SMSC_xxx | 4 | 0 | Out = one Dederang to South Morang 330kV line AND series capbank on the parallel line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
N>>N-964_DC | 3.9167 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage | NSW
S>>NIL_TBTU_TBMO_1 | 3.9167 | 0 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
S>X_RBPA+CB_06 | 3.9167 | 0.75 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV #1 transformer on trip of Canowie-Robertstown(this this trips Hallet WF and Generation and splits Robertstown 275kV bus), Feedback | Outage | SA
T_T_BA_JB_RC2_250 | 3.9167 | 20 | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
#NPS_O_E | 3.8333 | 19.0833 | VNPS.ENERGY * 1 >= 100 (Wt = 65) | Other | Direction
T_V_NIL_FCSPS | 3.8333 | 2.9167 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
V::N_SMF2_xxx | 3.8333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V_KARSF_21INV | 3.8333 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 21. Constraint swamp out if number of inverter available not exceed 21. This is to manage voltage oscillation. DS only | Outage | Vic
SA_ISLE_STRENGTH | 3.75 | 0 | Maximum limit (1300 MW) for SA non-synchronous generation for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
#CPP_3_E | 3.75 | 0 | QCAC3.ENERGY * 1 <= 420 (Wt = 360) | Other | Quick
#MTGELWF1_E | 3.75 | 0.58333 | VGTW1M.ENERGY * 1 <= 66 (Wt = 360) | Other | Quick
QNI_SOUTH_1150_DYN | 3.75 | 0 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL | Qld
S-DLBAT-G_0 | 3.75 | 0 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW | Outage | SA
S_WIMK_270 | 3.6667 | 0 | Out =Willalo-Mokota 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF <= 270 MW | Outage | SA
T_T_FASH_1_N-2 | 3.6667 | 6.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
VSML_220 | 3.5833 | 25 | Vic to SA on ML upper transfer limit of 220 MW | NIL | Vic
NC_S_PPCCGT | 3.5 | 0.5 | Non Conformance Constraint for Pelican Point Power Station | Other | Non-Conformance
S^NIL_PL_MAX | 3.5 | 9.4167 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
VT_050 | 3.5 | 0 | Vic to Tas on Basslink upper limit of 50 MW | Outage | Vic
V_BANSF_20INV | 3.5 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 20. Constraint swamp out otherwise. DS only | Outage | Vic
Q>>CLWU_BCRG_BCCP | 3.4167 | 0 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811), Feedback | Outage | Qld
N>>V-NIL_HJ | 3.3333 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) O/L on Nil trip; Feedback | NIL | NSW
Q_STR_43239_MEWF_26D | 3.3333 | 0 | Limit Mt Emerald WF to 50% capacity (26 turbines) if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=3 + (Stan+Cal+Glad >=9) + Haughton >0 + Sun Metals >0. Zero otherwise. | Outage | Qld
T>T_BUSH1_220 | 3.3333 | 0 | Out = Burnie to Sheffield 220kV line, West Coast 220/110 kV parallel open, avoid O/L a Sheffield 220/110kV transformer for loss of the other Sheffield 220/110kV transformer | Outage | Tas
V_MWWF_5 | 3.3333 | 0 | Murra Warra Wind Farm upper limit of 5 MW | Outage | Vic
#STAN-1_E | 3.1667 | 0 | QSTN1.ENERGY * 1 <= 385 (Wt = 360) | Other | Quick
V_ARARAT_ZERO | 3.1667 | 3.6667 | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
#LKBONNY3_E | 3.0833 | 0 | SMAY3W.ENERGY * 1 <= 32 (Wt = 360) | Other | Quick
N_MBTE1_A | 3.0833 | 1 | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
S>>MKRB_NIL_WEMWP4 | 3.0833 | 1.0833 | Out= Mokota-Robertstown 275kV line,, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
T_LIPM_PMWA_2_N-3 | 3.0833 | 0 | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to >= southern load - 15 MW | Outage | Tas
V>>V-LTWG_RADIAL_2 | 3.0833 | 0 | Outage = Lower Tumut to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload Murray to Dederang No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings; Feedback | Outage | Vic
V_GANWR_BAT_G_FLT_0 | 3.0833 | 0 | Limit Gannawarra Battery (Generation Component) upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
#DG_SA1_O_E | 3 | 0 | SDNSG.ENERGY * 1 = 0 (Wt = 1145) | Other | Direction
#DG_SA1_P_E | 3 | 0 | SDNSG.ENERGY * 1 = 20 (Wt = 1140) | Other | Direction
#MINTARO_P_E | 3 | 0 | SMPS.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
NC_Q_CHILDSF1 | 3 | 0 | Non Conformance Constraint for CHILDERS SF 1 | Other | Non-Conformance
SA_HYSE1 | 3 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage | SA
S>>X_RBPA+BGTX_05 | 2.9167 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
Q>>BCCP_CLWU_RGLC_2 | 2.8333 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
S>LFTI_PPPW_NOTI4 | 2.8333 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L New Osborne-TIPS #4 66kV line, on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | Constraint Automation - RT
#MINTARO_O_E | 2.75 | 0 | SMPS.ENERGY * 1 >= 30 (Wt = 65) | Other | Direction
NC_Q_WHITSF1 | 2.75 | 0 | Non Conformance Constraint for WHITSUNDAY SF | Other | Non-Conformance
NRM_NSW1_VIC1 | 2.75 | 2.5 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue
N_BKHSF_40INV | 2.75 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 40. Constraint swamp out otherwise. DS only | NIL | NSW
Q>>WOSP_WOPW_WOGP_2 | 2.75 | 0 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Qld
S:V_580 | 2.75 | 0 | Out = One Heywood 500/275 kV txfmr (two remain in service), maintain maximum SA to VIC transfer limit of 580 MW on Heywood and Murraylink combined to avoid oscillatory instability | Outage | SA
T^^V_GTSH_1 | 2.75 | 8.8333 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
V::N_KTSY_xxx | 2.75 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>SMLARHO4 | 2.75 | 0.083333 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
V_KARSF_19INV | 2.75 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | Outage | Vic
V_KARSF_19INV | 2.75 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | NIL | Vic
S>>NIL_RBTU_WEWT | 2.6667 | 0.25 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | SA
S>PATW_BWPA_HUWT | 2.6667 | 1.0833 | Out= Para-Templers West 275kV line, avoid O/L Hummocks- Waterloo132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S_SECB_LG3 | 2.6667 | 1.25 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
V::N_BYPASS_HW_SY_xxx | 2.6667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
CA_MQS_4C1211CB_02 | 2.5833 | 0 | Constraint Automation, O/L WATTEM_1 @W_LOO for CTG LSIT on trip of R_TOWN - PARA 275KV LINE. Generated by STNET[MANFL] Host MANEEMP1(MQ) | Outage | Constraint Automation
S_WTE_0 | 2.5833 | 0 | Discretionary upper limit for Waterloo generation of 0 MW | Outage | SA
T>T_TUMBNN1_110_3 | 2.5833 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line, avoid O/L Tungatinah to New Norfolk 110kV line on trip of Tungatinah to Meadowbank to New Norfolk No.2 110kV line, Feedback | Outage | Tas
S>>X_MKRB+WTTP_06 | 2.5 | 0 | Out= Mokota-Robertstown 275kV line (note:associated line CBs assumed I/S) + Waterloo-Templers 132kV line, avoid O/L Waterloo East-MWp4-Robertstown 132kV line on trip Nil trip, Feedback | Outage | SA
S>BRTW_BWPA_HUWT | 2.5 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S_PWSE_LG1 | 2.5 | 0 | Out=Penola West-South East 132kV line, Oscillatory stability limit Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
CA_MQS_4C1211CB_01 | 2.4167 | 0 | Constraint Automation, O/L R_TOWN TRANSF T_1 for CTG LSIT on trip of R_TOWN - PARA 275KV LINE. Generated by STNET[MANFL] Host MANEEMP1(MQ) | Outage | Constraint Automation
S>LFTI_PPPW_LFTX5 | 2.4167 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L LeFevre 275/132kV TX5 on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | SA
T::T_GTSH_2 | 2.4167 | 0 | Out = George Town to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage | Tas
V_BANNERTSF_FLT_45 | 2.4167 | 0 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
V_WEMENSF_FLT_44 | 2.4167 | 0 | Limit Wemen Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | Outage | Vic
#DRYCGT1_O_E | 2.3333 | 0 | SDCA1.ENERGY * 1 >= 30 (Wt = 65) | Other | Direction
#DRYCGT1_P_E | 2.3333 | 0 | SDCA1.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
N>N-GITN_TE_C1 | 2.3333 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
N_MBTE110_B | 2.3333 | 0 | Qld to NSW on Directlink upper transfer limit of -110 MW | Outage | NSW
#DRYCGT2_O_E | 2.25 | 0 | SDCA2.ENERGY * 1 >= 30 (Wt = 65) | Other | Direction
#DRYCGT2_P_E | 2.25 | 0 | SDCA2.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#DRYCGT3_O_E | 2.25 | 0 | SDCA3.ENERGY * 1 >= 30 (Wt = 65) | Other | Direction
#DRYCGT3_P_E | 2.25 | 0 | SDCA3.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
Q_NESTM_STRGTH_MEWF | 2.25 | 0 | Out = 822, Limit MT Emerald WF to 75% of max capacity (#40 turbine) if Kareeya > = 2 and Stanwell >= 3 and Callide >= 3 and Gladstone> = 3 and total of Stanwell, Callide and Gladstone >=10. Limit to zero otherwise. Swamp if Sun Metal+Haughton =0. | Outage | Qld
Q_NESTM_STRGTH_SMSF | 2.25 | 0 | Out = 822, Limit Sun Metal SF to 50% of max capacity (#38 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
S-BUPV1_0 | 2.25 | 3.6667 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | SA
S::V_PWSE_TBSE_2 | 2.25 | 0 | Out = Penola West - South East #1 132KV line (NOTE: with both Black Range series capacitors O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | SA
S>>X_RBTU+CB_7 | 2.25 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, avoid O/L Robertstown 275/132kV #1 transformer on trip of Robertstown - Para line (this offloads Robertstown TX#2 132/275kV ) | Outage | SA
V_GANWR_BAT_G_ISL_0 | 2.25 | 0 | Gannawarra Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
#NSW1-QLD1_RAMP_I_F | 2.1667 | 4.4167 | NSW1-QLD1 >= MIN(-76, InitialFlow + 200) (Wt=35) | Other | Quick
N>N-96H+96R_TE_1 | 2.1667 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage | NSW
NC_S_LKBONNY2 | 2.1667 | 0 | Non Conformance Constraint for Lake Bonney 2 Windfarm | Other | Non-Conformance
NC_S_LKBONNY3 | 2.1667 | 0 | Non Conformance Constraint for Lake Bonney 3 Windfarm | Other | Non-Conformance
Q>>BCCP_CLWU_LCCP_2 | 2.1667 | 2.25 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
S>X_RBPA+CB_01 | 2.1667 | 12.8333 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
T>T_NIL_BL_3C | 2.1667 | 5.4167 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
Q^^TR_CLHA_-250 | 2.1667 | 0 | Nominated offset -250 MW, Tarong voltage stability limit, Calvale-Halys contingency equation | Outage | Qld
V_MURRAWRWF_FLT_90 | 2.1667 | 0 | Limit Murra Warra Wind Farm upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | Vic
Q_HAMISF1_ZERO | 2.0833 | 0 | Hamilton solar farm upper limit of 0 MW | Outage | Qld
Q_WHITSF1_ZERO | 2.0833 | 0 | Whitsunday solar farm upper limit of 0 MW | Outage | Qld
S>>RBTU_RBPA_WEWT | 2.0833 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
S_TBL_0 | 2.0833 | 0 | Discretionary upper limit for The Bluff generation of 0 MW | Outage | SA
NC_V_GANNSF1 | 2 | 0 | Non Conformance Constraint for GANNAWARRA SOLAR | Other | Non-Conformance
N_FINLEYSF_49_INV | 2 | 0 | Limit Finley Solar Farm upper limit to 0 MW if number of inverter available exceed 49. Dispatch only. swamped out if Inverters are within the limit. | Outage | NSW
S_PW-CB6156_LG1 | 2 | 15.4167 | Out=Penola West 132kV CB 6156 O/S (Note: with Penola West 132kV CB 6158 CLOSED), Oscillatory stability limit Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
V>>N-MSUT_4 | 2 | 0 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Vic
CA_MQS_4C6B1A92_01 | 1.9167 | 0 | Constraint Automation, O/L N_W_B TRANSF T_1 for CTG LS5K on trip of R_TOWN-N_W_B132KV 2LN VIA1 2&3MWPS. Generated by STNET[MANFL] Host MANEEMP2(MQ) | Outage | Constraint Automation
NC_V_YWPS3 | 1.9167 | 0.83333 | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Other | Non-Conformance
N_TARALGAWF_ZERO | 1.9167 | 0 | Taralga WF upper limit of 0 MW | Outage | NSW
Q_CS_1750 | 1.9167 | 5.3333 | Qld Central to Qld South upper transfer limit of 1750MW (discretionary) | Outage | Qld
V_VS_MLMO_NETT | 1.9167 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage | Vic
#TARONG#4_E | 1.8333 | 0 | QTRN4.ENERGY * 1 <= 245 (Wt = 360) | Other | Quick
N>>N-SNVP_03 | 1.8333 | 0 | Out = SydneyNorth-ValesPoint(22), avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25) line, Feedback | Outage | NSW
NC_N_VP5 | 1.8333 | 11.4167 | Non Conformance Constraint for Vales Point VP5 Power Station | Other | Non-Conformance
SA_HYSE2 | 1.8333 | 0.41667 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage | SA
S_LB_1+2+3_110 | 1.8333 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=110 MW | Outage | SA
V>>V_LTMS_1 | 1.8333 | 0 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage | Vic
Q>NIL_SRMB_M020/1 | 1.75 | 0 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Qld
Q_HASMME_RAMP_ZERO | 1.75 | 0 | Ramp Haughton, Sun Metals and Mt Emerald generators to zero and hold at zero. | Outage | Qld
S>>BG6246_BGPR_HUWT | 1.75 | 4.1667 | Out= Bungama 132kV CB6246, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Port Pirie 132kV line (this offloads Snowtown-Bungama 132kV line), Feedback | Outage | SA
N>N-FLUR_99A | 1.6667 | 0 | Out= Finley to Uranquinty (99A), avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | Outage | NSW
Q::N_DM_CB_AR_2L-G | 1.6667 | 0 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
Q_STR_233310_SMSF_76 | 1.6667 | 0 | Limit Sun metal SF to 100% of max capacity (#76 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
NC_Q_STAN-1 | 1.5833 | 0.83333 | Non Conformance Constraint for Stanwell STAN-1 Power Station | Other | Non-Conformance
Q^^N_AR_SVC_1 | 1.5833 | 0 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Qld
S>LFTI_PPPW_LFTX4 | 1.5833 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L LeFevre 275/132kV TX4 on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | SA
S>NIL_NIL_SGBN | 1.5833 | 1.4167 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | SA
S_LBMY_2B-LB3 | 1.5833 | 0 | Out= Mayurra-Lake Bonney WF 2B 33kV line (OR Mayura CB4565 and CB4674 OPEN), Lake Bonney 3 constrained to 0 MW | Outage | SA
T>T_FASH_1_2_C1 | 1.5833 | 15.8333 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, West Coast 220/110 kV parallel closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
V_GANNSF_11INV | 1.5833 | 0 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Constraint swamp out otherwise. DS only | Outage | Vic
Q_STR_033310_MEMF_26 | 1.5 | 0 | Limit Mt Emerald WF to 50% capacity (26 turbines) if Kareeya < 2 + Stanwell >= 3 + Callide >=3 + Gladstone >= 3 and (Stan+Cal+Glad) >=10, Swamp if Kar >= 2 + Stan >= 3 + Cal >= 3 + Glad >= 3 and (Stan+Cal+Glad) >=10. Zero otherwise. Swamp during night. | NIL | Qld
S>>PATW_NIL_WEMWP4 | 1.5 | 1.1667 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
S>NWBCB6225_TX1 | 1.5 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 66/132kV TX1 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage | SA
S_SECB_LG-1 | 1.5 | 4.0833 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
T>T_PMWA_110_7 | 1.5 | 0.083333 | Out= Palmerston to Waddamana 110 kV line, avoid overloading the New Norfolk to Chapel St 110 kV line (flow to South) on trip of New Norfolk to Creek Road 110 kV line, feedback | Outage | Tas
V>>N-JNWO_RADIAL_2 | 1.5 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Vic
#N-Q-MNSP1_E_E | 1.4167 | 6.0833 | N-Q-MNSP1.ENERGY * 1 <= 100 (Wt = 35) | Other | Quick
N>>N-NIL__3_OPENED & CLOSED | 1.4167 | 15.9167 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
N>>V-LTMS_5 | 1.4167 | 0.91667 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L(15m rating) on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage | NSW
NC_Q_BRAEMAR3 | 1.4167 | 0.75 | Non Conformance Constraint for Braemar 3 Power Station | Other | Non-Conformance
NC_V_GANNBG1 | 1.4167 | 0.083333 | Non Conformance Constraint for GANNAWARRA BATT GEN | Other | Non-Conformance
Q_STR_233310_CSF_69 | 1.4167 | 0 | Limit Clare SF to 100% of max capacity (#69 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
S-WIWF_0 | 1.4167 | 0 | Discretionary upper limit for Willogolechi WF generation of 0 MW | Outage | SA
VSML_-050 | 1.4167 | 0 | Vic to SA on ML upper transfer limit of -50 MW | Outage | Vic
V_GANNSF_12INV | 1.4167 | 0 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out if number of inverter available not exceed 12. This is to manage voltage oscillation. DS only | Outage | Vic
NC_S_LGAPWF1 | 1.3333 | 0 | Non Conformance Constraint for Lincoln Gap Wind Farm | Other | Non-Conformance
NQTE_-090 | 1.3333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -90 MW | Outage | NSW
Q_NIL_STRGTH_HAUSF | 1.3333 | 0 | Out = Nil, limit Haughton SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to TOA 393 | NIL | Qld
Q_STR_033310_MEWF_26 | 1.3333 | 0 | Limit Mt Emerald WF to 50% capacity(26 turbines)day or 75%(39 turbine)night if Kar < 2 +Stan >= 3 + Cal >=3 + Glads>= 3 and (Stan+Cal+Glad) >=10, 75% day(swamp night )if Kar >= 2+Stan >= 3 + Cal >= 3 + Glad >= 3 and (Stan+Cal+Glad) >=10. Zero otherwise. | Outage | Qld
S>>X_DVLK+LKCN_02 | 1.3333 | 0 | Out= Davenport-Mt Lock-Canowie 275kV line (this offloads Hornsdale #1 & #2 &#3 WF & battery) OR Davenport-Mt Lock 275kV line O/S, avoid O/L Waterloo East-Waterloo 132kV line on trip of Belalie-Davenport 275kV line, Feedback | Outage | SA
V_MB_BUS2 | 1.3333 | 0 | Dartmouth PS upper limit set to zero due to outage of Mt Beauty No 2 220 kV Bus | Outage | Vic
N>>V-MSUT_5 | 1.25 | 0 | Out= Murray-UpperTumut(65), avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage | NSW
NC_Q_TARONG#1 | 1.25 | 0.58333 | Non Conformance Constraint for Tarong 1 Power Station | Other | Non-Conformance
N_WRWSF_ZERO | 1.25 | 0 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | NSW
S_HPRL1_E | 1.25 | 4.3333 | Out= Nil, Hornsdale Battery load energy target <= 40 MW | NIL | SA
V>>V-MSUT_1 | 1.25 | 5.1667 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback | Outage | Vic
V_WEMENSF_FLT_45 | 1.25 | 0 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
#WRWF1_E | 1.1667 | 50.5 | NWRK1W.ENERGY * 1 <= 35 (Wt = 360) | Other | Quick
Q>NIL_TV66 | 1.1667 | 0 | Out=Nil, limit Sun metals SF and Mt Stuart GTs to avoid over load on 66kV feeders on trip of one of the 66kV feeders in the Townsville area | NIL | Qld
S-LB2_0 | 1.1667 | 0.16667 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | SA
S>KNPW_NIL_SETX12 | 1.1667 | 0.16667 | Out=Penola West-Kincraig 132kV line, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
V::S_PATU_MAXG_2 | 1.1667 | 0 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
V>>DDSH_DDGN_N-2 | 1.1667 | 1.0833 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage | Vic
V>>SML_NSWRB_11 | 1.1667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Wemen to Red Cliffs 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL | Vic
V>>V_NIL_9 | 1.1667 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Vic
N_COLMBSF_60_INV | 1.1667 | 0 | Limit Coleambally Solar Farm upper limit to 0 MW if number of inverter available exceed 60. Dispatch only. swamped out if Inverters are within the limit. | Outage | NSW
S>>X_RBTU_CB_3 | 1.1667 | 0 | Out= Robertstown-Tungkillo 275kV line& RB 275kV CBs 6571 & 6572 O/S, avoid O/L Waterloo East-MWP4-RB 132kV line on trip of Mokota-Robertstown 275kV line(trips Willalo-Mokota 275kV line and Hallet Hill WF. The contingency SPLITS Robertstown bus) | Outage | SA
N>>N-X_AVMA_KCTX_11 | 1.0833 | 0 | Out= Avon to Macarthur (17) 330kV line and Kemps Creek No.2 or No.3 500/330kV transformer , avoid O/L Vales Point to Munmorah (23) on trip of remaining Kemps Creek transformer, Feedback | Outage | NSW
NC_Q_BRAEMAR6 | 1.0833 | 0 | Non Conformance Constraint for Braemar 6 Power Station | Other | Non-Conformance
NC_Q_SRSF1 | 1.0833 | 0 | Non Conformance Constraint for SUSANRIVERSOLARFARM | Other | Non-Conformance
NC_S_BARKIPS1 | 1.0833 | 0 | Non Conformance Constraint for BARKER INLET PS | Other | Non-Conformance
NV_0000 | 1.0833 | 0 | Discretionary NSW to Vic transfer upper limit of 0 MW | Outage | NSW
S>NIL_PL_GENMAX_YDMD | 1.0833 | 0 | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating. | NIL | SA
S_PWSE_LG3 | 1.0833 | 0 | Out=Penola West-South East 132kV line, Oscillatory stability limit max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
T>>T_GTSH_EXP_3H | 1.0833 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage | Tas
T_LIPM2_SLOAD_1_N-2 | 1.0833 | 0 | Out=Liapootah-Waddamana-Palmerston #2 220kV line and associated CBs at Waddamana I/S, loss of the #1 parallel 220kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Tas
V:T_SHGT_BL_1 | 1.0833 | 0 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
NC_N_WRSF1 | 1 | 0 | Non Conformance Constraint for WHITE ROCK SOLAR | Other | Non-Conformance
NC_Q_HAMISF1 | 1 | 1.8333 | Non Conformance Constraint for HAMILTON SOLAR FARM | Other | Non-Conformance
QN_1000 | 1 | 0 | Qld to NSW on QNI upper transfer limit of 1000 MW | Outage | Qld
QN_950 | 1 | 0 | Qld to NSW on QNI upper transfer limit of 950 MW | Outage | Qld
S>>RBTU_TWPA_TPRS | 1 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
V::S_PATU_MAXG | 1 | 0 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
V>V_WETS_BTX_1 | 1 | 0 | Out = Wemen 220/66kV B1 or B2 txfmr, prevent pre-contingent overload the remaining Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback. | Outage | Vic
V_BROKENHSF_FLT_0 | 1 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V_GANNSF_11INV | 1 | 0 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Constraint swamp out otherwise. DS only | NIL | Vic
V_MTGBRAND_33WT | 1 | 0.083333 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 33 | Outage | Vic
V_WEMENSF_19INV | 1 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | Outage | Vic
#FINLYSF1_E | 0.91667 | 0 | NFNS1F.ENERGY * 1 <= 90 (Wt = 360) | Other | Quick
CA_SPS_4B902E2A_01 | 0.91667 | 0 | Constraint Automation, O/L 9U7/M @MULLUMB for CTG LNYI on trip of 9G5 EWINGSDL-MULLUMB 132KV LINE. Generated by STNET[NORFR] Host NOREEMP3(SP) | Outage | Constraint Automation
NC_N_VP6 | 0.91667 | 4.6667 | Non Conformance Constraint for Vales Point VP6 Power Station | Other | Non-Conformance
NC_Q_BARRON-2 | 0.91667 | 0.25 | Non Conformance Constraint for Barron Gorge 2 Power Station | Other | Non-Conformance
NC_V_YWPS2 | 0.91667 | 2.1667 | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Other | Non-Conformance
N^N-X_96H_LS_SVC | 0.91667 | 0 | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Coffs Harbour to Lismore (89) trip; TG formulation only | Outage | NSW
Q_CS_1650 | 0.91667 | 0 | Qld Central to Qld South upper transfer limit of 1650MW (discretionary) | Outage | Qld
S^DVBR_SA_NTH | 0.91667 | 0 | Out = Davenport-Brinkworth 275kV line, Manage voltage collapse in northern SA for the trip of Davenport-Belalie 275kV line | Outage | SA
T_FARC1 | 0.91667 | 0.083333 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Tas
V::N_EPMB_xxx | 0.91667 | 6.3333 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>V_NIL_1A | 0.91667 | 9.1667 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
V_BANNERTSF_FLT_44 | 0.91667 | 0 | Limit Bannerton Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | Outage | Vic
V_WEMENSF_19INV | 0.91667 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | NIL | Vic
V_WEMENSF_21INV | 0.91667 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 21. Constraint swamp out if number of inverter available not exceed 21. This is to manage voltage oscillation. DS only | Outage | Vic
#V-SA_RAMP_E_F | 0.83333 | 0 | V-SA <= MAX(49, InitialFlow - 30) (Wt=35) | Other | Quick
N>>N-KVCW_10_15M | 0.83333 | 0 | Out = KangarooValley-Capital(3W), avoid O/L Canberra to Yass (9) on trip of Lower Tumut to Yass (3) line, Feedback | Outage | NSW
N>>V-NIL_O | 0.83333 | 21.75 | Out = Nil, avoid overloading Upper Tumut to Murray (65) using 15 mins rating line on trip of Lower Tumut to Wagga (051) + 970,990,99M (out of Yass) line, Feedback | NIL | NSW
N>N_LSDU_9U6_2 | 0.83333 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage | NSW
NC_N_TALWA1 | 0.83333 | 0.91667 | Non Conformance Constraint for Tallawarra Power Station | Other | Non-Conformance
N^N_KKLS_1 | 0.83333 | 20.1667 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | NSW
Q>N-MUTE_758 | 0.83333 | 47.8333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
S>>BRTW_BWPA_WTTP | 0.83333 | 0.16667 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>>CNRB_BWPA_HUWT | 0.83333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>>NIL_BWMP_TWPA | 0.83333 | 0 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | SA
S>X_DV-BR-PA_12 | 0.83333 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Mokota-Robertstown 275kV line on trip of Canowi-Robertstown 275kV line(this trips Hallet WF and GT) | Outage | SA
S_PWSE_LG2 | 0.83333 | 0 | Out=Penola West-South East 132kV line, Oscillatory stability limit Ladbroke Grove 2 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
T>T_CRNN_3 | 0.83333 | 0 | Out= Creek Rd to New Norfolk 110 kV line, avoid O/L New Norfolk to Chapel St 110 kV line for loss of Waddamana to Palmerston 110 kV line, Feedback | Outage | Tas
T_LIPM_SLOAD_1_N-2 | 0.83333 | 0 | Out=Liapootah-Waddamana-Palmerston 220kV line, loss of the remaining Liapootah to Waddamana to Palmerston 220kV line and 133 MW South load declared credible, limit Sth to Nth flow to rating of Palmerston-Waddamana 110kV line minus 133 MW, feedback | Outage | Tas
#WGWF1_E | 0.75 | 0.16667 | SWGL1W.ENERGY * 1 <= 83 (Wt = 360) | Other | Quick
NC_Q_CPSA | 0.75 | 0.41667 | Non Conformance Constraint for Condamine Power Station | Other | Non-Conformance
NC_Q_KAREEYA2 | 0.75 | 0 | Non Conformance Constraint for Kareeya 2 Power Station | Other | Non-Conformance
NC_S_AGLHAL | 0.75 | 0.25 | Non Conformance Constraint for AGL Hallet Power Station | Other | Non-Conformance
NC_V_WEMENSF1 | 0.75 | 0 | Non Conformance Constraint for WEMEN SF | Other | Non-Conformance
S:V_550_HY_TEST_DYN | 0.75 | 0 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
S>>X_DV-BR-PA_07 | 0.75 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West -Munno Para 275kV line, Feedback | Outage | SA
V^SML_NIL_3 | 0.75 | 0.083333 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Vic
N>N_LSDU_9U6_3 | 0.66667 | 0 | Out= one of Lismore 132 to Mullumbimby 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line for trip of 9G5 (Mullumbimby to Ewingsdale) 132kV line | Outage | NSW
NC_Q_DDPS1 | 0.66667 | 1.9167 | Non Conformance Constraint for Darling Downs Power Station | Other | Non-Conformance
S::V_NIL_TBSE_2 | 0.66667 | 0 | Out = Nil(Note: with both Black Range series capacitors O/S); SA to VIC Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
V:T_HAGT_BL_1 | 0.66667 | 0 | Out = Hadspen to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
V>>V-JNWG_RADIAL_1A | 0.66667 | 0 | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage | Vic
V>SMLMHNW2 | 0.66667 | 0 | Out = Monash-North West Bend # 2 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 1 132kV line | Outage | Vic
V_KARADSF_ISL_0 | 0.66667 | 0 | Karadoc Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
#YWPS4_E | 0.58333 | 0 | VYP24.ENERGY * 1 >= 220 (Wt = 35) | Other | Quick
CA_MQS_4C47A69C_01 | 0.58333 | 0 | Constraint Automation, O/L BATS_WBTS_220 @WBTS for CTG LNAB on trip of DARL-BAL-BURONGA X5/1&/3 220KV LNS. Generated by STNET[NORFL] Host MANEEMP2(MQ) | Outage | Constraint Automation
N>>N-NIL_DPTX_2 | 0.58333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | NSW
N>>V-JNWG_RADIAL_3 | 0.58333 | 0 | Out = Jindera to Wagga(62), avoid O/L Upper Tumut to Murray (65) using 15 mins rating on trip of Lower Tumut to Murray (66) line, Feedback | Outage | NSW
NC_N_HUMENSW | 0.58333 | 0.75 | Non Conformance Constraint for Hume Hydro Power Station | Other | Non-Conformance
NC_Q_KAREEYA3 | 0.58333 | 0 | Non Conformance Constraint for Kareeya 3 Power Station | Other | Non-Conformance
NC_S_SNOWNTH1 | 0.58333 | 0 | Non Conformance Constraint for Snowtown North Wind Farm | Other | Non-Conformance
NC_V_BALBG1 | 0.58333 | 1.4167 | Non Conformance Constraint for BALLARAT BATT (GEN) | Other | Non-Conformance
NC_V_YWPS4 | 0.58333 | 0.5 | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Other | Non-Conformance
NQTE_-040 | 0.58333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -40 MW | Outage | NSW
Q>>LCCP_CLWU_BCCP_2 | 0.58333 | 1.8333 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
Q>>PWSP_WOSP_PWCE | 0.58333 | 0.25 | Out= Palmwoods to South Pine (808) line, avoid O/L Palmwood to Caboolture (746/4) 110kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
S:V_550_HY_TEST | 0.58333 | 0 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
S>NIL_WERB_WEWT | 0.58333 | 4.75 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
T>>T_NIL_BL_EXP_5F | 0.58333 | 0.33333 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T_ROCOF_3 | 0.58333 | 0 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | Tas
T_T_FASH_10_N-2 | 0.58333 | 0 | Out = NIL, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain John Butters and Bastyan to 0 MW as per TAS Networks advice | Outage | Tas
V:SS_820_HY_TEST_DYN | 0.58333 | 0.083333 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
V>>BABE_DDGN_N-2 | 0.58333 | 0.16667 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage | Vic
V_BANSF_20INV | 0.58333 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 20. Constraint swamp out otherwise. DS only | NIL | Vic
V_KARSF_8INV | 0.58333 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 8. Constraint swamp out if number of inverter available not exceed 8. This is to manage voltage oscillation. DS only | Outage | Vic
#WRSF1_E | 0.5 | 21.8333 | NWRK2W.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
N>>N-NIL__B_15M | 0.5 | 0 | Out= Nil, avoid O/L Upper Tumut to Canberra (01) using 15 mins rating on trip of Lower Tumut to Canberra (07) line, Feedback | NIL | NSW
N>>N_65+66_N-2_5 | 0.5 | 0 | Out= Nil, avoid O/L Wodonga to Jindera (060) on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL | NSW
NC_N_MP1 | 0.5 | 1.0833 | Non Conformance Constraint for Mt Piper 1 Power Station | Other | Non-Conformance
NC_Q_KPP_1 | 0.5 | 0 | Non Conformance Constraint for Kogan Creek Power Station | Other | Non-Conformance
NC_Q_MPP_2 | 0.5 | 1.1667 | Non Conformance Constraint for Millmerran 2 Power Station | Other | Non-Conformance
NC_S_SNOWSTH1 | 0.5 | 0 | Non Conformance Constraint for Snowtown South Wind Farm | Other | Non-Conformance
N_WOODLWN1_ZERO | 0.5 | 0 | Woodlawn unit upper limit of 0 MW | Outage | NSW
Q>>CPSP_WOPW_WOGP_2 | 0.5 | 0 | Out= Calliope River to South Pine (813+815+807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Qld
S>>RBTU_BWMP_TWPA | 0.5 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | SA
S>>X_DVBR+BRTW_15 | 0.5 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | Outage | SA
SA_ISLE_STRENGTH_BU | 0.5 | 0 | Maximum limit (130 MW) for Bungala Solar Farm for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
V^^SML_NIL_3 | 0.5 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Vic
V_BANSF_BBD_80 | 0.5 | 0 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Vic
V_WEMENSF_ISL_0 | 0.5 | 0 | Wemen Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
#JLB01_E | 0.41667 | 0 | VJLGB1.ENERGY * 1 = 65 (Wt = 35) | Other | Quick
#JLB02_E | 0.41667 | 0 | VJLGB2.ENERGY * 1 = 65 (Wt = 35) | Other | Quick
#JLB03_E | 0.41667 | 0 | VJLGB3.ENERGY * 1 = 65 (Wt = 35) | Other | Quick
#NSW1_E_20190222 | 0.41667 | 0 | Multiple NSW1 LHS = 35 (Wt = 35) | Other | Quick
NC_Q_BRAEMAR2 | 0.41667 | 1.8333 | Non Conformance Constraint for Braemar 2 Power Station | Other | Non-Conformance
NC_Q_GSTONE6 | 0.41667 | 0.16667 | Non Conformance Constraint for Gladstone 6 Power Station | Other | Non-Conformance
NC_Q_MPP_1 | 0.41667 | 0.16667 | Non Conformance Constraint for Millmerran 1 Power Station | Other | Non-Conformance
NC_Q_SMCSF1 | 0.41667 | 0 | Non Conformance Constraint for Sun Metals solar farm | Other | Non-Conformance
NC_Q_TARONG#2 | 0.41667 | 0.41667 | Non Conformance Constraint for Tarong 2 Power Station | Other | Non-Conformance
NC_S_TBSF1 | 0.41667 | 0 | Non Conformance Constraint for Tailembend Solar Farm | Other | Non-Conformance
NC_V_BDL01 | 0.41667 | 0 | Non Conformance Constraint for Bairnsdale 1 Power Station | Other | Non-Conformance
NC_V_JLB01 | 0.41667 | 0.083333 | Non Conformance Constraint for Jeeralang B - 01 Power Station | Other | Non-Conformance
Q_STR_MEWF_26 | 0.41667 | 0 | Limit Mt Emerald WF to 50% capacity (26 turbines) | Outage | Qld
S>>BWMP_TWPA_TPRS | 0.41667 | 0.083333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
SVML_FLT_070 | 0.41667 | 0 | SA to Vic on ML upper transfer limit of 70 MW to manage system stability on the next contingency due to fault level issue | Outage | SA
S_TB2_TX | 0.41667 | 0 | Torrens B 2 Transformer O/S; unit=0 | Outage | SA
T_FARC2 | 0.41667 | 0 | Out=Farrell-Reece 2 220KV line. Energy <= 0MW | Outage | Tas
V::N_MLMO_xxx | 0.41667 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>SML_NIL_6 | 0.41667 | 0 | Out= Nil, Avoid pre-contingent overload of Waubra to Ballarat 220kV line, Feedback | NIL | Vic
V>>V_NIL_1B | 0.41667 | 1.5833 | Out = Nil, avoid O/L Murray to Dederang No.2 330kV line (flow MSS to DDTS) for loss of the parallel No.1 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
V>V_HWYP2_1_R | 0.41667 | 2.0833 | Out = Hazelwood to Yallourn No. 2 220 kV line, avoid O/L Yallourn to Hazelwood PS No.1 220kV line on trip of Yallourn to Rowville No.5 220kV line, Radial mode, YWG1 on 220kV, Feedback | Outage | Vic
V^^S_TBTX+CB_SETB_2 | 0.41667 | 1.3333 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
#JLA04_E | 0.33333 | 0 | VJLGA4.ENERGY * 1 <= 54 (Wt = 360) | Other | Quick
NC_N_BW04 | 0.33333 | 0.41667 | Non Conformance Constraint for Bayswater 4 Power Station | Other | Non-Conformance
NC_Q_BRAEMAR1 | 0.33333 | 0.083333 | Non Conformance Constraint for Braemar 1 Power Station | Other | Non-Conformance
N_BROKENHSF_FLT_26 | 0.33333 | 0 | Limit Broken Hill Solar Farm upper limit to 26 MW to manage post contingent voltage oscillation | Outage | NSW
Q>>CPSP_WOSP_PWCE | 0.33333 | 0 | Out= 808(Palmwoods to South Pine)+ 813 +815 (Calliope River to Woolooga) 275kV lines with 132kV/110kV network between Woolooga to Palmwoods network closed, avoid O/L Palmwood to Caboolture(746/4) on trip of Woolooga to South Pine (807)line, Feedback | Outage | Qld
Q>>WOPW_WOSP_WOGP_1 | 0.33333 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
Q_CS_1550 | 0.33333 | 0 | Qld Central to Qld South upper transfer limit of 1550MW (discretionary) | Outage | Qld
Q_STR_233310_HASF_60 | 0.33333 | 0 | Limit Haughton SF to 75% of max capacity (#60 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
S>>PATW_BWPA_WEMWP4 | 0.33333 | 0 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T>T_NIL_BL_110_8_1 | 0.33333 | 0 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
T^T_LFWA_1 | 0.33333 | 0 | Out = Lindisfarne to Waddamana 220 kV line, avoid voltage instability or violations for loss of the other Lindisfarne to Waddamana 220 kV line line | Outage | Tas
T_FATI | 0.33333 | 0.25 | Out=Farrell-Tribute 220KV line. Energy <= 0MW | Outage | Tas
V::S_NIL_TBSE_1 | 0.33333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
V>>V-LTWG_RADIAL_1 | 0.33333 | 0 | Outage = Lower Tumut to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings; Feedback | Outage | Vic
VS_050 | 0.33333 | 7.1667 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Vic
V_MURRAWR_ZERO | 0.33333 | 0 | Murra Warra wind farm upper limit of 0 MW | Outage | Vic
V_OAKLANDSHILL_42 | 0.33333 | 0 | Oaklands Hill Windfarm upper limit of 42 MW | Outage | Vic
#LBBG1_E | 0.25 | 0 | SLBB1L.ENERGY * 1 <= 2 (Wt = 755) | Other | Quick
#OAKEY1SF_E | 0.25 | 0 | QTKS1O.ENERGY * 1 <= 12 (Wt = 360) | Other | Quick
#STWF1_E | 0.25 | 153.3333 | NBKW1S.ENERGY * 1 <= 131 (Wt = 360) | Other | Quick
N>>N-NIL__H_15M | 0.25 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | NSW
N>>V-LTUT_J | 0.25 | 0 | Out = LowerTumut-UpperTumut(64), avoid Upper Tumut to Murray(65) O/L on Nil trip; Feedback | Outage | NSW
N>N-BAMB_132_OPEN_B | 0.25 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage | NSW
NC_N_LD04 | 0.25 | 0.58333 | Non Conformance Constraint for Liddell LD04 Power Station | Other | Non-Conformance
NC_Q_CLERMSF1 | 0.25 | 0 | Non Conformance Constraint for CLERMONT SOLAR FARM | Other | Non-Conformance
NC_Q_GSTONE1 | 0.25 | 0.25 | Non Conformance Constraint for Gladstone 1 Power Station | Other | Non-Conformance
NC_Q_GSTONE3 | 0.25 | 0.58333 | Non Conformance Constraint for Gladstone 3 Power Station | Other | Non-Conformance
NC_Q_STAN-2 | 0.25 | 0.16667 | Non Conformance Constraint for Stanwell STAN-2 Power Station | Other | Non-Conformance
NC_Q_TARONG#3 | 0.25 | 1.9167 | Non Conformance Constraint for Tarong 3 Power Station | Other | Non-Conformance
NC_Q_TNPS1 | 0.25 | 0.25 | Non Conformance Constraint for Tarong North Power Station | Other | Non-Conformance
NC_Q_YABULU | 0.25 | 0 | Non Conformance Constraint for Yabulu Power Station | Other | Non-Conformance
NC_S_OSB-AG | 0.25 | 0 | Non Conformance Constraint for Osborne Power Station | Other | Non-Conformance
NC_T_GORDON | 0.25 | 0 | Non Conformance Constraint for Gordon Power Station | Other | Non-Conformance
NC_T_LI_WY_CA | 0.25 | 0.083333 | Non Conformance Constraint for Liapootah + Wayatinah + Catagunya Power Stations | Other | Non-Conformance
NC_V_JLB02 | 0.25 | 0 | Non Conformance Constraint for Jeeralang B - 02 Power Station | Other | Non-Conformance
N_BODWF1_ZERO | 0.25 | 8.5833 | Bodangora wind farm upper limit of 0 MW | Outage | NSW
Q_STR_SMHAU_MEWF_26 | 0.25 | 0 | Limit Mt Emerald WF to 75% capacity(39 turbines)during day or (swamp at night) if Kar >=2 (2 TX during day) +Stan >= 3 + Cal >=3 + Glads>= 3 and (Stan+Cal+Glad) >=10, 50%during day if Kar< 2 ( or 1 TX ). Zero otherwise. | Outage | Qld
S-DLBAT-L_0 | 0.25 | 0 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW | Outage | SA
S>>CNLK_BWMP_MKRB | 0.25 | 0 | Out= Canowie-Mt Lock 275kV line, avoid O/L Mokota-Robertstown 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>>DVBL_LKDV_WEWT | 0.25 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East- Waterloo 132kV on trip of Mt Lock-Davenport 275kV line, Feedback | Outage | SA
S_LB3_0 | 0.25 | 0.83333 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
T>>T_NIL_BL_EXP_6E | 0.25 | 0 | Out = Nil, avoid O/L a Sheffield to Georgetown 220 kV line (flow to Georgetown) for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T>T_SH_TX | 0.25 | 0 | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Tas
T_LIWY | 0.25 | 0 | Out=Liapootah-Wayatinah 220KV line | Outage | Tas
T_PMPO_220 | 0.25 | 0 | Out=A single Palmerston-Poatina 220KV line. One line out of service only | Outage | Tas
T_T_FASH_3_N-2 | 0.25 | 6.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain Reece Unit 1 to 0 MW as per TAS Networks advice | Outage | Tas
V::S_BLKRG_MAXG_2 | 0.25 | 17.0833 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
V>>N-JNWO_RADIAL_1 | 0.25 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
V>V_NIL_17 | 0.25 | 0 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback. Constraint only active when either Wemen or Bannerton solar farm runback scheme disabled. | NIL | Vic
V>V_NIL_9 | 0.25 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Crowlands to Bulgana to Horsham 220kV line (this trips Bulgana WF), Feedback | NIL | Vic
#LBBL1_E | 0.16667 | 0 | SLBB2L.ENERGY * 1 <= 2 (Wt = 755) | Other | Quick
#V-S-MNSP1_E_E | 0.16667 | 0.16667 | V-S-MNSP1.ENERGY * 1 <= 60 (Wt = 360) | Other | Quick
N::V_WA_BUSA_MSDD | 0.16667 | 0 | Out= Wagga 330kV A Bus, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | NSW
N>>N-MNYS5_01_15M | 0.16667 | 0 | Out = Marulan-Yass(5), avoid O/L Marulan to Yass (4) using 15 mins rating on trip of Bannaby to Gullen Range (61) line, Feedback | Outage | NSW
N>>N-NIL_64 | 0.16667 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | NSW
NC_N_BW02 | 0.16667 | 0.25 | Non Conformance Constraint for Bayswater 2 Power Station | Other | Non-Conformance
NC_N_BW03 | 0.16667 | 0 | Non Conformance Constraint for Bayswater 3 Power Station | Other | Non-Conformance
NC_N_ER01 | 0.16667 | 0.33333 | Non Conformance Constraint for Eraring ER01 Power Station | Other | Non-Conformance
NC_N_ER02 | 0.16667 | 0 | Non Conformance Constraint for Eraring ER02 Power Station | Other | Non-Conformance
NC_N_LD02 | 0.16667 | 0.16667 | Non Conformance Constraint for Liddell LD02 Power Station | Other | Non-Conformance
NC_N_MP2 | 0.16667 | 0.83333 | Non Conformance Constraint for Mt Piper 2 Power Station | Other | Non-Conformance
NC_Q_BARRON-1 | 0.16667 | 0.083333 | Non Conformance Constraint for Barron Gorge 1 Power Station | Other | Non-Conformance
NC_Q_OAKEY1SF | 0.16667 | 0 | Non Conformance Constraint for OAKEY 1 SOLAR FARM | Other | Non-Conformance
NC_Q_STAN-3 | 0.16667 | 0.66667 | Non Conformance Constraint for Stanwell STAN-3 Power Station | Other | Non-Conformance
NC_Q_STAN-4 | 0.16667 | 2.4167 | Non Conformance Constraint for Stanwell STAN-4 Power Station | Other | Non-Conformance
NC_S_HALLWF1 | 0.16667 | 0 | Non Conformance Constraint for Hallet Wind Farm | Other | Non-Conformance
NC_V_BDL02 | 0.16667 | 0.16667 | Non Conformance Constraint for Bairnsdale 2 Power Station | Other | Non-Conformance
NRM_SA1_VIC1 | 0.16667 | 7.6667 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue
N^^N_NIL_1 | 0.16667 | 1.5 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
Q_NIL_STRGTH_SMSF | 0.16667 | 0 | Out = Nil, limit Sun Metal SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to TOA 393 | NIL | Qld
Q_STR_43239_SMSF_38 | 0.16667 | 0 | Limit Sun Metals SF to 50% capacity (38 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=3 + (Stan+Cal+Glad >=9). Zero otherwise. | Outage | Qld
S>>NIL_TBCG_TBTU_1 | 0.16667 | 0 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | SA
S>>TBTU_TBCG_TBMO | 0.16667 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage | SA
S>>X_BLDV+WEMWP4_05 | 0.16667 | 0 | Out= Out= Belalie-Davenport 275kV line + Waterloo East-MWP4-Robertstown 132kV line), avoid O/L Templers-Roseworthy 132k on trip of Templers West-Para 275kV line, Feedback | Outage | SA
S>>X_RBPA+BGTX_02 | 0.16667 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Robertstown-MWP4-Waterloo East 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
S>>X_RBTU+CB_1 | 0.16667 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) lines, Feedback | Outage | SA
SVML_120 | 0.16667 | 0 | SA to Vic on ML upper transfer limit of 120 MW | Outage | SA
SV_070 | 0.16667 | 0 | SA to Victoria on VicSA upper transfer limit of 70 MW | Outage | SA
T>T_GTSH_5K | 0.16667 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L line terminal equipment of Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line, feedback | Outage | Tas
T>T_NIL_BL_220_6B | 0.16667 | 0 | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
T>T_NIL_BL_IMP_6E | 0.16667 | 0 | Out = Nil, avoid O/L Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action, feedback | NIL | Tas
V::N_SMSY_xxx | 0.16667 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::N_X_HWSM_12_xxx | 0.16667 | 0 | Out= Hazelwood - South Morang No.1 and No.2 500kV lines, prevent transient instability for loss of ROTS-SMTS 500kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::N_X_HWSM_HWRO_xxx | 0.16667 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V:SS_820_HY_TEST | 0.16667 | 0 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
V_ARWF_FSTTRP_5 | 0.16667 | 2.0833 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
#EMERASF1_E | 0.083333 | 155.5833 | QLIS1E.ENERGY * 1 <= 4 (Wt = 360) | Other | Quick
#OSB-AG_E | 0.083333 | 0 | SNBN1.ENERGY * 1 >= 160 (Wt = 35) | Other | Quick
CA_BRIS_4D0EE093_1 | 0.083333 | 0 | Constraint Automation, O/L EPS_MBTS2_220:LEP2:Z:220@MBTS@VIC for CTG LVCY on trip of EPS-MBTS1 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage | Constraint Automation
CA_MQS_4BA18A48_01 | 0.083333 | 0 | Constraint Automation, O/L OSBTOA_4 @N_OSBN for CTG LSHR on trip of PGWEST-PELI_P 275KV LINE. Generated by STNET[MANBL] Host MANEEMP1(MQ) | Outage | Constraint Automation
N-SAPHWF_TX | 0.083333 | 0 | Outage = One Sapphire wind farm 330/33kV transformer (1A or 1B), Sapphire WF Isolators 2415 and 2416 closed | Outage | NSW
N::Q_NIL_KC | 0.083333 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | NSW
N>>V-NIL_HC | 0.083333 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; Feedback | NIL | NSW
NC_N_BW01 | 0.083333 | 0.5 | Non Conformance Constraint for Bayswater 1 Power Station | Other | Non-Conformance
NC_N_ER03 | 0.083333 | 0.33333 | Non Conformance Constraint for Eraring ER03 Power Station | Other | Non-Conformance
NC_N_LD01 | 0.083333 | 0.16667 | Non Conformance Constraint for Liddell LD01 Power Station | Other | Non-Conformance
NC_N_NEVERSF1 | 0.083333 | 0 | Non Conformance Constraint for NEVERTIRE SOLAR FARM | Other | Non-Conformance
NC_Q_CLARESF1 | 0.083333 | 0 | Non Conformance Constraint for CLARE SOLAR FARM | Other | Non-Conformance
NC_Q_CPP_3 | 0.083333 | 0 | Non Conformance Constraint for Callide C CPP_3 | Other | Non-Conformance
NC_Q_GSTONE2 | 0.083333 | 0 | Non Conformance Constraint for Gladstone 2 Power Station | Other | Non-Conformance
NC_Q_MSTUART3 | 0.083333 | 0 | Non Conformance Constraint for Mt Stuart 3 Power Station | Other | Non-Conformance
NC_Q_OAKEY2SF | 0.083333 | 0 | Non Conformance Constraint for OAKEY 2 SOLAR FARM | Other | Non-Conformance
NC_Q_TARONG#4 | 0.083333 | 0.16667 | Non Conformance Constraint for Tarong 4 Power Station | Other | Non-Conformance
NC_S_NBHWF1 | 0.083333 | 0 | Non Conformance Constraint for North Brown Hill Windfarm | Other | Non-Conformance
NC_T_POAT110 | 0.083333 | 0 | Non Conformance Constraint for Poatina 110kV Power Station | Other | Non-Conformance
NC_V_BANN1 | 0.083333 | 0 | Non Conformance Constraint for BANNERTON SOLAR PARK | Other | Non-Conformance
NC_V_LNGS2 | 0.083333 | 0 | Non Conformance Constraint for Laverton North 2 | Other | Non-Conformance
NC_V_LOYYB2 | 0.083333 | 0.25 | Non Conformance Constraint for Loy Yang B2 Power Station | Other | Non-Conformance
NC_V_MUWAWF1 | 0.083333 | 0 | Non Conformance Constraint for MURRA WARRA WF 1 | Other | Non-Conformance
NRM_VIC1_SA1 | 0.083333 | 0.25 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
N_COLEASF1_100 | 0.083333 | 0 | Coleambally solar farm upper limit of 100 MW | Outage | NSW
N_FINLYSF1_66 | 0.083333 | 0 | Finley solar farm upper limit of 66 MW | Outage | NSW
Q>>WOSP_WOPW_WOGP_1 | 0.083333 | 0 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Qld
Q_CS_0800 | 0.083333 | 0 | Qld Central to Qld South upper transfer limit of 800MW (discretionary) | Outage | Qld
Q_CS_0900 | 0.083333 | 0 | Qld Central to Qld South upper transfer limit of 900MW (discretionary) | Outage | Qld
Q_CS_1000 | 0.083333 | 0 | Qld Central to Qld South upper transfer limit of 1000MW (discretionary) | Outage | Qld
Q_CS_2000 | 0.083333 | 1.5833 | Qld Central to Qld South upper transfer limit of 2000MW (discretionary) | Outage | Qld
Q_KMBG_7184 | 0.083333 | 0 | Out= 7184 Kamerunga Barron Gorge PS 132kV line | Outage | Qld
Q_NESTM_STRGTH_HAUSF | 0.083333 | 0 | Out = 822, Limit Haughton SF to 50% of max capacity (#40 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
Q_STR_SMHAU_HASF_40 | 0.083333 | 0 | Limit Haughton SF to 50% capacity (40 inverters) If Stan >= 3 + Cal >=3 + Glad >= 3 and (Stan+Cal+Glad) >=10, Zero otherwise | Outage | Qld
S>>BRTW_RBTU_WTTP | 0.083333 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
S>SETXH1_SETXL2 | 0.083333 | 0 | Constraint Automation, O/L S_EAST TRANSF T_2 for CTG TSHZ on trip of S_EAST 1 275/132KV TX. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
S>X_DV-BR-PA_06 | 0.083333 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Canowi-Robertstown 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S_HDWF1_0 | 0.083333 | 6.4167 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | SA
S_PWLG_LG2 | 0.083333 | 0 | Outage of Penola West to Ladbroke Grove 132kV circuit | Outage | SA
T>T_LIPM_110_2B | 0.083333 | 129.0833 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
T>T_NIL_BL_IMP_5FF | 0.083333 | 0 | Out = Nil, avoid O/L Hadspen to Georgetown No. 2 220 kV line (flow to North) for trip of the Hadspen to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
T^V_NIL_BL_6 | 0.083333 | 0 | Outage = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
T_PMPO_TWO_220 | 0.083333 | 0 | Out= two Palmerston to Poatina 220KV lines | Outage | Tas
T_T_FASH_8_N-2 | 0.083333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation >= 90% of West Coast load | Outage | Tas
T_T_JB_RC1+2_TI_250 | 0.083333 | 8.0833 | Discretionary 250 MW upper limit on John Butters, Reece 1+2 and Tribute | Outage | Tas
V::N_WBHO_xxx | 0.083333 | 17.8333 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::N_X_HWSM_ROSM_xxx | 0.083333 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_RBTU_SETB | 0.083333 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
V>>V_KGWT_2 | 0.083333 | 0 | Out = Kerang to Wemen 220kV line, avoid overloading Bulgana to Horsham 220kV line section for loss of Balranald to Buronga (X3) 220kV line | Outage | Vic
V>>V_KTS_TX_A3_3A_R | 0.083333 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr for trip of ROTS A1 500/220 kV txfmr, radial mode, Yallourn W unit 1 on 500 kV network, feedback | Outage | Vic
V>SML_NSWRB_10 | 0.083333 | 2.4167 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL | Vic
V_GANWR_BAT_L_ISL_0 | 0.083333 | 0 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
V_S_NIL_ROCOF | 0.083333 | 0.25 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | Vic

## Binding FCAS
Constraint Equation ID | 2019 Hours | 2018 Hours | Description | Type
F_I+NIL_MG_R5 | 6863.5833 | 5646.9167 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL
F_I+NIL_APD_TL_L5 | 6646.3333 | 6258.1667 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R6 | 6306.5833 | 4569.5 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL
F_I+NIL_MG_R60 | 6113.9167 | 4449.6667 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL
F_I+NIL_APD_TL_L60 | 5908.1667 | 5400.25 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_T_AUFLS2_R6 | 5082.5833 | 1491.1667 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL
F_I+ML_L6_0400 | 3789.8333 | 2092.4167 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL
F_MAIN+NIL_DYN_RREG | 3535.25 | 1072.3333 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL
F_MAIN++APD_TL_L5 | 2465.75 | 1644.5833 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_MAIN++NIL_MG_R60 | 2131.25 | 2546.4167 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_MAIN++APD_TL_L60 | 2115.25 | 1332.8333 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_I+LREG_0210 | 2082.9167 | 0 | NEM Lower Regulation Requirement greater than 210 MW | NIL
F_I+LREG_0210 | 2049.3333 | 0 | NEM Lower Regulation Requirement greater than 210 MW | Other
F_MAIN++NIL_MG_R6 | 1768.4167 | 2404.3333 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_T+NIL_MG_RECL_R60 | 1705.25 | 1368.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R6 | 1656.3333 | 1344.5 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_I+LREG_0120 | 1581.3333 | 3998.0833 | NEM Lower Regulation Requirement greater than 120 MW | NIL
F_T+NIL_MG_RECL_R5 | 1501.6667 | 1243 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++ML_L6_0400 | 1417.9167 | 687.5 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 1340.6667 | 1111.6667 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R5 | 1306.8333 | 937.6667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_I+RREG_0220 | 1273.0833 | 0 | NEM Raise Regulation Requirement greater than 200 MW | NIL
F_T+NIL_WF_TG_R6 | 1272.8333 | 1066.8333 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_I+RREG_0220 | 1240.75 | 0 | NEM Raise Regulation Requirement greater than 200 MW | Other
F_T_NIL_MINP_R6 | 1218 | 1274.9167 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL
F_MAIN+NIL_MG_R60 | 1185.3333 | 2186.0833 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 1185.3333 | 2184.0833 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 1184.75 | 2182.9167 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_T+NIL_ML_L6 | 1184.6667 | 2240.0833 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L60 | 1184.4167 | 2162.5 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T+LREG_0050 | 1184.3333 | 2258 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L5 | 1145.1667 | 1914.0833 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L5 | 1143.5 | 1893.0833 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_T+RREG_0050 | 1127.3333 | 1705.8333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 1123 | 1870.6667 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 1122.6667 | 1667.9167 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_MAIN+ML_L6_0400 | 1000.8333 | 1618.3333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_T+NIL_MG_R60 | 850.5 | 1318.5833 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R5 | 821 | 933.5 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R6 | 737.1667 | 1221.9167 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_I+LREG_0190 | 688.75 | 0 | NEM Lower Regulation Requirement greater than 190 MW | Other
F_I+LREG_0170 | 675.5 | 0 | NEM Lower Regulation Requirement greater than 170 MW | Other
F_MAIN+LREG_0210 | 673.75 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+TASCAP_RREG | 637.25 | 233.5833 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_I+NIL_RREG | 611.4167 | 2288.25 | NEM Raise Regulation Requirement | NIL
F_V_APD01_R5 | 605.4167 | 0.66667 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage
F_V_APD01_L6 | 605.4167 | 0.66667 | Out= NIL, APD Potline 1 L6 Requirement <= 0MW | Outage
F_V_APD01_R60 | 605.4167 | 0.66667 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage
F_V_APD01_R6 | 605.4167 | 0.66667 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage
F_V_APD01_L5 | 605.4167 | 0.58333 | Out= NIL, APD Potline 1 L5 Requirement <= 0MW | Outage
F_V_APD01_L60 | 605.4167 | 0.66667 | Out= NIL, APD Potline 1 L60 Requirement <= 0MW | Outage
F_T++RREG_0050 | 549.3333 | 572.1667 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_S++HYSE_L60 | 443.5 | 8.5 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
F_I+RREG_0180 | 440.75 | 0 | NEM Raise Regulation Requirement greater than 180 MW | Other
F_I+RREG_0200 | 426 | 0 | NEM Raise Regulation Requirement greater than 200 MW | Other
F_S++HYSE_L6_1 | 390.4167 | 9.4167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
F_TASCAP_RREG_0180 | 348.0833 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | Other
F_TASCAP_LREG_0210 | 341.25 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | Other
F_MAIN+NIL_DYN_LREG | 328.8333 | 535 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL
F_MAIN+RREG_0220 | 322.25 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+LREG_0210 | 301.5833 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | Other
F_T++NIL_ML_L60 | 275.5833 | 673.9167 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_MAIN++LREG_0120 | 273.75 | 378.0833 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL
F_TASCAP_LREG_0210 | 272 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_MAIN+TASCAP_LREG | 264.4167 | 2077.1667 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_T++NIL_ML_L6 | 246.9167 | 1035.6667 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_T++NIL_MG_RECL_R6 | 216.5 | 157.5833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_TASCAP_RREG_0220 | 206.25 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | Other
F_T++NIL_MG_RECL_R5 | 194.3333 | 69.0833 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_TASCAP_RREG_0220 | 190.3333 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_MAIN+RREG_0220 | 181.9167 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | Other
F_MAIN++LREG_0210 | 179.25 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
F_T++LREG_0050 | 174.5 | 733.0833 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_I+ML_L6_APD | 166.25 | 173.1667 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage
F_TASCAP_LREG_0190 | 162.6667 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | Other
F_Q++BCDM_L6 | 140.1667 | 82.9167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
F_TASCAP_RREG_0200 | 138.75 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | Other
F_Q++BCDM_L60 | 133.0833 | 82.8333 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage
F_MAIN++LREG_0170 | 107.1667 | 0 | Mainland Lower Regulation Requirement greater than 170 MW, Basslink able transfer FCAS | Other
F_T++NIL_MG_RECL_R60 | 106.1667 | 162.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN+LREG_0120 | 102.5 | 1692.3333 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | NIL
F_S++HYSE_L5 | 101.5 | 0.5 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
F_MAIN++LREG_0210 | 97.6667 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Other
F_T++NIL_WF_TG_R5 | 95.3333 | 74.5 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_TASCAP_LREG_0170 | 88.25 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | Other
F_MAIN++NIL_BL_L60 | 85 | 2.4167 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_MAIN++RREG_0220 | 74.5833 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | Other
F_T++NIL_BLSPS_L60_1 | 72.25 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_T++NIL_BLSPS_L6_1 | 72.1667 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_T++NIL_WF_TG_R60 | 63.9167 | 107.3333 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++NIL_WF_TG_R6 | 61.75 | 80.9167 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_Q++BCDM_L5 | 61.5833 | 74.1667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
F_T++NIL_MG_R5 | 49.1667 | 20.3333 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN++LREG_0190 | 42.4167 | 0 | Mainland Lower Regulation Requirement greater than 190 MW, Basslink able transfer FCAS | Other
F_MAIN+NIL_RREG | 41.5 | 772.0833 | Mainland Raise Regulation Requirement, Basslink unable transfer FCAS | NIL
F_I+ML_L5_0400 | 35.8333 | 26 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL
F_MAIN++ML_L6_APD | 35 | 109.5833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_I+ML_L5_APD | 33 | 20.5 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage
F_MAIN++RREG_0220 | 29.0833 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
F_ESTN++MLTR_L60 | 28.25 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_I+ML_L60_APD | 27.25 | 18.5833 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage
F_MAIN+LREG_0170 | 25 | 0 | Mainland Lower Regulation Requirement greater than 170 MW, Basslink unable to transfer FCAS | Other
F_T++NIL_BLSPS_L5 | 22.5 | 0 | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
F_MAIN+LREG_0190 | 22.4167 | 0 | Mainland Lower Regulation Requirement greater than 190 MW, Basslink unable to transfer FCAS | Other
F_T++NIL_MG_R6 | 21.6667 | 43.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_Q++ARTW_L60 | 20.0833 | 73.75 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_Q++ARTW_L6 | 20.0833 | 83.5833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
F_T++NIL_MG_R60 | 20.0833 | 59.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_Q++ARTW_L5 | 16.4167 | 64.4167 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
F_T+FASH_N-2_RREG | 16.1667 | 26.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_MAIN+RREG_0200 | 15.8333 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | Other
F_MAIN++RREG_0180 | 15.1667 | 0 | Mainland Raise Regulation Requirement greater than 180 MW, Basslink able transfer FCAS | Other
F_I+ML_L60_0400 | 14.75 | 12.8333 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL
F_ESTN++MLMO_L60 | 14.0833 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_I+ML_L6_0500 | 13.9167 | 0 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 500 | Outage
F_MAIN+RREG_0180 | 13.75 | 0 | Mainland Raise Regulation Requirement greater than 180 MW, Basslink unable to transfer FCAS | Other
F_MAIN++ML_L5_APD | 13.5833 | 9.9167 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_I+WIP_N-2_ML_L6 | 13.5833 | 29.5833 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 6 sec requirement | Outage
F_V_GESS_G_RREG | 13.1667 | 0 | Gannawarra Battery (Gen Component) RREG requirement <=0 MW | Outage
F_MAIN++RREG_0200 | 12.0833 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | Other
F_S++HYSE_L6_2 | 11.8333 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage
F_MAIN++NIL_RREG | 10.8333 | 61.0833 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL
F_NQ++65_66_RAD_L5 | 10.0833 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 5 min Requirement | Outage
F_QNV+MLMO_L60 | 10.0833 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_NQ++65_66_RAD_L60 | 10.0833 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 60 sec Requirement | Outage
F_MAIN++WIP_N-2_MLL6 | 9.5833 | 3.75 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage
F_ESTN++HYTR_L60 | 9.5833 | 2.4167 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_I+ML_L5_0500 | 9.5833 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 500 | Outage
F_T+NIL_BB_TG_R60 | 9.3333 | 0.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_Q_W/HOE_R5 | 8.9167 | 0 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage
F_VST++65_66_RAD_R5 | 8.5833 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; VIC, SA and TAS Raise 5 min Requirement | Outage
F_I+ML_L60_0500 | 8 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 500 | Outage
F_MAIN++ML_L60_APD | 7.5833 | 11.6667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_Q++NIL_R5 | 7.3333 | 1.5833 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
F_NQ++65_66_RAD_L6 | 7 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 6 sec Requirement | Outage
F_MAIN+ML_L6_APD | 6.75 | 7.5 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_VST++65_66_RAD_R60 | 6.6667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; VIC, SA and TAS Raise 60 sec Requirement | Outage
F_VS++65_66_RAD_R60 | 6 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+CSGO_TG_R60 | 6 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_MAIN+ML_L5_0400 | 5.6667 | 4 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_T+FASH_N-2_TG_R6_1 | 5.5833 | 12.9167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage
F_T+FASH_N-2_TG_R5 | 5.4167 | 4.4167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T+FASH_N-2_TG_R60 | 5.3333 | 6 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T+FARE_N-2_TG_R60 | 5.25 | 1.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_V+NIL_APD01_R60 | 5.0833 | 3.4167 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_V+NIL_APD01_L6 | 5.0833 | 3.4167 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_V+NIL_APD01_R5 | 5.0833 | 3.5833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_APD01_L60 | 5.0833 | 3.5833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_T+NIL_BB_TG_R6 | 5.0833 | 0.33333 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_V+NIL_APD01_L5 | 5.0833 | 3.5833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_V+NIL_APD01_R6 | 5.0833 | 3.5 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_ESTN++MLTR_L5 | 5 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
F_QNV++MLTR_L60 | 4.9167 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_S+TL_L60_OD | 4.8333 | 0.25 | Lower 60 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_ESTN+ML_L6_0400 | 4.8333 | 0.083333 | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_ESTN+MG_R60 | 4.8333 | 0 | Raise 60 sec Service Requirement for Eastern Generation Event | Outage
F_ESTN+MG_R5 | 4.8333 | 0.083333 | Raise 5 min Service Requirement for Eastern Generation Event | Outage
F_ESTN+LREG_0210 | 4.8333 | 0 | Eastern Lower Regulation Requirement greater than 210 MW | Outage
F_ESTN+MG_R6 | 4.8333 | 0 | Raise 6 sec Service Requirement for Eastern Generation Event | Outage
F_S+TL_L6_OD | 4.8333 | 0.25 | Lower 6 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_T+FARE_N-2_RREG | 4.8333 | 1 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_T++NIL_BLSPS_R6_2 | 4.6667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_T+FASH_N-2_TG_R6_2 | 4.6667 | 0.41667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage
F_S+TL_L5_OD | 4.6667 | 0.25 | Lower 5 min Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_ESTN+ML_L5_0400 | 4.6667 | 0 | Lower 5 min requirement for a Eastern Load Event, ML = 400 | Outage
F_ESTN+ML_L60_0400 | 4.6667 | 0.083333 | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_T++NIL_BLSPS_R60_2 | 4.5833 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_ESTN+RREG_0220 | 4.5833 | 0 | Eastern Raise Regulation Requirement greater than 220 MW | Outage
F_T+CSGO_TG_R6_1 | 4.25 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage
F_S++OSB_R6_1 | 4.25 | 0.41667 | Raise 6 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA, Segment 1 | Outage
F_Q_MEWV_823_R5 | 3.6667 | 0 | Out= Mt England to Wivenhoe (823) line, Raise 5 min requirement of zero for Wivenhoe #1 | Outage
F_QNV++MG_R60 | 3.5833 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_Q++8C_L6 | 3.5833 | 26.9167 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
F_Q++8C_L60 | 3.5833 | 16.0833 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage
F_I+TL_L60_0550 | 3.3333 | 0 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 550 | Outage
F_I+TL_L5_0550 | 3.3333 | 0 | Lower 5 min Service Requirement for a NEM Network Event, TL = 550 | Outage
F_T++FASH_N-2_TG_R6 | 3.25 | 1.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_MAIN+ML_L60_0400 | 3.1667 | 3.6667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN++ML_L6_0500 | 3 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage
F_S+PPT_R6_1 | 2.9167 | 0.41667 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 1 | Outage
F_S+PPT_R60 | 2.9167 | 0.083333 | Raise 60 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage
F_QNV+HYMO_L60 | 2.9167 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T+FARE_N-2_TG_R6_1 | 2.8333 | 1.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage
F_Q++BCDM_R60 | 2.8333 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage
F_MAIN++ML_L5_0500 | 2.8333 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage
F_S+SNS_TG_R6_1 | 2.8333 | 0 | Raise 6 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line, Segment1 | Outage
F_T+FARE_N-2_TG_R5 | 2.8333 | 2.5833 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_T++FASH_N-2_TG_R60 | 2.75 | 3.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_WESTCOAST_RREG_0 | 2.75 | 0 | RREG FCAS of West Coast Generation limited to 0 MW | Outage
F_S+PPT_R5 | 2.6667 | 0.41667 | Raise 5 min Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage
F_T++COGT_TL_L6 | 2.6667 | 19.5 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_Q_MACKAYGT_R5 | 2.6667 | 0 | Out= NIL, Mackay GT R5 Requirement <= 0MW | Outage
F_MAIN++ML_L5_0400 | 2.5 | 3.5 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_T++FARE_N-2_TG_R6 | 2.5 | 0.41667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_VS++65_66_RAD_R5 | 2.25 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 5 min Requirement, Basslink able to transfer FCAS | Outage
F_Q++8C_L5 | 2.1667 | 16.6667 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
F_MAIN++ML_L60_0500 | 2 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage
F_T+FARE_N-2_TG_R6_2 | 2 | 2.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage
F_T+FASH1_2C_TG_R5 | 1.9167 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_Q_MEWV_824_R60 | 1.8333 | 0 | Out= Mt England to Wivenhoe (824) line, Raise 60 sec requirement of zero for Wivenhoe #2 | Outage
F_WESTCOAST_LREG_0 | 1.8333 | 0 | LREG FCAS of West Coast Generation limited to 0 MW | Outage
F_QNV+MLTR_L60 | 1.5 | 0.16667 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+WIP_N-2_ML_L6 | 1.5 | 1 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink unable to transfer FCAS | Outage
F_S++OSB_R60 | 1.5 | 0.083333 | Raise 60 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA | Outage
F_Q_MEWV_823_R60 | 1.5 | 0 | Out= Mt England to Wivenhoe (823) line, Raise 60 sec requirement of zero for Wivenhoe #1 | Outage
F_Q++BCDM_R6 | 1.5 | 0.083333 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
F_S++OSB_R5 | 1.4167 | 0.16667 | Raise 5 min Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA | Outage
F_S++TIB3_R6_1 | 1.3333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA, Segment 1 | Outage
F_ESTN++HYTR_L5 | 1.3333 | 2.4167 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
F_T++FARE_N-2_TG_R5 | 1.3333 | 0.083333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_MAIN++ML_L60_0400 | 1.3333 | 1.8333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_QNV++MG_R5 | 1.25 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_T+NIL_BB_TG_R5 | 1.1667 | 0.16667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_T++COGT_TL_L60 | 1.1667 | 19.5 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T++FASH_N-2_TG_R5 | 1.1667 | 2.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_MAIN+ML_L60_APD | 1.1667 | 0.16667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_MAIN+ML_L5_APD | 1.0833 | 0.083333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_S++TIB4_R6_1 | 0.91667 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA, Segment 1 | Outage
F_VS+65_66_RAD_R5 | 0.91667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_VS+65_66_RAD_R60 | 0.91667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_Q_MK_33BUS_R5 | 0.91667 | 0 | Out=T38 Mackay 33kV C Bus (R5 Requirement) | Outage
F_T++NIL_BLSPS_L6_2 | 0.91667 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_T++NIL_BLSPS_L60_2 | 0.83333 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_T+CSGO_TG_R5 | 0.66667 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_MAIN++ML_L6_APD_LD | 0.58333 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
F_Q_W/HOE_R60 | 0.58333 | 0 | Out= Nil, Wivenhoe Raise 60 services <= 0 MW when both units are online in gen mode | Outage
F_S+PPT_R6_2 | 0.5 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 2 | Outage
F_S+SNS_TG_R5 | 0.5 | 0 | Raise 5 min Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage
F_S+SNS_TG_R60 | 0.41667 | 0 | Raise 60 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage
F_QNV++HYTR_L60 | 0.41667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_MAIN+ML_L5_0500 | 0.41667 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS | Outage
F_MAIN+ML_L60_0500 | 0.41667 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS | Outage
F_MAIN+ML_L6_0500 | 0.41667 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS | Outage
F_QNV++MG_R6 | 0.41667 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_T++COGT_TL_L5 | 0.41667 | 19.5 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T++CSGO_TG_R5 | 0.33333 | 0.58333 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_T+FASH1_2C_TG_R60 | 0.33333 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_I+ML_L6_APD_LD | 0.33333 | 0 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage
F_QNV++MLTR_L5 | 0.33333 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T+FASH1_2C_TG_R6 | 0.33333 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_S+RREG_0035 | 0.33333 | 17.5833 | SA Raise Regulation FCAS Requirement greater than 35 MW | Outage
F_T++CSGO_TG_R60 | 0.33333 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_T++NIL_BLSPS_R5 | 0.25 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
F_T_FARC2_R6 | 0.25 | 0 | Out=Farrell-Reece 2 220KV line. R6 <= 0MW | Outage
F_QNV++ML_L60_0400 | 0.25 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_QNV+HYMO_L5 | 0.25 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_I+WIP_N-2_ML_L5 | 0.16667 | 3.5833 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 5 Min requirement | Outage
F_QNV++HYTR_L5 | 0.16667 | 0.083333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T+FASH1_2C_RREG | 0.16667 | 16.3333 | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS | Outage
F_QNV++MLMO_L60 | 0.16667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_ESTN+APD_TL_L5 | 0.16667 | 0 | Lower 5 min requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_ESTN+APD_TL_L60 | 0.16667 | 0 | Lower 60 sec requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_QNV+HYTR_L60 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+MLMO_L6 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_I+WIP_N-2_ML_L60 | 0.083333 | 3.4167 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 60 sec requirement | Outage
F_QNV+MLTR_L5 | 0.083333 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_QNV++ML_L6_0400 | 0.083333 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_T+CSGO_TG_R6_4 | 0.083333 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment4 | Outage
F_T++NIL_BLSPS_R60_3 | 0.083333 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 3, FCSPS unavailable | NIL
F_QNV++ML_L5_0400 | 0.083333 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_S+LREG_0035 | 0.083333 | 17.8333 | SA Lower Regulation FCAS Requirement greater than 35 MW | Outage
F_T++FARE_N-2_TG_R60 | 0.083333 | 0.083333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T+CSGO_TG_R6_3 | 0.083333 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment3 | Outage
F_MAIN++WIP_N-2_MLL5 | 0.083333 | 0.75 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 5 Min requirement, Basslink able to transfer FCAS | Outage
F_MAIN++WIPN-2_MLL60 | 0.083333 | 0.75 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 60 sec requirement, Basslink able to transfer FCAS | Outage
F_T+CSGO_TG_R6_2 | 0.083333 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment2 | Outage
F_T+FASH_N-2_TG_R6_3 | 0.083333 | 0.083333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment3 | Outage
F_S+NIL_HPR_G+L_LREG | 0.083333 | 0 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS LowerReg ramping constraint | NIL
F_T++CSGO_TG_R6 | 0.083333 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_S++OSB_R6_2 | 0.083333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA, Segment 2 | Outage

## Binding Impact
Constraint Equation ID | 2019 Marginal Values | 2018 Marginal Values | 2019 Hours | 2018 Hours | Description | Type | Region
S_WIND_1200_AUTO & S_NIL_STRENGTH_1 | 8084357.5743 | 13582752.5298 | 669 | 1094.4167 | Upper limit (1300 to 1750 MW) for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements. Automatically swamps out when required HIGH combination is online. | NIL | SA
N>N-NIL_CLDP_1 | 5628169.9325 | 0 | 443.5 | 0 | Out= Nil, avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | NIL | NSW
N_SILVERWF_MAX | 3656611.4042 | 1562642.1245 | 267.0833 | 119.0833 | Limit MW output of Silverton wind farm to not exceed 131 MW with Broken Hill solar generating | Outage | NSW
T>T_NIL_110_1 | 3244766.4534 | 1518119.5609 | 251.5833 | 118.0833 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Tas
F_MAIN+NIL_DYN_RREG | 2708935.0518 | 541024.5211 | 3535.3333 | 1076.3333 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL | FCAS
Q_CS_1100 | 2564013.8801 | 0 | 210.5 | 0 | Qld Central to Qld South upper transfer limit of 1100MW (discretionary) | Outage | Qld
N^^V_NIL_1 | 2543881.3387 | 1000022.8137 | 2105 | 1166.0833 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | NSW
Q_LILYSF1_ZERO | 1689078.4567 | 0 | 147.75 | 0 | Lilyvale Solar Farm upper limit of 0 MW | Outage | Qld
F_T_AUFLS2_R6 | 1581843.1973 | 439302.184 | 5076.5 | 1382.1667 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL | FCAS
N_STWF1_ZERO | 1548348.9304 | 589083.1609 | 118.5833 | 45.3333 | Silverton wind farm upper limit of 0 MW | Outage | NSW
N_BROKENHSF_FLT_26 | 1429240.3057 | 0 | 127.8333 | 0 | Limit Broken Hill Solar Farm upper limit to 26 MW to manage post contingent voltage oscillation | NIL | NSW
Q_CS_1850 | 1377378.7018 | 0 | 212.9167 | 0 | Qld Central to Qld South upper transfer limit of 1850MW (discretionary) | Outage | Qld
S>V_NIL_SETX_SETX1 | 1332092.373 | 0 | 218.4167 | 0 | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL | SA
S_PLN_ISL_01 | 1330852.7169 | 0 | 7.5833 | 0 | Out = Cultana to Yadnarie (via Middleback Tee) 132kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
V_MTMERCER_ZERO | 1193661.6379 | 16643.4278 | 89.0833 | 1.25 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
N_BROKENH1_ZERO | 1120113.3125 | 15498.6414 | 85.1667 | 1.1667 | Broken Hill Solar Farm upper limit of 0 MW | Outage | NSW
V_BANSF_BBD_60 | 1023512.6408 | 0 | 79.9167 | 0 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Vic
V_BANNERTSF_FLT_0 | 950617.7562 | 0 | 72.3333 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V_WEMENSF_FLT_0 | 906918.1398 | 0 | 100.5833 | 0 | Limit Wemen Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
Q>NIL_COLNVSF1 | 905855.2266 | 0 | 86.4167 | 0 | Out = Nil, Limit Collinsville Solar Farm to thermal rating of Powerlink's RMU | NIL | Qld
V_GANWRSF_FLT_25 | 899364.8397 | 0 | 231.6667 | 0 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | NIL | Vic
V_GANWR_SF_BAT_50 | 894670.4805 | 0 | 16.8333 | 0 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Vic
S>V_NIL_NIL_RBNW | 894161.8111 | 195921.3558 | 330.8333 | 315 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL | SA
N_COLEASF1_ZERO | 804083.8048 | 94022.1295 | 55.25 | 7.4167 | Coleambally solar farm upper limit of 0 MW | Outage | NSW
S_HALWF2_0 | 803222.3856 | 161194.4544 | 59.1667 | 12.75 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | SA
S_HALWF_0 | 796089.0003 | 0 | 60.5833 | 0 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW | Outage | SA
V_OWF_TGTSNRBHTN_30 | 795516.0394 | 335465.8393 | 65.5833 | 26.0833 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Vic
V>>V_NIL_3 | 788396.9359 | 409.8728 | 8.0833 | 0.5 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL | Vic
V_MACARTHUR_ZERO | 775383.7835 | 3367.7312 | 311.6667 | 0.33333 | Macarthur upper limit of 0 MW | Outage | Vic
Q>X_CPWO_BI_INTACT | 773115.987 | 0 | 96.25 | 0 | Out= 813+815 or 814,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines,7104 and 7105(T022 Callide A to T152 Gladstone South) 132 kV lines open with 132 kV intact/split btw T022 Callide A and H015 Lilyvale, Feedback | Outage | Qld
V_OAKHILL_TFB_42 | 758019.1767 | 268832.4489 | 48.4167 | 20.6667 | Out = Nil, Oaklands Hill Windfarm upper limit of 42.7 MW due to Oaklands Hill windfarm TFB mode operation, DS only. Swamp out if TFB mode is OFF | NIL | Vic
F_S++HYSE_L60 | 732902.7202 | 31140.3029 | 433.9167 | 7.3333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage | FCAS
V_MURRAWRWF_FLT_25 | 696606.5086 | 0 | 53.6667 | 0 | Limit Murra Warra Wind Farm upper limit to 25 MW to manage system stability on the next contingency due to voltage oscillation | Outage | Vic
V_BANSF_45_22INV | 695856.7734 | 0 | 52.0833 | 0 | Limit Bannerton Solar Farm upper limit to 45 MW with max 22 inverter available, upper limit set to 0 MW if number of inverter available exceed 22. This is to manage voltage oscillation | Outage | Vic
F_T+NIL_WF_TG_R6 | 680382.4102 | 478720.9504 | 1278.5 | 1074 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
S-DLBAT-G_0 | 652500 | 0 | 3.75 | 0 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW | Outage | SA
V>V_ELTS_TX_R2 | 611543.8835 | 0 | 46.75 | 0 | Out = Elaine R2 220/132kV transformer, limit Mt Mercer WF MW output to avoid overloading the remaining in service R1 220/132kV transformer. | Outage | Vic
Q_CLST_STRGTH_MEWF | 610820.3928 | 0 | 47.5833 | 0 | Out = 855 or 8873 or 8874 or 856 or 8831, limit Mt Emerald WF to 50% capacity (26 turbines) if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=3 + Gladstone >=3 + (Stan+Cal+Glad >=10) + Haughton >0 + Sun Metals >0. Zero otherwise. | Outage | Qld
NSA_Q_BARCALDN | 594049.7646 | 326982.8027 | 40.0833 | 29.4167 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Qld
V_T_NIL_FCSPS | 592891.9397 | 38525.5556 | 966.25 | 107.25 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Vic
S>>PARB_RBTU_WEWT | 582902.0033 | 16262.8896 | 195.25 | 25.8333 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
N_BROKENHSF_FLT_0 | 580557.7778 | 0 | 44.8333 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | NSW
V_VS_LB_CAN_50 | 558165.3316 | 0 | 47.4167 | 0 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage | SA
N_BROKENHSF_FLT_30 | 550601.6203 | 0 | 43.5833 | 0 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | NSW
V::V_1900 | 507500 | 0 | 2.9167 | 0 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Vic
N_MOREESF1_ZERO | 489990.2891 | 0 | 36.0833 | 0 | Moree Solar Farm upper limit of 0 MW | Outage | NSW
V_MURRAWRWF_FLT_50 | 477683.4882 | 0 | 37.5 | 0 | Limit Murra Warra Wind Farm upper limit to 50 MW to manage system stability on the next contingency due to voltage oscillation | Outage | Vic
S_DVRB_270 | 477046.6253 | 0 | 51.0833 | 0 | Out = DV-BL 275kV line Or MK-RB 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF + Hallet Hill WF (i.e. generation + load component) <= 270 MW | Outage | SA
V_KIATAWF_FLT_0 | 474476.6365 | 0 | 271.1667 | 0 | Limit Kiata Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
Q>>WOPW_WOSP_WOGP_2 | 457838.8046 | 0 | 191.0833 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
F_S++HYSE_L6_1 | 457495.6124 | 7500.2296 | 375.8333 | 8.0833 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage | FCAS
S>NIL_NIL_NWMH2 | 450786.0819 | 29101.0599 | 59.5833 | 10.6667 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
F_I+LREG_0210 | 433292.9139 | 0 | 2080.0833 | 0 | NEM Lower Regulation Requirement greater than 210 MW | NIL | FCAS
T_MRWF_QLIM_xx | 433109.7214 | 53843.5906 | 30.9167 | 4.0833 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Tas
F_T+NIL_MG_RECL_R6 | 420950.384 | 324887.7909 | 1669.3333 | 1350.1667 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
Q>CPWO_B_CAGS_CALV_C | 412765.3497 | 0 | 67.1667 | 0 | Out= 813+815 or 814+816,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines,7104 and/or 7105 (T022 Callide A to T152 Gladstone South)132 kV lines close with 132 kV intact btw T022 Callide A and H015 Lilyvale, Feedback | Outage | Qld
Q_NIL_STRGTH_MEWF | 405396.1337 | 0 | 32.1667 | 0 | Out = Nil, limit Mt Emerald WF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to TOA 393 | NIL | Qld
F_I+RREG_0220 | 402238.1693 | 0 | 1272.5 | 0 | NEM Raise Regulation Requirement greater than 200 MW | NIL | FCAS
S>>X_CNRB+CB_01 | 401303.2211 | 0 | 39.9167 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
N_SILVERTWF_FLT_0 | 401151.2848 | 0 | 30.0833 | 0 | Limit Silverton Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | NSW
F_I+LREG_0210 | 390955.4148 | 0 | 2047.0833 | 0 | NEM Lower Regulation Requirement greater than 210 MW | Other | FCAS
F_T+RREG_0050 | 390284.4628 | 337884.9104 | 1145.6667 | 1752.8333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
V_GANWRSF_FLT_0 | 389691.807 | 0 | 166.5833 | 0 | Limit Gannawarra solar farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V_WEMENSF_45_21INV | 376509.9359 | 0 | 28.0833 | 0 | Limit Wemen Solar Farm upper limit to 45 MW with max 21 inverter available, upper limit set to 0 MW if number of inverter available exceed 21. This is to manage voltage oscillation | Outage | Vic
SVML_ZERO | 356708.3815 | 38914.9767 | 141.75 | 242.75 | SA to Vic on ML upper transfer limit of 0 MW | Outage | SA
F_T+LREG_0050 | 353986.6038 | 271971.3372 | 1198.25 | 2351.9167 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
V_CWWF_FLT_50 | 340589.0505 | 0 | 27.0833 | 0 | Limit Crowlands Wind Farm upper limit to 50 MW to manage system stability on the next contingency | Outage | Vic
Q^^NIL_QNI_SRAR | 338816.6768 | 0 | 800.5833 | 0 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Qld
S_HPRG1_E | 335197.7915 | 275838.0574 | 8.6667 | 31.0833 | Out= Nil, Hornsdale Battery generation energy target <= 30 MW | NIL | SA
N_MBTE1_B | 334940.1455 | 120502.648 | 475.75 | 126.5833 | Out= one Directlink cable, Qld to NSW limit | Outage | NSW
S:V_500_HY_TEST | 331467.3492 | 10071.2765 | 144.9167 | 17.1667 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
S:V_500_HY_TEST_DYN | 330410.1469 | 54435.4071 | 212.4167 | 78.4167 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
F_T+NIL_MG_R6 | 318836.4857 | 364786.5503 | 743.25 | 1230.0833 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_I+NIL_MG_R6 | 311558.3065 | 256098.6958 | 6288.5833 | 4517 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL | FCAS
N_BKHSF_44INV | 307464.4715 | 0 | 22.1667 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 44. Constraint swamp out if number of inverter available not exceed 44. This is to manage voltage oscillation. DS only | Outage | NSW
S_DVRB2_270 | 305778.8316 | 78852.9709 | 70.0833 | 29.25 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | SA
Q_STR_233310_MEWF_26 | 301042.6966 | 0 | 23.0833 | 0 | Limit MT Emerald WF to 50% of max capacity (#26 turbine) if Kareeya > = 2 and Stanwell >= 3 and Callide >= 3 and Gladstone> = 3 and total of Stanwell, Callide and Gladstone >=10. Limit to zero otherwise. | Outage | Qld
T_TAMARCCGT_GCS | 300171.9948 | 98388.4384 | 27.25 | 61.5 | Tamar Valley 220 kV CCGT Generation Control Scheme (GCS) constraint to manage effective size of generation contingency for loss of Tamar CCGT. Limit output of Tamar CCGT based on load available and/or armed for shedding by Tamar GCS. | NIL | Tas
F_I+RREG_0220 | 298495.5446 | 0 | 1240 | 0 | NEM Raise Regulation Requirement greater than 200 MW | Other | FCAS
F_S+TL_L6_OD | 296421.5599 | 9386.1841 | 4.8333 | 0.25 | Lower 6 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
V_KARADSF_FLT_45 | 290377.5484 | 0 | 163.5833 | 0 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | NIL | Vic
S>>PARB_RBTU_WTTP | 290187.5419 | 4256.4509 | 71.5 | 7.25 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
NRM_VIC1_NSW1 | 286368.6673 | 0 | 10.6667 | 0 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue
S>NIL_TINO3_TINO4 | 282427.2767 | 55.4436 | 24.75 | 0.083333 | Out = Nil, avoid O/L of TIPS-New Osborne #4 66kV line on trip of TIPS-New Osborne #3 66kV line (Note: Assumed CB 5536 at New Osborne is CLOSED). This constraint swamps out if New Osborne CB 5536 is OPEN. | NIL | SA
N_BKHSF_30_44INV | 277030.7961 | 0 | 20.9167 | 0 | Limit Broken Hill Solar Farm upper limit to 30 MW with max 44 inverter available, upper limit set to 0 MW if number of inverter available exceed 44. This is to manage voltage oscillation | Outage | NSW
V_MURRAWRWF_FLT_0 | 272157.5749 | 0 | 28 | 0 | Limit Murra Warra Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V_KIATA_ISL_0 | 270806.3781 | 0 | 127.9167 | 0 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
F_MAIN++NIL_MG_R60 | 258953.8326 | 276004.9275 | 2128.8333 | 2460.5833 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS
S-TBTX4_TBSF1_80 | 255155.7784 | 0 | 19.6667 | 0 | Out =Tailem Bend 132/275 kV #4 Transformer O/S, constrain Tailem Bend (Coorong) Solar PV to 80 MW to manage voltage collapse for trip of Tailembend-Mobilong 132kV line | Outage | SA
V_WEMENSF_FLT_44 | 254537.5348 | 0 | 97.25 | 0 | Limit Wemen Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | NIL | Vic
F_MAIN+NIL_MG_R6 | 253671.0696 | 398917.722 | 1199.6667 | 2281 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
V_KARADSF_FLT_0 | 245975.6804 | 0 | 141.0833 | 0 | Limit Karadoc solar farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V_CWWF_GFT_5 | 245464.9989 | 0 | 18.5833 | 0 | Out= Crowlands WF associated fast tripping scheme (disabled), Limit Crowlands Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
F_MAIN+LREG_0210 | 244273.7961 | 0 | 676.9167 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL | FCAS
Q_STR_233310_MEWF_39 | 240776.2939 | 0 | 19.0833 | 0 | Limit MT Emerald WF to 75% of max capacity (#39 turbine) if Kareeya > = 2 and Stanwell >= 3 and Callide >= 3 and Gladstone> = 3 and total of Stanwell, Callide and Gladstone >=10. Swamp during night. Limit to zero otherwise. | Outage | Qld
V^^SML_NSWRB_2 | 240622.3496 | 0 | 59.1667 | 0 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Vic
T_LIPM_PMWA_1_N-3 | 239317.6836 | 0 | 115.9167 | 0 | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to <= southern load + 15 MW | Outage | Tas
Q_CLST_STRGTH_HAUSF | 237698.1059 | 0 | 18.6667 | 0 | Out = 855 or 8873 or 8874 or 856 or 8831, limit Haughton SF to 50% capacity (40 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=3 + Gladstone >=3 + (Stan+Cal+Glad >=10). Zero otherwise. | Outage | Qld
Q_CLST_STRGTH_SMSF | 235624.3823 | 0 | 18.5 | 0 | Out = 855 or 8873 or 8874 or 856 or 8831, limit Sun Metals SF to 50% capacity (40 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=3 + Gladstone >=3 + (Stan+Cal+Glad >=10). Zero otherwise. | Outage | Qld
Q_STR_233310_HASF_40 | 235501.1658 | 0 | 18.75 | 0 | Limit Haughton SF to 50% of max capacity (#40 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
T>T_NIL_BL_110_18_1 | 233115.2278 | 92735.7046 | 24.5833 | 26.75 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
F_MAIN+NIL_MG_R60 | 232547.9869 | 277623.1052 | 1199.6667 | 2282.9167 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
V_BANSF_22INV | 229987.8699 | 0 | 17.9167 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 22. Constraint swamp out if number of inverter available not exceed 22. This is to manage voltage oscillation. DS only | Outage | Vic
Q_STR_43249_SMSF_38 | 229169.8293 | 0 | 18 | 0 | Limit Sun Metals SF to 50% capacity (38 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=4 + (Stan+Cal+Glad >=9). Zero otherwise. | Outage | Qld
Q_STR_43249_HASF_40 | 227233.6204 | 0 | 18 | 0 | Limit Haughton SF to 50% capacity (40 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=4 + (Stan+Cal+Glad >=9). Zero otherwise. | Outage | Qld
S>KNPW_SETX_SETX1 | 221071.1707 | 1424.128 | 18.75 | 0.25 | Out=Penola West-Kincraig 132kV line, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | Outage | SA
S>>X_CNRB+CB_04 | 219077.8019 | 0 | 15.6667 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 132/275kV TX2 on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
V>V_NIL_7 | 219018.9261 | 1087.306 | 10 | 0.083333 | Out = NIL, prevent overload of either MBTS-DDTS 220 kV line (flow north) for trip of the EPS-TTS 220 kV line, feedback. | NIL | Vic
V_CWWF_5 | 218855.3942 | 0 | 16.5 | 0 | Crowlands Wind Farm total upper limit of 5 MW, limit to manage MW risk of islanding | Outage | Vic
F_I+NIL_MG_R60 | 218474.6851 | 179632.406 | 6098 | 4396.3333 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL | FCAS
F_I+NIL_MG_R5 | 201396.0639 | 757552.4563 | 6846.1667 | 5581.1667 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL | FCAS
S_SECB_LG-2 | 199273.7355 | 0 | 13.8333 | 0 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 2 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
S>>PATW_BWPA_TPRS | 196682.2904 | 145061.273 | 21.5 | 35.3333 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V^^S_NIL_MAXG_xxx | 179782.9748 | 14402.5801 | 4.0833 | 14.8333 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
S>NIL_HUWT_STBG2 | 178507.7541 | 4267.444 | 15.3333 | 0.33333 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL | SA
Q>NIL_SRMB_M020/1 | 176401.4941 | 0 | 14.1667 | 0 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Qld
F_I+LREG_0120 | 174143.7877 | 430085.6586 | 1578.25 | 3920.1667 | NEM Lower Regulation Requirement greater than 120 MW | NIL | FCAS
F_T+NIL_MG_RECL_R60 | 173964.476 | 88384.7133 | 1711.25 | 1371.5833 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 172627.6603 | 70186.0854 | 230.75 | 144.5833 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Qld
Q>>CPPW_WOSP_WOGP_2 | 167361.0385 | 0 | 26.5833 | 0 | Out= Calliope River to Palmwoods (813+815+810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
N_GUNNING1_ZERO | 166425.3591 | 0 | 12.75 | 0 | Gunning unit upper limit of 0 MW | Outage | NSW
Q_STR_43249_MEWF_26 | 165989.9024 | 0 | 13.0833 | 0 | Limit Mt Emerald WF to 50% capacity (26 turbines) if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=4 + (Stan+Cal+Glad >=9) + Haughton >0 + Sun Metals >0. Zero otherwise. | Outage | Qld
F_MAIN++NIL_MG_R6 | 162896.1524 | 331057.7381 | 1764.8333 | 2339.1667 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS
F_T_NIL_MINP_R6 | 159708.0994 | 293912.5375 | 1227 | 1277.8333 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL | FCAS
TV_150 | 159598.7313 | 0 | 21.25 | 0 | Tas to Vic on Basslink upper limit of 150 MW | Outage | Tas
SA_ISLE_STRENGTH | 158914.6217 | 0 | 15.8333 | 0 | Maximum limit (1300 MW) for SA non-synchronous generation for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
V_BANNERTSF_FLT_44 | 154575.839 | 0 | 12.25 | 0 | Limit Bannerton Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | NIL | Vic
V_SV_MLMO_NETT | 153677.9979 | 0 | 105.4167 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW. Swamp out when MOPS/DUNDWF not generating | Outage | Vic
T_WIND_100 | 149418.9115 | 0 | 8.9167 | 0 | Limit output of TAS wind generation to less than 100 MW. Note, due to 144 MW rating of Non-Scheduled Woolnorth Wind Farm, directions may be required to reduce Woolnorth MW output if this constraint violates | Outage | Tas
N_X_MBTE2_A & N_X_MBTE2_B | 148266.3023 | 18624.8162 | 212 | 302.9167 | Out= two Directlink cables, NSW to Qld limit | Outage | NSW
Q_STBS_STRGTH_MEWF | 144327.6442 | 0 | 11.3333 | 0 | Out = 856+822, limit Mt Emerald WF to 50% capacity (26 turbines) if Kareeya >=2 and Invicta is ON and Stanwell >=3 + Callide >=3 + Gladstone >=3 and Stan+Cal+Glad >=10 + Haughton >0 + Sun Metals >0. Zero otherwise. | Outage | Qld
V_MURRAWRWF_MAX | 142820.3209 | 0 | 174.5833 | 0 | Limit MW output of Murra Warra wind farm to hold point levels during day/night | Outage | Vic
S>NIL_BWMP_HUWT | 140837.5144 | 25345.6255 | 8.5 | 0.91667 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
S>VMLMHNW1 | 139616.8993 | 1.3222 | 76.9167 | 0.083333 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | SA
S^SETX_GEN_CAP | 138435.3051 | 0 | 27.5 | 0 | Out= One South East 275/132kV transformer O/S, avoid local voltage collapse on trip of remaining South East transformer, | Outage | SA
F_T+NIL_WF_TG_R60 | 137687.9406 | 74114.6853 | 1345.75 | 1121 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
V_MWWF_GFT_5 | 137008.0965 | 0 | 10.4167 | 0 | Out= Murra Warra WF associated fast tripping scheme (disabled), Limit Murra Warra Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
S>VMLMHNW2 | 136263.8479 | 0 | 29 | 0 | Out=Monash-North West Bend #2 132kV line, SA-V on ML avoid overload on North West Bend-Monash #1 132kV line, feedback | Outage | SA
Q_STBS_STRGTH_SMSF | 131936.5448 | 0 | 10.3333 | 0 | Out = 856+822, limit Sun Metals SF to 50% of max capacity (38 inverters) if Kareeya >=2 and Invicta is ON and Stanwell >=3 + Callide >=3 + Gladstone >=3 and Stan+Cal+Glad >=10. Zero otherwise. | Outage | Qld
V>>V_NIL_1B | 130500 | 92094.2854 | 0.75 | 1.9167 | Out = Nil, avoid O/L Murray to Dederang No.2 330kV line (flow MSS to DDTS) for loss of the parallel No.1 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
V_OWF_NRB_0 | 129875.9871 | 62034.4505 | 9.6667 | 4.8333 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Vic
F_MAIN+NIL_DYN_LREG | 129647.1208 | 119630.1339 | 328.8333 | 534.75 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL | FCAS
N_FINLYSF1_ZERO | 129062.464 | 0 | 4.6667 | 0 | Finley solar farm upper limit of 0 MW | Outage | NSW
S>NIL_NIL_SETX12 | 125723.7564 | 83169.2698 | 16.3333 | 5.5 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
Q_STBS_STRGTH_HAUSF | 125687.1685 | 0 | 9.9167 | 0 | Out = 856+822, limit Haughton SF to 50% of max capacity (40 inverters) if Kareeya >=2 and Invicta is ON and Stanwell >=3 + Callide >=3 + Gladstone >=3 and Stan+Cal+Glad >=10. Zero otherwise. | Outage | Qld
V_HM_VIC_ZERO | 125430.5921 | 0 | 9.1667 | 0 | Hume VIC unit upper limit of 0 MW | Outage | Vic
F_MAIN+RREG_0220 | 123237.0721 | 0 | 323.25 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL | FCAS
F_I+LREG_0170 | 121294.4888 | 0 | 673.0833 | 0 | NEM Lower Regulation Requirement greater than 170 MW | Other | FCAS
S^NIL_PL_MAX | 120722.2791 | 264096.2377 | 2.75 | 9.5833 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
T_MRWF_ZERO | 118190.6664 | 0 | 8.6667 | 0 | Discretionary 0 MW upper limit on Musselroe Wind Farm | Outage | Tas
Q_RRSF1_ZERO | 118142.3883 | 0 | 9.25 | 0 | Ross River solar farm upper limit of 0 MW | Outage | Qld
Q>NIL_BI_CAGS_CALV_O | 117980.2119 | 7318.1464 | 82.9167 | 33.6667 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104/7105 (T022 Callide A to T152 Gladstone South) 132 kV lines closed with 132 kV split between T022 Callide A and H015 Lilyvale. | NIL | Qld
F_I+LREG_0190 | 115958.7117 | 0 | 688.75 | 0 | NEM Lower Regulation Requirement greater than 190 MW | Other | FCAS
F_V_APD01_R60 | 114404.9163 | 66.8742 | 598.6667 | 0.66667 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage | FCAS
T>T_NWSD_110_1 | 113139.9067 | 0 | 8.9167 | 0 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752, avoid O/L Scottsdale Tee to Norwood 110kV line on Nil trip, Feedback | Outage | Tas
S>V_NWRB_RBMWP3 | 105345.3961 | 0 | 9 | 0 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage | SA
F_MAIN+LREG_0210 | 103747.1247 | 0 | 303.5833 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | Other | FCAS
Q>EMBW_NIL_EMLV_DS | 102517.7769 | 0 | 12.5 | 0 | Out= 6056 or 6011 Emerald - Comet - Blackwater 66kV line ,limit Emerald SF to 40MW avoid overloading on Emerald - Lilyvale 66kV line, swap if Emerald CBs S612 or S610 or Blackwater CB S605 is closed (DS only) | NIL | Qld
F_T+NIL_WF_TG_R5 | 101872.1492 | 78031.946 | 1315 | 948.5833 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
Q_RGBYRSF1_ZERO | 101808.623 | 0 | 8 | 0 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Qld
S_WATERLWF_RB | 100126.2333 | 207403.9713 | 10.9167 | 16.6667 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | SA
S>NIL_SGBN_SGSE-T2 | 99915.109 | 105339.3463 | 30.9167 | 11.75 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
F_T++RREG_0050 | 98631.6362 | 111814.9603 | 535.3333 | 510.0833 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
F_V_APD01_R6 | 98258.797 | 130.26 | 598.25 | 0.66667 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage | FCAS
F_S+TL_L60_OD | 98196.49 | 30997.69 | 4.8333 | 0.25 | Lower 60 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
V^^N_NIL_1 | 96626.9711 | 57328.8963 | 150.75 | 67.5 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Vic
SVML_ROC_80 | 92916.3038 | 39228.1946 | 27.8333 | 47.5833 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
F_T+NIL_MG_R5 | 92721.6834 | 60187.8736 | 822.5 | 941.4167 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
V_CWWF_ISL_0 | 91926.1148 | 0 | 7.1667 | 0 | Crowlands Wind Farm total upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
S>X_DV-BR-PA_08 | 89176.8855 | 0 | 6.25 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Hummocks-Waterloo 132kV lineon trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
NSA_V_BDL0xxx | 88242.7499 | 224446.4483 | 3.5833 | 2.4167 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Vic
Q>NIL_BI_xxx | 87292.2936 | 136204.5911 | 130.1667 | 98.8333 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104 and 7105 (T022 Callide A to T152 Gladstone South) 132 kV lines open with 132 kV intact/split between T022 Callide A and H015 Lilyvale. | NIL | Qld
V_YENDWF_MAX | 86854.7926 | 0 | 31.6667 | 0 | Limit MW output of Yendon wind farm to hold point levels during day/night | Outage | Vic
Q_STR_43239_HASF_40 | 85845.2153 | 0 | 6.8333 | 0 | Limit Haughton SF to 50% capacity (40 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=3 + (Stan+Cal+Glad >=9). Zero otherwise. | Outage | Qld
F_S++OSB_R6_1 | 85120.2784 | 1038.0672 | 4.25 | 0.33333 | Raise 6 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA, Segment 1 | Outage | FCAS
V_ARARATWF_FLT_0 | 84613.4693 | 0 | 28.5833 | 0 | Limit Ararat Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
S-SNWWF_0 | 81857.4785 | 0 | 6.25 | 0 | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
V>>V_NIL_1A | 81413.6117 | 433616.5918 | 0.5 | 9.6667 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
S>SE6161_SETX2_SGBL | 80754.1944 | 601071.676 | 18.4167 | 66.8333 | Out= South East 132kV CB6161, avoid O/L Snuggery-Blanche 132kV line on trip of South East 132/275 TX2 ( this offloads Mayura-South East T 132kV line), Feedback | Outage | SA
V>>V_NIL_5 | 80401.3317 | 1897.642 | 14.4167 | 2.25 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Vic
F_MAIN+RREG_0220 | 78976.7366 | 0 | 183.9167 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | Other | FCAS
Q>>WOSP_WOPW_WOGP_2 | 77099.056 | 0 | 2.75 | 0 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Qld
V_BANNERTON_ZERO | 76995.7283 | 217721.5637 | 5.6667 | 16.25 | Bannerton Solar Farm upper limit of 0 MW | Outage | Vic
S>NIL_LKDV_CNRB | 76608.3841 | 2363.829 | 4.0833 | 0.25 | Out= NIL, avoid O/L Canowi-Robertstown 275kV on trip of Mt Lock-Davenport 275kV line, Feedback | NIL | SA
Q:NIL_CS | 75571.0837 | 2748.6657 | 57.75 | 7.5 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW) | NIL | Qld
F_I+RREG_0200 | 74552.2749 | 0 | 426.0833 | 0 | NEM Raise Regulation Requirement greater than 200 MW | Other | FCAS
V_MORTLAKE12_150 | 74365.4169 | 0 | 30.6667 | 0 | Mortlake unit 1 & 2 upper limit of 150 MW | Outage | Vic
V_KIATAWF_FLT_15 | 74138.9107 | 0 | 45.1667 | 0 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
Q^WOPW_CS_WOSP_O | 70854.6533 | 0 | 20.25 | 0 | Out= Any of the 275kV lines between Woolooga to South Pine (807,808 or 810),avoid voltage instability on CQSQ on trip of the remaining 275kV Parallel line lines between Woolooga to South Pine (807,808 or 810) (132kV and 110kV parallel network open) | Outage | Qld
F_T++NIL_MG_RECL_R6 | 70472.7016 | 57267.99 | 215.8333 | 162.4167 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
Q:NIL_OAKEY2SF | 70202.6565 | 0 | 41.9167 | 0 | Limit Oakey 2 solar farm to 0MW when Oakey GT is online to prevent transient instability for 3 phase fault at Tangkam | NIL | Qld
Q>X_CPWO2_CPWU_CPWO1 | 68365.8082 | 0 | 31.9167 | 0 | Out= Calliope River to Woolooga (814+816) line, avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (813+815) line, Feedback | Outage | Qld
V>>V-LTWG_RADIAL_2 | 67501.6692 | 0 | 3.1667 | 0 | Outage = Lower Tumut to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload Murray to Dederang No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings; Feedback | Outage | Vic
Q_CS_1700 | 67012.6311 | 0 | 41 | 0 | Qld Central to Qld South upper transfer limit of 1700MW (discretionary) | Outage | Qld
N>>N-NIL_996_IN | 65769.045 | 0 | 0.41667 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback | NIL | NSW
N_SILVERWF_WT | 65189.0814 | 3230.041 | 4.8333 | 0.25 | Limit number of turbine online for Silverton wind farm to not exceed 38 with Broken Hill solar generating | Outage | NSW
F_T+NIL_MG_RECL_R5 | 63312.5873 | 76621.8266 | 1506 | 1249.75 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
V_SALTCREEK_ZERO | 63033.5183 | 0 | 4.6667 | 0 | Salt Creek wind farm upper limit of 0 MW | Outage | Vic
F_S++HYSE_L5 | 60428.4638 | 11.9375 | 99.8333 | 0.5 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage | FCAS
T_T_FASH_10_N-2 | 60216.04 | 0 | 0.66667 | 0 | Out = NIL, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain John Butters and Bastyan to 0 MW as per TAS Networks advice | Outage | Tas
VT_000 | 60208.357 | 0 | 44.0833 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Vic
V>>V_NIL_8 | 60195.4279 | 200212.9906 | 7.1667 | 12 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL | Vic
V_BANNERTSF_ISL_0 | 58773.8296 | 0 | 4.4167 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Vic
N>N-NIL_DC | 58668.1414 | 29041.3331 | 83.75 | 87.25 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL | NSW
V_KARSF_12INV | 58515.0626 | 0 | 17.25 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out otherwise. This is to manage voltage oscillation. DS only | Outage | Vic
S_NBH_0 | 57922.3585 | 0 | 4.3333 | 0 | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | SA
S:VS_650_HY_TEST_DYN | 56498.97 | 16090.1156 | 30 | 11 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
S>BRTW_BWPA_HUWT | 55665.8181 | 1440.3125 | 2.5 | 0.083333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T>T_LIPM_110_2A | 55547.9602 | 6101.2296 | 101.1667 | 2.5833 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
V^SML_NSWRB_2 | 55546.4455 | 151775.6622 | 6 | 60.1667 | Out = NSW Murraylink runback scheme, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | NIL | Vic
S>NWCB6024+25_TX3 | 54575.884 | 0 | 14.3333 | 0 | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | SA
F_S++HYSE_L6_2 | 53938.9675 | 0 | 11.1667 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage | FCAS
Q_CS_1600 | 52103.3044 | 0 | 18.5833 | 0 | Qld Central to Qld South upper transfer limit of 1600MW (discretionary) | Outage | Qld
V_KARSF_45_21INV | 51232.1899 | 0 | 43.6667 | 0 | Limit Karadoc Solar Farm upper limit to 45 MW with max 21 inverter available, upper limit set to 0 MW if number of inverter available exceed 21. This is to manage voltage oscillation | Outage | Vic
F_T++NIL_MG_RECL_R5 | 50776.277 | 16096.4222 | 194.8333 | 71.4167 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
T>T_FASH_1_N-2 | 50182.0448 | 12997.2081 | 6.8333 | 10.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, limit Bastyan, John Butters & Mackintosh to west coast load plus Hampshire link line rating | Outage | Tas
S_CNLK_270 | 50175.196 | 0 | 5.9167 | 0 | Out =Canowie-Mt Lock 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3 + Hornsdale battery (i.e. generation + load component)<= 270 MW | Outage | SA
N>N-FLML_9R4 | 49802.609 | 0 | 4 | 0 | Out= Finley to Mulwala (9R4) or Mulwala to Corowa(997/2) or Corowa to Albury (997/1), avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | Outage | NSW
F_MAIN+TASCAP_RREG | 47094.8578 | 16648.2278 | 639.1667 | 241.0833 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS
F_MAIN+NIL_MG_R5 | 47082.6254 | 493839.7628 | 1198.6667 | 2279.4167 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
S>>NIL_TBTU_TBMO_1 | 46853.8367 | 70.9652 | 3.9167 | 0.75 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
S_WIMK_270 | 46482.0717 | 0 | 3.6667 | 0 | Out =Willalo-Mokota 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF <= 270 MW | Outage | SA
S>>X_RBPA+BGTX_04 | 46111.0378 | 0 | 7.6667 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
V_MWWF_5 | 44138.227 | 0 | 3.3333 | 0 | Murra Warra Wind Farm upper limit of 5 MW | Outage | Vic
T_T_FASH_3_N-2 | 44100 | 14501.8966 | 0.25 | 6.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain Reece Unit 1 to 0 MW as per TAS Networks advice | Outage | Tas
F_Q++BCDM_L6 | 43574.9958 | 42560.2093 | 142.75 | 82.9167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage | FCAS
N^^V_MSUT_1 | 43198.0987 | 618.0509 | 21 | 2.1667 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
S>LFTI_PPPW_NOTI4 | 43184.2064 | 0 | 2.8333 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L New Osborne-TIPS #4 66kV line, on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | SA
T::T_HA_GT_PM_4 | 42057.2059 | 16584.7657 | 5.4167 | 9.1667 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Tas
S>>PARB_RBTU_RBMWP4 | 41827.1521 | 0 | 12 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
F_TASCAP_RREG_0180 | 41579.5232 | 0 | 345.6667 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | Other | FCAS
Q_STR_43239_MEWF_26D | 41235.837 | 0 | 3.3333 | 0 | Limit Mt Emerald WF to 50% capacity (26 turbines) if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=3 + (Stan+Cal+Glad >=9) + Haughton >0 + Sun Metals >0. Zero otherwise. | Outage | Qld
F_T+FASH_N-2_RREG | 41063.7043 | 7273.5676 | 17.1667 | 25.9167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | FCAS
NRM_NSW1_VIC1 | 39023.559 | 18794.8279 | 2.75 | 2.5 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue
F_I+RREG_0180 | 38421.4233 | 0 | 437.0833 | 0 | NEM Raise Regulation Requirement greater than 180 MW | Other | FCAS
N^^V_BUDP_1 | 38102.1805 | 1113.9697 | 36 | 1.5833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
S_SECB_LG3 | 37181.6688 | 16946.8952 | 2.6667 | 1.25 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
S>PATW_BWPA_HUWT | 36962.7365 | 4765.3088 | 2.6667 | 1.0833 | Out= Para-Templers West 275kV line, avoid O/L Hummocks- Waterloo132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V::N_HWSM_xxx | 36734.1849 | 1054.8256 | 82.75 | 8.6667 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>N-NIL_HA | 36418.491 | 24066.2253 | 60.5 | 29.9167 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Vic
SV_100 | 35740.1841 | 0 | 30.1667 | 0 | SA to Victoria on VicSA upper transfer limit of 100 MW | Outage | SA
S_PWSE_LG1 | 34979.0414 | 0 | 2.4167 | 0 | Out=Penola West-South East 132kV line, Oscillatory stability limit Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
S>X_RBPA+CB_01 | 34699.5979 | 217845.0338 | 3 | 12.8333 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
SV_250 | 34622.5812 | 0 | 23.3333 | 0 | SA to Victoria on Heywood upper transfer limit of 250 MW | Outage | SA
S>V_NWRB2_RBNW1 | 34426.9488 | 0 | 9.8333 | 0 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage | SA
S_WTE_0 | 34204.0644 | 0 | 2.6667 | 0 | Discretionary upper limit for Waterloo generation of 0 MW | Outage | SA
F_MAIN++LREG_0120 | 33358.7938 | 38428.1904 | 271.5 | 328 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL | FCAS
V_BANNERTSF_FLT_45 | 33091.7552 | 0 | 2.4167 | 0 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
CA_MQS_4C1211CB_02 | 32393.3688 | 0 | 2.5833 | 0 | Constraint Automation, O/L WATTEM_1 @W_LOO for CTG LSIT on trip of R_TOWN - PARA 275KV LINE. Generated by STNET[MANFL] Host MANEEMP1(MQ) | Outage | Constraint Automation
V_KARADSF_FLT_25 | 32289.5678 | 0 | 9.3333 | 0 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | Vic
F_TASCAP_LREG_0210 | 32160.6183 | 0 | 342 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | Other | FCAS
NRM_QLD1_NSW1 | 31694.3993 | 0 | 9.25 | 0 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue
T>T_NIL_BL_110_4 | 31404.0446 | 0 | 40.0833 | 0 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Tas
S>X_RBPA+CB_06 | 31290.4008 | 8889.0724 | 4.8333 | 0.75 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV #1 transformer on trip of Canowie-Robertstown(this this trips Hallet WF and Generation and splits Robertstown 275kV bus), Feedback | Outage | SA
F_Q++ARTW_L6 | 31023.7601 | 11879.8784 | 20.0833 | 83 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage | FCAS
T>>T_NIL_BL_EXP_5F | 30894.8207 | 1418.5756 | 0.58333 | 0.33333 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
S-BUPV1_0 | 30849.9068 | 47853.7469 | 2.25 | 3.6667 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | SA
S_TBL_0 | 30693.0452 | 0 | 2.0833 | 0 | Discretionary upper limit for The Bluff generation of 0 MW | Outage | SA
T_FARC1 | 30636.0259 | 14200 | 1 | 0.083333 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Tas
V_MLMO_VS_LB_CAN_50 | 30348.9156 | 0 | 18.5 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS/DUNDWF generating. | Outage | SA
T_FARC2 | 30150.1401 | 0 | 0.5 | 0 | Out=Farrell-Reece 2 220KV line. Energy <= 0MW | Outage | Tas
V>>DDSH_DDGN_N-2 | 29869.8492 | 15438.5853 | 1.1667 | 1.0833 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage | Vic
Q_NESTM_STRGTH_MEWF | 29345.8329 | 0 | 2.25 | 0 | Out = 822, Limit MT Emerald WF to 75% of max capacity (#40 turbine) if Kareeya > = 2 and Stanwell >= 3 and Callide >= 3 and Gladstone> = 3 and total of Stanwell, Callide and Gladstone >=10. Limit to zero otherwise. Swamp if Sun Metal+Haughton =0. | Outage | Qld
Q_NESTM_STRGTH_SMSF | 29345.6399 | 0 | 2.25 | 0 | Out = 822, Limit Sun Metal SF to 50% of max capacity (#38 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
V_KARSF_20_8INV | 29271.5959 | 0 | 17.1667 | 0 | Limit Karadoc Solar Farm upper limit to 20 MW with max 8 inverter available, upper limit set to 0 MW if number of inverter available exceed 8. This is to manage voltage oscillation | Outage | Vic
F_T+NIL_MG_R60 | 29230.2554 | 69053.3169 | 855.25 | 1329.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_TASCAP_RREG_0220 | 28797.0184 | 0 | 175.0833 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS
N>N-NIL_MBDU | 28753.5321 | 39.9128 | 65.75 | 1.25 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
S:V_550_HY_TEST | 27683.5912 | 0 | 0.5 | 0 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
V_T_NIL_BL1 | 27621.4212 | 31103.1857 | 61.3333 | 27.5 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL | Vic
V_WEMENSF_ZERO | 27358.9677 | 0 | 11.3333 | 0 | Wemen Solar Farm upper limit of 0 MW | Outage | Vic
T::T_NIL_2 | 27285.7135 | 0 | 51.4167 | 0 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL | Tas
V_MURRAWRWF_FLT_15 | 27267.3713 | 0 | 37.4167 | 0 | Limit Murra Warra Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
F_MAIN++NIL_MG_R5 | 27215.4973 | 309872.5953 | 1121.75 | 1615.9167 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS
Q::N_ARSVC_AR_2L-G | 27196.7862 | 1265.236 | 5.6667 | 14.9167 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
V>>N-NIL_HG | 27066.8196 | 8906.7718 | 15.5833 | 7.4167 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
N_TARALGAWF_ZERO | 26657.5946 | 0 | 2 | 0 | Taralga WF upper limit of 0 MW | Outage | NSW
V_GANNSF_30_12INV | 26249.0433 | 0 | 10 | 0 | Limit Gannawarra Solar Farm upper limit to 30 MW with max 12 inverter available, upper limit set to 0 MW if number of inverter available exceed 12. This is to manage voltage oscillation | Outage | Vic
F_T++LREG_0050 | 26070.6597 | 55733.3892 | 170.3333 | 708.75 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
S_PW-CB6156_LG1 | 26012.0243 | 201979.5804 | 2 | 15.4167 | Out=Penola West 132kV CB 6156 O/S (Note: with Penola West 132kV CB 6158 CLOSED), Oscillatory stability limit Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
N_FINLEYSF_49_INV | 25433.54 | 0 | 2 | 0 | Limit Finley Solar Farm upper limit to 0 MW if number of inverter available exceed 49. Dispatch only. swamped out if Inverters are within the limit. | Outage | NSW
V_ARARATWF_FLT_150 | 25413.508 | 0 | 11.3333 | 0 | Limit Ararat Wind Farm upper limit to 150 MW to manage system stability on the next contingency | Outage | Vic
F_S+SNS_TG_R6_1 | 25400.9143 | 0 | 2.8333 | 0 | Raise 6 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line, Segment1 | Outage | FCAS
N_X_MBTE_3A & N_X_MBTE_3B | 24983.0281 | 27924.6924 | 172.4167 | 251.8333 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | NSW
Q_STR_233310_SMSF_38 | 24163.9017 | 0 | 19.4167 | 0 | Limit Sun Metal SF to 50% of max capacity (#38 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
I_QNI_ONE_PHASE_N-2 | 23900.1975 | 118.571 | 33.9167 | 1.4167 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage | Other
N>N-FLUR_99A | 23681.7129 | 0 | 1.8333 | 0 | Out= Finley to Uranquinty (99A), avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | Outage | NSW
S_LB_1+2+3_110 | 23582.7792 | 0 | 1.8333 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=110 MW | Outage | SA
F_TASCAP_RREG_0220 | 23522.5398 | 0 | 200.5 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | Other | FCAS
F_TASCAP_LREG_0210 | 23367.2571 | 0 | 266.1667 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS
S>NIL_PL_GENMAX_YDMD | 22887.5176 | 0 | 1.0833 | 0 | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating. | NIL | SA
S:VS_650_HY_TEST | 22777.4571 | 5139.7441 | 18.5 | 3.3333 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
Q>X_CPWO1_CPWU_CPWO2 | 22446.1734 | 0 | 8.5 | 0 | Out= Calliope River to Woolooga (813+815) line, avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (814) line, Feedback | Outage | Qld
V_ARARATWF_ISL_0 | 22337.3374 | 0 | 7.3333 | 0 | Limit Ararat Wind Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Vic
N^^V_DDSM1 | 22188.5309 | 3237.3533 | 34.3333 | 6.25 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | NSW
Q_HASMME_RAMP_ZERO | 21553.9997 | 0 | 1.75 | 0 | Ramp Haughton, Sun Metals and Mt Emerald generators to zero and hold at zero. | Outage | Qld
SA_ISLE_STRENGTH_LB | 21055.9345 | 0 | 4.6667 | 0 | Maximum limit (0 MW) for Lake Bonney and Canunda Wind Farm for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
T_T_FASH_7_N-2 | 20965.4193 | 0 | 7.8333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation <= 110% of West Coast load | Outage | Tas
S_SECB_LG-1 | 20836.8819 | 54875.0923 | 1.5 | 4.0833 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
V_MURRAWRWF_30WT | 20643.3149 | 0 | 4.1667 | 0 | Limit Murra Warra Wind Farm upper limit to 0 MW if number of turbine ON exceed 30. Constraint swamp out if number of turbine ON not exceed 30. This is to manage voltage oscillation. DS only | Outage | Vic
S>NIL_NIL_SGBN | 20496.1987 | 24012.6753 | 1.5833 | 1.9167 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | SA
T>T_TU_LE_WA12_2 | 20293.597 | 0 | 4.3333 | 0 | Out = either Tungatinah to Waddamana 110kV line (direct or via Lake Echo tee), avoid O/L the remaining Tungatinah to Waddamana 110 kV line (flow to North) on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, feedback | Outage | Tas
Q_STR_033310_MEMF_26 | 19665.0443 | 0 | 1.5 | 0 | Limit Mt Emerald WF to 50% capacity (26 turbines) if Kareeya < 2 + Stanwell >= 3 + Callide >=3 + Gladstone >= 3 and (Stan+Cal+Glad) >=10, Swamp if Kar >= 2 + Stan >= 3 + Cal >= 3 + Glad >= 3 and (Stan+Cal+Glad) >=10. Zero otherwise. Swamp during night. | NIL | Qld
N_BKHSF_40INV | 19590.0798 | 0 | 1.4167 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 40. Constraint swamp out otherwise. DS only | NIL | NSW
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 19520.3924 | 22014.5713 | 93.3333 | 79.0833 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | NSW
F_Q++ARTW_L60 | 19225.7743 | 11724.4929 | 20.0833 | 74.5833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS
F_MAIN+TASCAP_LREG | 19022.1884 | 133421.2436 | 263.5833 | 2083.9167 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS
CA_MQS_4C1211CB_01 | 18861.8022 | 0 | 2.4167 | 0 | Constraint Automation, O/L R_TOWN TRANSF T_1 for CTG LSIT on trip of R_TOWN - PARA 275KV LINE. Generated by STNET[MANFL] Host MANEEMP1(MQ) | Outage | Constraint Automation
N^^V_CNCW_1 | 18619.5632 | 7799.6653 | 16.3333 | 11.5833 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
F_MAIN+LREG_0120 | 18310.5489 | 220320.4028 | 105.0833 | 1727.3333 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | NIL | FCAS
F_I+NIL_RREG | 18244.5378 | 248430.3825 | 607.9167 | 2238.75 | NEM Raise Regulation Requirement | NIL | FCAS
Q_STR_033310_MEWF_26 | 17966.2102 | 0 | 1.3333 | 0 | Limit Mt Emerald WF to 50% capacity(26 turbines)day or 75%(39 turbine)night if Kar < 2 +Stan >= 3 + Cal >=3 + Glads>= 3 and (Stan+Cal+Glad) >=10, 75% day(swamp night )if Kar >= 2+Stan >= 3 + Cal >= 3 + Glad >= 3 and (Stan+Cal+Glad) >=10. Zero otherwise. | Outage | Qld
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 17930.3082 | 32298.2571 | 28.8333 | 20.1667 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL | Qld
F_Q++BCDM_L60 | 17764.8235 | 29724.1997 | 136.6667 | 82.8333 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage | FCAS
F_MAIN++LREG_0210 | 17706.0574 | 0 | 181.1667 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL | FCAS
F_Q++BCDM_L5 | 17119.827 | 63546.5184 | 65.4167 | 75.0833 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage | FCAS
V_GANWRSF_FLT_25 | 17044.7659 | 0 | 10.25 | 0 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | Vic
V^SML_HORC_3 | 16868.6121 | 2253.3327 | 79.0833 | 16.9167 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
S>>BG6246_BGPR_HUWT | 16668.4775 | 22662.4294 | 1.75 | 3.8333 | Out= Bungama 132kV CB6246, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Port Pirie 132kV line (this offloads Snowtown-Bungama 132kV line), Feedback | Outage | SA
F_I+NIL_APD_TL_L5 | 16438.5076 | 11523.2165 | 6641.8333 | 6268.25 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS
N>>N-NIL_1G | 16285.6469 | 0 | 4.1667 | 0 | Out= Nil, avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22) line, Feedback | NIL | NSW
S_PWSE_LG3 | 16113.8454 | 0 | 1.3333 | 0 | Out=Penola West-South East 132kV line, Oscillatory stability limit max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
F_T+FASH1_2C_TG_R6 | 15958.9234 | 0 | 0.33333 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
T::T_NIL_4 | 15942.4099 | 7836.5439 | 29.4167 | 14.1667 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
S>>NIL_RBTU_WEWT | 15660.0357 | 0.58379 | 2.75 | 0.33333 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | SA
V:S_600_HY_TEST_DYN | 15553.9445 | 48945.8157 | 20 | 89.8333 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
S>LFTI_PPPW_LFTX5 | 15482.6735 | 0 | 2.3333 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L LeFevre 275/132kV TX5 on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | SA
N>N-96H+96R_TE_1 | 15382.6554 | 0 | 1.9167 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage | NSW
N_COLMBSF_60_INV | 15275.2362 | 0 | 1.1667 | 0 | Limit Coleambally Solar Farm upper limit to 0 MW if number of inverter available exceed 60. Dispatch only. swamped out if Inverters are within the limit. | Outage | NSW
T_FATI | 15137.98 | 42600 | 0.33333 | 0.25 | Out=Farrell-Tribute 220KV line. Energy <= 0MW | Outage | Tas
F_V_APD01_R5 | 14935.1152 | 144.9243 | 591.3333 | 0.66667 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage | FCAS
T_TA_ZERO | 14700 | 0 | 0.083333 | 0 | Discretionary 0 MW upper limit on total Tarraleah generation | Outage | Tas
F_MAIN++APD_TL_L5 | 14563.731 | 4533.1843 | 2428.1667 | 1551.8333 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS
Q_KMBG_7184 | 14500 | 0 | 0.083333 | 0 | Out= 7184 Kamerunga Barron Gorge PS 132kV line | Outage | Qld
S>>X_RBPA+BGTX_05 | 14397.6797 | 0 | 1.75 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
F_MAIN++RREG_0220 | 14314.5077 | 0 | 74.0833 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | Other | FCAS
S>NWBCB6025_TX2 | 14186.1452 | 0 | 4 | 0 | Out= North West Bend 132kV CB6025 , avoid O/L of North West Bend 132/66kV TX2 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage | SA
F_T++NIL_WF_TG_R6 | 14166.7623 | 20152.9149 | 60.1667 | 80.5833 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
V_BROKENHSF_FLT_0 | 13821.1981 | 0 | 1 | 0 | Limit Broken Hill Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
S>>RBTU_BWMP_TWPA | 13510.0024 | 0 | 5.6667 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | SA
N_WRWSF_055 | 13388.9248 | 0 | 12.1667 | 0 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | NSW
S^DVBR_SA_NTH | 13297.3609 | 0 | 1.8333 | 0 | Out = Davenport-Brinkworth 275kV line, Manage voltage collapse in northern SA for the trip of Davenport-Belalie 275kV line | Outage | SA
S-WIWF_0 | 13286.6854 | 0 | 1.4167 | 0 | Discretionary upper limit for Willogolechi WF generation of 0 MW | Outage | SA
V_MTGBRAND_33WT | 13266.9567 | 1089.4284 | 1 | 0.083333 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 33 | Outage | Vic
V>V_WETS_BTX_1 | 13131.9087 | 0 | 1 | 0 | Out = Wemen 220/66kV B1 or B2 txfmr, prevent pre-contingent overload the remaining Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback. | Outage | Vic
N^^V_SMTXF2_1 | 12984.217 | 835.9719 | 11.1667 | 1.3333 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
T_FASH_MAXGEN_1 | 12773.2299 | 10376.924 | 8.0833 | 12.3333 | Upper limit on Mackintosh + Bastyan + John Butters with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Tas
F_V_GESS_G_RREG | 12767.1862 | 0 | 13.1667 | 0 | Gannawarra Battery (Gen Component) RREG requirement <=0 MW | Outage | FCAS
F_MAIN++LREG_0170 | 12606.0358 | 0 | 98.5 | 0 | Mainland Lower Regulation Requirement greater than 170 MW, Basslink able transfer FCAS | Other | FCAS
Q_NIL_STRGTH_HAUSF | 12541.1875 | 0 | 1.3333 | 0 | Out = Nil, limit Haughton SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to TOA 393 | NIL | Qld
T>T_NIL_BL_IMP_7CC | 12211.1617 | 7914.9913 | 22.3333 | 50.25 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
Q:N_1078 | 11802.8422 | 4381.8721 | 24.9167 | 18.5833 | QNI oscillatory stability limit of 1078 MW | Outage | Qld
V_GANNSF_12INV | 11730.7768 | 0 | 3 | 0 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out if number of inverter available not exceed 12. This is to manage voltage oscillation. DS only | Outage | Vic
S_LB2WF_CONF | 11523.677 | 2237.5445 | 4.3333 | 0.66667 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
VT_050 | 11108.2311 | 0 | 3.5 | 0 | Vic to Tas on Basslink upper limit of 50 MW | Outage | Vic
Q>>CPSP_WOPW_WOGP_2 | 11057.5271 | 0 | 0.5 | 0 | Out= Calliope River to South Pine (813+815+807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Qld
S>LFTI_PPPW_LFTX4 | 10945.456 | 0 | 1.4167 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L LeFevre 275/132kV TX4 on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | SA
N^^Q_NIL_A | 10777.3842 | 1425.3606 | 24.75 | 6.9167 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | NSW
F_TASCAP_LREG_0190 | 10724.0711 | 0 | 159.5 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | Other | FCAS
T^V_NIL_9 | 10599.887 | 31730.7858 | 21.25 | 58.5833 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
F_TASCAP_RREG_0200 | 10558.7391 | 0 | 139.4167 | 0 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | Other | FCAS
S>>BRTW_BWPA_WTTP | 10382.4902 | 136.3539 | 0.83333 | 0.25 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 10224.5985 | 43440.3774 | 36.5833 | 145.1667 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Vic
S>>V_NIL_WTTP_WEMW4 | 9998.7102 | 12484.4893 | 0.75 | 1.0833 | Out= Nil, avoid O/L Waterloo East - Morgan Whyalla 4 132kV on trip of Waterloo - Templers 132 kV line, Feedback | NIL | SA
S>>PATW_NIL_WEMWP4 | 9949.0547 | 6119.4155 | 1.5833 | 1.1667 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
V_ARARAT_ZERO | 9930.8959 | 8703.0586 | 3.1667 | 3.6667 | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
S_PWSE_LG2 | 9746.3031 | 0 | 0.83333 | 0 | Out=Penola West-South East 132kV line, Oscillatory stability limit Ladbroke Grove 2 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
F_T+FASH_N-2_TG_R6_1 | 9597.3336 | 4693.4839 | 5.5 | 11.3333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
F_T+NIL_ML_L6 | 9591.2301 | 9994.3283 | 1199 | 2322.75 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
V_BANNERTSF_FLT_44 | 9367.4329 | 0 | 0.75 | 0 | Limit Bannerton Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | Outage | Vic
T::T_NIL_3 | 9100.5075 | 262.8822 | 14.1667 | 1.9167 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Tas
N>>N-SNVP_03 | 8683.2002 | 0 | 1.8333 | 0 | Out = SydneyNorth-ValesPoint(22), avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25) line, Feedback | Outage | NSW
Q_HAMISF1_ZERO | 8614.1114 | 0 | 2.0833 | 0 | Hamilton solar farm upper limit of 0 MW | Outage | Qld
VSML_ROC_80 | 8611.0013 | 31946.5082 | 28.5833 | 43.25 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
V::N_SMSC_xxx | 8592.6919 | 0 | 20.25 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V^SML_BUDP_3 | 8444.5031 | 648.089 | 43.25 | 5.3333 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
F_T++NIL_WF_TG_R5 | 8258.6123 | 13917.8086 | 94.1667 | 74.5833 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
F_MAIN+LREG_0170 | 8180.5507 | 0 | 32 | 0 | Mainland Lower Regulation Requirement greater than 170 MW, Basslink unable to transfer FCAS | Other | FCAS
T^V_NIL_11 | 8179.3981 | 38832.3731 | 5.1667 | 70 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
V_KARSF_21INV | 8121.0333 | 0 | 3.8333 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 21. Constraint swamp out if number of inverter available not exceed 21. This is to manage voltage oscillation. DS only | Outage | Vic
S>>CNLK_MKRB_WEMWP4 | 8080.041 | 0 | 4.75 | 0 | Out= Canowie-Mt Lock 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV on trip of Mokota-Robertstown 275kV line( this offloads Belalie-Mokota 275kV line and trips Hallet Hill WF), Feedback | Outage | SA
T_T_FASH_1_N-2 | 8048.555 | 8001.4103 | 3.6667 | 6.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
N_WR_55_30WT-INV | 7969.2682 | 0 | 7.8333 | 0 | Limit White Rock wind/solar farm upper limit to 55 MW with max 30 wind turbine and inverter available, upper limit set to 0 MW if number of wind turbine + inverter available exceed 30. This is to manage low SCR. | Outage | NSW
VSML_ZERO | 7964.3382 | 234097.2069 | 26 | 546.5833 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Vic
SA_HYSE1 | 7920.981 | 0 | 2.9167 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage | SA
S>RB_275KV_S_BUS_9 | 7805.6629 | 0 | 11.8333 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage | SA
F_MAIN++LREG_0210 | 7795.7717 | 0 | 97.0833 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Other | FCAS
S>V_460_DYN | 7745.3365 | 0 | 11.6667 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | SA
F_MAIN+APD_TL_L5 | 7631.4908 | 7609.876 | 1162.5833 | 1942.4167 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS
S>>CNRB_BWPA_HUWT | 7608.9769 | 0 | 1.3333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
N>LSDU9U6_LSDU9U7 | 7567.7643 | 492.5812 | 29 | 6.6667 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | NSW
V_BANSF_20INV | 7561.9134 | 0 | 0.58333 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 20. Constraint swamp out otherwise. DS only | NIL | Vic
F_T++NIL_MG_R6 | 7452.9412 | 24957.7937 | 21.25 | 43.25 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
V:S_600_HY_TEST | 7384.0735 | 10327.1785 | 20.6667 | 36.5 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
S>>X_RBTU+CB_2 | 7371.8643 | 0 | 12.4167 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) | Outage | SA
TVBL_ROC | 7280.3198 | 4007.6324 | 9.8333 | 7.0833 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Tas
CA_MQS_4C6B1A92_01 | 7052.2021 | 0 | 2 | 0 | Constraint Automation, O/L N_W_B TRANSF T_1 for CTG LS5K on trip of R_TOWN-N_W_B132KV 2LN VIA1 2&3MWPS. Generated by STNET[MANFL] Host MANEEMP2(MQ) | Outage | Constraint Automation
T>T_BWLF_110_4 | 7004.5886 | 0 | 7.75 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana 110 kV line, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Tas
V_KARADSF_FLT_45 | 6942.7508 | 0 | 4.5833 | 0 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
T:T_LIPM_1 | 6901.4805 | 11968.2835 | 26.25 | 17.4167 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Tas
F_Q++ARTW_L5 | 6808.3032 | 10802.8841 | 16.4167 | 65.9167 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage | FCAS
S>X_DV-BR-PA_12 | 6740.4688 | 0 | 0.83333 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Mokota-Robertstown 275kV line on trip of Canowi-Robertstown 275kV line(this trips Hallet WF and GT) | Outage | SA
F_S+TL_L5_OD | 6645.1099 | 21205.9612 | 4.6667 | 0.16667 | Lower 5 min Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
N_WOODLWN1_ZERO | 6616.2141 | 0 | 0.5 | 0 | Woodlawn unit upper limit of 0 MW | Outage | NSW
T_FASH_MAXGEN_2 | 6525.2318 | 0 | 5.6667 | 0 | Upper limit on West Coast generation to maintain transient stability, West Coast 220/110 kV parallel closed, Farrell 220 kV bus NOT split, constraint swamped if only one machine on line | Outage | Tas
V_GANWR_BAT_G_ISL_0 | 6491.3653 | 0 | 2.25 | 0 | Gannawarra Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
V_BANSF_BBD_80 | 6436.0837 | 0 | 0.5 | 0 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Vic
S>>TBTU_CGTB_MOTB | 6387.1386 | 0 | 5.9167 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of Cherry Gardens-Tailem Bend 275kV line, Feedback | Outage | SA
V_WEMENSF_FLT_44 | 6278.0047 | 0 | 3.0833 | 0 | Limit Wemen Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | Outage | Vic
Q>>WOPW_WOSP_WOGP_1 | 6272.711 | 0 | 0.33333 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
VTBL_ROC | 6267.8093 | 25578.4215 | 8.9167 | 6.1667 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Vic
I_CTRL_ISSUE_TE | 6242.2966 | 10433.1791 | 19.8333 | 113.25 | DC Link Control Issue Constraint for Terranora | Outage | Other
T_LIPM_PMWA_2_N-3 | 6039.4443 | 0 | 3.0833 | 0 | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to >= southern load - 15 MW | Outage | Tas
N>Q_LSLS_9U8 | 5947.422 | 0 | 8.5833 | 0 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 directlink cable O/S. | Outage | NSW
NQTE_-060 | 5946.7939 | 0 | 76.1667 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -60 MW | Outage | NSW
N^^N_NIL_1 | 5933.0407 | 42750.7841 | 0.16667 | 1.5 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
N^^V_DDWG | 5917.9992 | 2091.4779 | 5.9167 | 3.8333 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
F_MAIN+LREG_0190 | 5890.0075 | 0 | 22.3333 | 0 | Mainland Lower Regulation Requirement greater than 190 MW, Basslink unable to transfer FCAS | Other | FCAS
F_TASCAP_LREG_0170 | 5832.6265 | 0 | 83.5 | 0 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | Other | FCAS
V_KARSF_8INV | 5804.1163 | 0 | 3.3333 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 8. Constraint swamp out if number of inverter available not exceed 8. This is to manage voltage oscillation. DS only | Outage | Vic
V_KARSF_19INV | 5748.7892 | 0 | 2.3333 | 0 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | NIL | Vic
F_S++TIB3_R6_1 | 5736.0665 | 0 | 1 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA, Segment 1 | Outage | FCAS
T_V_NIL_FCSPS | 5702.6571 | 16609.4534 | 3.8333 | 3.0833 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
F_T++NIL_WF_TG_R60 | 5699.5178 | 5947.2597 | 63.8333 | 118.4167 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
F_S++TIB4_R6_1 | 5682.2461 | 0 | 0.66667 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA, Segment 1 | Outage | FCAS
N_GULLRWF1_ZERO | 5587.9763 | 0 | 5.0833 | 0 | Gullen Range WF upper limit of 0 MW | Outage | NSW
F_T++NIL_MG_RECL_R60 | 5564.0619 | 6985.5697 | 104.9167 | 170.9167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
V>V_NIL_8 | 5548.4967 | 0 | 4.3333 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Vic
F_I+NIL_APD_TL_L60 | 5347.0009 | 3163.9779 | 5905.1667 | 5415.9167 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS
F_MAIN++RREG_0220 | 5308.3421 | 0 | 30.1667 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL | FCAS
Q_STR_MEWF_26 | 5256.9421 | 0 | 0.41667 | 0 | Limit Mt Emerald WF to 50% capacity (26 turbines) | Outage | Qld
T_LIPM1_SLOAD_1_N-2 | 5180.1089 | 0 | 10.75 | 0 | Out=Liapootah-Waddamana-Palmerston #1 220kV line and associated 220kV CBs at Waddamana I/S, loss of #2 parallel 220 kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Tas
S_TB2_TX | 5157.9905 | 0 | 0.41667 | 0 | Torrens B 2 Transformer O/S; unit=0 | Outage | SA
N>>N-964_DC | 5153.9772 | 0 | 3.9167 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage | NSW
QNTE_SUPPORT | 4987.6967 | 0 | 81.5 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Qld
S>>X_RBTU_CB_3 | 4870.3198 | 0 | 0.91667 | 0 | Out= Robertstown-Tungkillo 275kV line& RB 275kV CBs 6571 & 6572 O/S, avoid O/L Waterloo East-MWP4-RB 132kV line on trip of Mokota-Robertstown 275kV line(trips Willalo-Mokota 275kV line and Hallet Hill WF. The contingency SPLITS Robertstown bus) | Outage | SA
S>>X_DVBR_BRTW_05 | 4819.3304 | 0 | 15.5833 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX), avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
N^N_CHLS_1 | 4807.6018 | 92.4042 | 30.25 | 2.75 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | NIL | NSW
S>RB_275KV_N_BUS_1 | 4628.2799 | 0 | 5.75 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | SA
F_T++NIL_MG_R5 | 4554.2575 | 2952.8572 | 47.5833 | 21.5833 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
T>T_GTSH_IMP_4K | 4553.8742 | 1188.6571 | 4.25 | 3.25 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
F_MAIN+RREG_0200 | 4552.6742 | 0 | 15.6667 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | Other | FCAS
V:T_NIL_BL_1 | 4542.1911 | 1597.47 | 6.0833 | 2.8333 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL | Vic
T_T_BA_JB_RC2_250 | 4534.5623 | 12973.3448 | 3.75 | 20 | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
F_MAIN+RREG_0180 | 4533.1876 | 0 | 14.3333 | 0 | Mainland Raise Regulation Requirement greater than 180 MW, Basslink unable to transfer FCAS | Other | FCAS
Q_CS_1750 | 4528.4816 | 3175.0616 | 1.9167 | 5.3333 | Qld Central to Qld South upper transfer limit of 1750MW (discretionary) | Outage | Qld
N>>N_65+66_N-2_2 | 4524.2787 | 0 | 7.5833 | 0 | Out= Nil, avoid O/L Dederang to Wodonga on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL | NSW
Q_CS_1650 | 4404.6629 | 0 | 0.91667 | 0 | Qld Central to Qld South upper transfer limit of 1650MW (discretionary) | Outage | Qld
V_MURRAWR_ZERO | 4384.0064 | 0 | 0.33333 | 0 | Murra Warra wind farm upper limit of 0 MW | Outage | Vic
T>T_NIL_BL_3C | 4364.4829 | 1853.2154 | 2.1667 | 5.4167 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
V::N_NIL_xxx | 4302.9745 | 115464.4404 | 16.8333 | 271.25 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL | Vic
S>>MKRB_CNRB_WEMWP4 | 4294.1393 | 15084.8235 | 13.1667 | 11.75 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage | SA
Q_STR_233310_HASF_60 | 4226.0551 | 0 | 0.33333 | 0 | Limit Haughton SF to 75% of max capacity (#60 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
Q>>PWSP_WOSP_PWCE | 4216.6367 | 131.0262 | 0.58333 | 0.25 | Out= Palmwoods to South Pine (808) line, avoid O/L Palmwood to Caboolture (746/4) 110kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
N^^V_GRYS_1 | 4177.7887 | 0 | 5.1667 | 0 | Out = Gullen Range to Yass (3J), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
V_OAKLANDSHILL_42 | 4164.4369 | 0 | 0.33333 | 0 | Oaklands Hill Windfarm upper limit of 42 MW | Outage | Vic
QNTE_OSCILLATE | 4125.7455 | 1334.9034 | 20.5 | 4.9167 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Qld
V::S_PATU_MAXG_2 | 4104.4535 | 0 | 1.1667 | 0 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
S>>X_DV-BR-PA_07 | 4063.2197 | 0 | 0.75 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West -Munno Para 275kV line, Feedback | Outage | SA
T>T_NIL_BL_IMP_7C | 4063.1663 | 2071.2001 | 8.9167 | 11.5 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Tas
S_LBMY_2B-LB3 | 4011.1334 | 0 | 1.5 | 0 | Out= Mayurra-Lake Bonney WF 2B 33kV line (OR Mayura CB4565 and CB4674 OPEN), Lake Bonney 3 constrained to 0 MW | Outage | SA
F_MAIN++LREG_0190 | 4005.0318 | 0 | 43.0833 | 0 | Mainland Lower Regulation Requirement greater than 190 MW, Basslink able transfer FCAS | Other | FCAS
Q^^CS_-240 | 3945.1665 | 0 | 5.75 | 0 | Nominated Offset -240MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage | Qld
F_MAIN++APD_TL_L60 | 3926.5747 | 1156.3701 | 2078 | 1232.9167 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS
V::N_HORC_xxx | 3914.2645 | 3878.3174 | 7.8333 | 5.4167 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
Q>NIL_TV66 | 3861.6129 | 0 | 1.1667 | 0 | Out=Nil, limit Sun metals SF and Mt Stuart GTs to avoid over load on 66kV feeders on trip of one of the 66kV feeders in the Townsville area | NIL | Qld
T_V_NIL_BL1 | 3858.7799 | 3046.1384 | 7.3333 | 6.6667 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL | Tas
T>>T_NIL_BL_EXP_7C | 3848.5279 | 16.5312 | 11.0833 | 0.16667 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
F_MAIN+NIL_RREG | 3846.49 | 113753.422 | 41.5 | 784.6667 | Mainland Raise Regulation Requirement, Basslink unable transfer FCAS | NIL | FCAS
Q>>CPSP_WOSP_PWCE | 3724.7501 | 0 | 0.33333 | 0 | Out= 808(Palmwoods to South Pine)+ 813 +815 (Calliope River to Woolooga) 275kV lines with 132kV/110kV network between Woolooga to Palmwoods network closed, avoid O/L Palmwood to Caboolture(746/4) on trip of Woolooga to South Pine (807)line, Feedback | Outage | Qld
Q>>BCCP_CLWU_RGLC_2 | 3693.5459 | 0 | 2.8333 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
F_T+NIL_ML_L60 | 3680.0316 | 5312.8175 | 1198.75 | 2216.6667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
SVML_FLT_150 | 3678.9164 | 0 | 3.4167 | 0 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | SA
F_T+FASH_N-2_TG_R6_2 | 3649.5333 | 12.4651 | 4.75 | 0.33333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS
S>>X_DVBR+BRTW_15 | 3635.1604 | 0 | 0.5 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | Outage | SA
F_VS++65_66_RAD_R60 | 3585.916 | 0 | 6 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
V_WEMENSF_21INV | 3505.1512 | 0 | 1 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 21. Constraint swamp out if number of inverter available not exceed 21. This is to manage voltage oscillation. DS only | Outage | Vic
V^SML_BAWB_3 | 3467.1036 | 0 | 33.5833 | 0 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
N_NIL_TE_B | 3382.5411 | 5550.4471 | 15.0833 | 12.5 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
N_BODWF1_ZERO | 3271.4009 | 111575.1989 | 0.25 | 8.5833 | Bodangora wind farm upper limit of 0 MW | Outage | NSW
T_LIWY | 3246.078 | 0 | 0.25 | 0 | Out=Liapootah-Wayatinah 220KV line | Outage | Tas
N_MBTE1_A | 3243.9341 | 6.1906 | 3.0833 | 1.1667 | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
Q_STR_SMHAU_MEWF_26 | 3195.2473 | 0 | 0.25 | 0 | Limit Mt Emerald WF to 75% capacity(39 turbines)during day or (swamp at night) if Kar >=2 (2 TX during day) +Stan >= 3 + Cal >=3 + Glads>= 3 and (Stan+Cal+Glad) >=10, 50%during day if Kar< 2 ( or 1 TX ). Zero otherwise. | Outage | Qld
V>>V-LTWG_RADIAL_1 | 3192.4547 | 0 | 0.25 | 0 | Outage = Lower Tumut to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings; Feedback | Outage | Vic
N^^V_LTWG_1 | 3156.8276 | 0 | 5.5 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
V::N_KGRC_xxx | 3154.1061 | 0 | 8.0833 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_QNV++MG_R60 | 3149.0278 | 0 | 3.6667 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS
V::S_NIL_MAXG_xxx | 3123.6259 | 5960.3952 | 11.3333 | 32.9167 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
F_T+CSGO_TG_R6_1 | 3061.3649 | 0 | 4.25 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
S>NWBCB6225_TX1 | 3030.6414 | 0 | 1.5 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 66/132kV TX1 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage | SA
T_ROCOF_1 | 3029.7256 | 4520.5502 | 5.0833 | 24.25 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL | Tas
F_ESTN+RREG_0220 | 2922.2523 | 0 | 4.5833 | 0 | Eastern Raise Regulation Requirement greater than 220 MW | Outage | FCAS
S>>X_RBPA+BGTX_16 | 2871.6642 | 0 | 0.5 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on NIL trip, Feedback | Outage | SA
T^V_NIL_8 | 2819.4858 | 19805.1663 | 6.5 | 46.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
V>>V_KGWT_3 | 2755.3534 | 0 | 3.5 | 0 | Out= Kerang to Wemen 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Balranald to Darlington Point (X5) 220kV line, Feedback | Outage | Vic
F_MAIN+APD_TL_L60 | 2679.4472 | 2838.9591 | 1141.4167 | 1916.4167 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS
V^SML_ARWB_3 | 2666.0865 | 0 | 12.0833 | 0 | Out = Ararat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
V>>V_BUDP_6 | 2631.5839 | 0 | 3.6667 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Vic
QNTE_ROC | 2611.0712 | 2116.0317 | 13.5 | 43.5 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
V>>V_KTS_TX_A2_2A_R | 2598.6936 | 369.2916 | 3.75 | 1.75 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
NQTE_ROC | 2598.3537 | 1218.5704 | 12.0833 | 48.75 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | NSW
N>N-NIL_LSDU | 2590.1799 | 265.3292 | 26.9167 | 6 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
S>>X_MKRB+WTTP_06 | 2562.6716 | 0 | 1.9167 | 0 | Out= Mokota-Robertstown 275kV line (note:associated line CBs assumed I/S) + Waterloo-Templers 132kV line, avoid O/L Waterloo East-MWp4-Robertstown 132kV line on trip Nil trip, Feedback | Outage | SA
F_MAIN++ML_L6_0400 | 2554.0684 | 222.0729 | 1385.4167 | 610.75 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS
F_MAIN++RREG_0180 | 2548.0003 | 0 | 16.5 | 0 | Mainland Raise Regulation Requirement greater than 180 MW, Basslink able transfer FCAS | Other | FCAS
N_WRWSF_ZERO | 2525.7477 | 0 | 1 | 0 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | NSW
S>>CNLK_BWMP_MKRB | 2508.7706 | 0 | 0.25 | 0 | Out= Canowie-Mt Lock 275kV line, avoid O/L Mokota-Robertstown 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S::V_PWSE_TBSE_2 | 2498.6447 | 0 | 2.25 | 0 | Out = Penola West - South East #1 132KV line (NOTE: with both Black Range series capacitors O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | SA
F_ESTN+MG_R6 | 2473.2229 | 0 | 4.8333 | 0 | Raise 6 sec Service Requirement for Eastern Generation Event | Outage | FCAS
S:V_PA_SVC_420 | 2456.6519 | 1209.5097 | 0.5 | 1.3333 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | SA
NQTE_-070 | 2408.2195 | 93.0858 | 10.1667 | 1.25 | NSW to Qld on Terranora Interconnector upper transfer limit of -70 MW | Outage | NSW
F_Q++8C_L6 | 2382.9562 | 3433.3968 | 3.5833 | 27.3333 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage | FCAS
N>N-LSTN_TE_C1 | 2363.2335 | 15.8889 | 13.1667 | 0.16667 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
S>V_460 | 2353.6802 | 0 | 10.1667 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage | SA
F_T++FASH_N-2_TG_R6 | 2350.1411 | 182.6174 | 3.3333 | 1.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
V>>BABE_DDGN_N-2 | 2304.635 | 68.7371 | 0.58333 | 0.16667 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage | Vic
N^N-LS_SVC | 2230.9698 | 60323.1631 | 21.8333 | 481.1667 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage | NSW
S>NIL_WERB_WEWT | 2199.9992 | 75482.364 | 0.58333 | 7 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
SA_HYSE2 | 2185.5504 | 3692.4021 | 1.9167 | 0.41667 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage | SA
T^^V_GTSH_1 | 2152.5937 | 5889.7639 | 2.75 | 9.5833 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
Q>>CLWU_BCRG_BCCP | 2149.7973 | 0 | 3.4167 | 0 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811), Feedback | Outage | Qld
Q_WHITSF1_ZERO | 2070.0582 | 0 | 2.0833 | 0 | Whitsunday solar farm upper limit of 0 MW | Outage | Qld
V_WEMENSF_FLT_45 | 2066.6556 | 0 | 1.25 | 0 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
V_WEMENSF_19INV | 2060.4898 | 0 | 0.91667 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | NIL | Vic
V>SMLMHNW1 | 2023.5184 | 0 | 5.0833 | 0 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | SA
S>>MKRB_NIL_WEMWP4 | 1991.0537 | 296.0492 | 2.5 | 0.91667 | Out= Mokota-Robertstown 275kV line,, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
VT_ZERO | 1973.223 | 0 | 4.1667 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Vic
F_S+PPT_R5 | 1971.6065 | 14654.18 | 2.75 | 0.25 | Raise 5 min Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage | FCAS
N>>N-NIL__H_15M | 1954.1905 | 0 | 0.25 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | NSW
N>>N-NIL__3_OPENED | 1928.1756 | 41910.2427 | 1.4167 | 18.3333 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
F_MAIN+ML_L6_0400 | 1902.5578 | 718.75 | 1019.1667 | 1663.9167 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
V_MURRAWRWF_FLT_90 | 1891.5574 | 0 | 2.1667 | 0 | Limit Murra Warra Wind Farm upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | Vic
QNI_SOUTH_1150_DYN | 1873.1913 | 0 | 2.5833 | 0 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL | Qld
S>>PATW_BWPA_WEMWP4 | 1861.3852 | 0 | 0.33333 | 0 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_I+ML_L6_0400 | 1819.5434 | 562.4403 | 3775.75 | 2086.5833 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS
S>>V_NIL_RBTX_MW4RB | 1801.2879 | 0 | 0.16667 | 0 | Out= Nil, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of one Robertstown 275/132kV transformer, Feedback | NIL | SA
S>>PARB_TWPA_TPRS | 1795.0075 | 33.9701 | 0.083333 | 0.083333 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
F_MAIN++RREG_0200 | 1783.733 | 0 | 12.25 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | Other | FCAS
F_ESTN+LREG_0210 | 1696.6658 | 0 | 4.8333 | 0 | Eastern Lower Regulation Requirement greater than 210 MW | Outage | FCAS
F_Q_W/HOE_R5 | 1689.035 | 2.78 | 8.9167 | 0.083333 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage | FCAS
V_GANNSF_11INV | 1655.5837 | 0 | 0.83333 | 0 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Constraint swamp out otherwise. DS only | NIL | Vic
S>KNPW_NIL_SETX12 | 1584.6858 | 2167.4258 | 1.1667 | 0.16667 | Out=Penola West-Kincraig 132kV line, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
V::N_KTSY_xxx | 1584.4693 | 0 | 2.75 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
Q_STR_233310_SMSF_76 | 1552.6643 | 0 | 1.5833 | 0 | Limit Sun metal SF to 100% of max capacity (#76 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
SA_ISLE_STRENGTH_BU | 1528.8189 | 0 | 0.25 | 0 | Maximum limit (130 MW) for Bungala Solar Farm for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
VSML_220 | 1517.9106 | 27129.0853 | 3.5833 | 28.0833 | Vic to SA on ML upper transfer limit of 220 MW | NIL | Vic
V_MB_BUS2 | 1508.6958 | 0 | 1.3333 | 0 | Dartmouth PS upper limit set to zero due to outage of Mt Beauty No 2 220 kV Bus | Outage | Vic
F_VST++65_66_RAD_R5 | 1507.2234 | 0 | 8.5833 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; VIC, SA and TAS Raise 5 min Requirement | Outage | FCAS
T>T_PMWA_110_7 | 1489.2574 | 1005.19 | 1.5 | 0.083333 | Out= Palmerston to Waddamana 110 kV line, avoid overloading the New Norfolk to Chapel St 110 kV line (flow to South) on trip of New Norfolk to Creek Road 110 kV line, feedback | Outage | Tas
S>>BRTW_RBTU_WTTP | 1487.2006 | 0 | 0.083333 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
S>>X_RBPA+BGTX_14 | 1449.8045 | 0 | 0.25 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | SA
N>>N-NIL_DPTX_2 | 1427.6925 | 0 | 0.5 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | NSW
S>>NIL_BWMP_TWPA | 1426.5189 | 0 | 0.83333 | 0 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | SA
T>T_TUMBNN1_110_3 | 1420.5677 | 0 | 2.5 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line, avoid O/L Tungatinah to New Norfolk 110kV line on trip of Tungatinah to Meadowbank to New Norfolk No.2 110kV line, Feedback | Outage | Tas
Q_STR_233310_CSF_69 | 1409.5914 | 0 | 1.4167 | 0 | Limit Clare SF to 100% of max capacity (#69 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
V::N_DDSM_xxx | 1389.7642 | 682.1571 | 6.75 | 1.3333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V_WEMENSF_ISL_0 | 1378.313 | 0 | 0.5 | 0 | Wemen Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
NSA_Q_GSTONE34_xxx | 1361.0764 | 0 | 12.75 | 0 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Qld
V_KARADSF_ISL_0 | 1357.7271 | 0 | 0.66667 | 0 | Karadoc Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
V::N_BYPASS_HW_SY_xxx | 1354.6816 | 0 | 3.0833 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
N>>N-NIL__B_15M | 1294.8529 | 0 | 0.5 | 0 | Out= Nil, avoid O/L Upper Tumut to Canberra (01) using 15 mins rating on trip of Lower Tumut to Canberra (07) line, Feedback | NIL | NSW
Q>>BCCP_CLWU_LCCP_2 | 1292.7214 | 224.238 | 2.1667 | 1.5 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
S:V_580 | 1284.2021 | 0 | 2.75 | 0 | Out = One Heywood 500/275 kV txfmr (two remain in service), maintain maximum SA to VIC transfer limit of 580 MW on Heywood and Murraylink combined to avoid oscillatory instability | Outage | SA
F_T+FASH_N-2_TG_R60 | 1281.5555 | 266.5566 | 5.6667 | 6 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
V_GANWR_BAT_G_FLT_0 | 1274.8293 | 0 | 3.0833 | 0 | Limit Gannawarra Battery (Generation Component) upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
QN_950 | 1271.4109 | 0 | 1 | 0 | Qld to NSW on QNI upper transfer limit of 950 MW | Outage | Qld
Q^^TR_CLHA_-250 | 1269.4848 | 0 | 2.25 | 0 | Nominated offset -250 MW, Tarong voltage stability limit, Calvale-Halys contingency equation | Outage | Qld
F_T++NIL_MG_R60 | 1252.8539 | 2996.3348 | 20 | 61.1667 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
F_T++NIL_BLSPS_R6_2 | 1226.3026 | 0 | 4.6667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL | FCAS
S>>NIL_CNRB_WEMWP4 | 1224.0334 | 18618.3038 | 0.83333 | 0.66667 | Out= Nil, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line (this offloads Mt Lock-Canowie 275kV line and trips Hallet WF and GTs), Feedback | NIL | SA
S-LB2_0 | 1203.2899 | 238.3763 | 1.1667 | 0.16667 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | SA
F_Q++8C_L60 | 1201.6739 | 507.5702 | 3.5833 | 16.4167 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage | FCAS
F_T++FARE_N-2_TG_R6 | 1193.9755 | 19.6721 | 2.8333 | 0.33333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
N>N-ARKS_TE_A1 | 1193.3621 | 0 | 11.6667 | 0 | Out= Armidale to Kempsey (965), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
S>X_MKRB+WTTP_01 | 1157.4445 | 0 | 0.33333 | 0 | Out= Mokota-Robertstown 275kV line (note:associated line CBs assumed I/S) + Waterloo-Templers 132kV line, avoid O/L Canowi-Robertstown 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
N>>N-X_AVMA_KCTX_11 | 1110.4462 | 0 | 1.0833 | 0 | Out= Avon to Macarthur (17) 330kV line and Kemps Creek No.2 or No.3 500/330kV transformer , avoid O/L Vales Point to Munmorah (23) on trip of remaining Kemps Creek transformer, Feedback | Outage | NSW
I_CTRL_ISSUE_ML | 1087.0519 | 963.8263 | 8.6667 | 0.58333 | DC Link Control Issue Constraint for Murraylink | Outage | Other
N_FINLYSF1_66 | 1068.1806 | 0 | 0.083333 | 0 | Finley solar farm upper limit of 66 MW | Outage | NSW
Q_CS_0900 | 1064.6258 | 0 | 0.083333 | 0 | Qld Central to Qld South upper transfer limit of 900MW (discretionary) | Outage | Qld
Q_CS_1000 | 1063.814 | 0 | 0.083333 | 0 | Qld Central to Qld South upper transfer limit of 1000MW (discretionary) | Outage | Qld
S_HDWF1_0 | 1063.2513 | 88216.5518 | 0.083333 | 6.4167 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | SA
Q_STR_SMHAU_HASF_40 | 1058.2084 | 0 | 0.083333 | 0 | Limit Haughton SF to 50% capacity (40 inverters) If Stan >= 3 + Cal >=3 + Glad >= 3 and (Stan+Cal+Glad) >=10, Zero otherwise | Outage | Qld
T>T_FASH_1_2_C1 | 1057.81 | 33803.4084 | 1.5833 | 15.8333 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, West Coast 220/110 kV parallel closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
Q_CS_0800 | 1056.4443 | 0 | 0.083333 | 0 | Qld Central to Qld South upper transfer limit of 800MW (discretionary) | Outage | Qld
F_T++NIL_ML_L6 | 1047.2038 | 1032.0469 | 241.75 | 995.1667 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
F_MAIN++NIL_RREG | 1035.2429 | 7655.0188 | 10.75 | 57.25 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL | FCAS
F_T+FARE_N-2_TG_R6_2 | 1021.2978 | 1924.5062 | 1.9167 | 2.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage | FCAS
Q::N_DM_CB_AR_2L-G | 1011.0932 | 0 | 1.6667 | 0 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
S_PWLG_LG2 | 1007.6422 | 0 | 0.083333 | 0 | Outage of Penola West to Ladbroke Grove 132kV circuit | Outage | SA
T::T_GTSH_2 | 989.2624 | 0 | 2.1667 | 0 | Out = George Town to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage | Tas
V>V_NIL_17 | 985.596 | 0 | 0.25 | 0 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback. Constraint only active when either Wemen or Bannerton solar farm runback scheme disabled. | NIL | Vic
S>>NIL_MKRB_WEMWP4 | 955.6785 | 0 | 0.33333 | 0 | Out= Nil, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line(This offloads Belalie-Mokota 275kV line and trips Hallet Hill WF), Feedback | NIL | SA
F_T+NIL_ML_L5 | 915.3407 | 4646.2086 | 1150.5 | 1924.0833 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
T>>T_GTSH_EXP_3H | 870.7175 | 0 | 1.0833 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage | Tas
F_S+LREG_0035 | 865.15 | 386344.5599 | 0.083333 | 17.5833 | SA Lower Regulation FCAS Requirement greater than 35 MW | Outage | FCAS
V>SMLARHO1 | 859.9974 | 272269.9705 | 5.4167 | 49.5833 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
F_T+CSGO_TG_R60 | 837.3767 | 0 | 6 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
N>N-NIL_TE_E1 | 835.586 | 0 | 6.4167 | 0 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST | NIL | NSW
F_Q++NIL_R5 | 833.2284 | 71.5019 | 7.1667 | 2.25 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL | FCAS
F_VS+65_66_RAD_R60 | 811.9819 | 0 | 0.91667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
V^SML_NIL_3 | 758.8834 | 1.2793 | 0.58333 | 0.083333 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Vic
N_MBTE110_B | 742.1711 | 0 | 2.4167 | 0 | Qld to NSW on Directlink upper transfer limit of -110 MW | Outage | NSW
S>>DVBL_WTTP_WEMWP4 | 720.0669 | 0 | 0.083333 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | SA
S_LB3_0 | 706.05 | 2820.5682 | 0.25 | 0.83333 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
F_ESTN+MG_R60 | 700.616 | 0 | 4.8333 | 0 | Raise 60 sec Service Requirement for Eastern Generation Event | Outage | FCAS
V>>N-MSUT_4 | 675.5725 | 0 | 1.6667 | 0 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Vic
V::N_X_DDSM_SMSC_xxx | 669.8293 | 0 | 2.5833 | 0 | Out = one Dederang to South Morang 330kV line AND series capbank on the parallel line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
Q_CS_1550 | 648.8612 | 0 | 0.33333 | 0 | Qld Central to Qld South upper transfer limit of 1550MW (discretionary) | Outage | Qld
F_S++OSB_R5 | 645.3442 | 267.462 | 1.25 | 0.083333 | Raise 5 min Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA | Outage | FCAS
Q>N-MUTE_758 | 642.9178 | 2515.3888 | 0.83333 | 47.8333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
T>T_SH_TX | 627.5654 | 0 | 0.25 | 0 | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Tas
V>>SML_NSWRB_11 | 624.335 | 0 | 1.1667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Wemen to Red Cliffs 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL | Vic
S>>X_MKRB+WTTP_14 | 612.2678 | 0 | 2.5833 | 0 | Mokota - Robertstown 275kV line(i.e. Line ONLY O/S, line CBs I/S) + Waterloo-Templers 132kV line O/S, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kVline (this trips Hallet GT + WF), Feedback | Outage | SA
F_WESTCOAST_LREG_0 | 584.4026 | 0 | 1.8333 | 0 | LREG FCAS of West Coast Generation limited to 0 MW | Outage | FCAS
N>>N-KVCW_10_15M | 580.7093 | 0 | 0.83333 | 0 | Out = KangarooValley-Capital(3W), avoid O/L Canberra to Yass (9) on trip of Lower Tumut to Yass (3) line, Feedback | Outage | NSW
F_T+FASH_N-2_TG_R5 | 550.2721 | 113.928 | 5.3333 | 4.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
V::N_EPMB_xxx | 540.6151 | 335.6252 | 0.66667 | 3.8333 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
VSML_-050 | 539.828 | 0 | 1.4167 | 0 | Vic to SA on ML upper transfer limit of -50 MW | Outage | Vic
NQTE_-050 | 536.7098 | 0 | 6.5 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -50 MW | Outage | NSW
V>V_NIL_9 | 534.9116 | 0 | 0.25 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Crowlands to Bulgana to Horsham 220kV line (this trips Bulgana WF), Feedback | NIL | Vic
F_Q++BCDM_R60 | 530.7901 | 0 | 2.1667 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage | FCAS
S>>RBTU_RBPA_WEWT | 520.0212 | 0 | 4.0833 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
V:T_HAGT_BL_1 | 517.0429 | 0 | 0.66667 | 0 | Out = Hadspen to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
S_HPRL1_E | 500.2828 | 2647.6904 | 0.91667 | 3.1667 | Out= Nil, Hornsdale Battery load energy target <= 40 MW | NIL | SA
V>>V-MSUT_1 | 499.8434 | 2484.9675 | 1.25 | 4.4167 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback | Outage | Vic
S>>RBTU_TWPA_TPRS | 499.2274 | 0 | 1.1667 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
F_NQ++65_66_RAD_L5 | 491.0509 | 0 | 10.0833 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 5 min Requirement | Outage | FCAS
V::N_SMF2_xxx | 483.8453 | 0 | 3.8333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>V_KTS_TX_A3_2A_R | 468.8826 | 0 | 3.25 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
V_ARWF_FSTTRP_5 | 460.3213 | 5044.5111 | 0.16667 | 2.0833 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
CA_MQS_4C47A69C_01 | 458.7169 | 0 | 0.75 | 0 | Constraint Automation, O/L BATS_WBTS_220 @WBTS for CTG LNAB on trip of DARL-BAL-BURONGA X5/1&/3 220KV LNS. Generated by STNET[NORFL] Host MANEEMP2(MQ) | Outage | Constraint Automation
F_Q_MEWV_823_R5 | 454.1647 | 0 | 3.6667 | 0 | Out= Mt England to Wivenhoe (823) line, Raise 5 min requirement of zero for Wivenhoe #1 | Outage | FCAS
V>V_HWYP2_1_R | 427.8044 | 1891.6976 | 0.41667 | 2.0833 | Out = Hazelwood to Yallourn No. 2 220 kV line, avoid O/L Yallourn to Hazelwood PS No.1 220kV line on trip of Yallourn to Rowville No.5 220kV line, Radial mode, YWG1 on 220kV, Feedback | Outage | Vic
Q_CS_2000 | 405.909 | 413.9815 | 0.083333 | 1.5833 | Qld Central to Qld South upper transfer limit of 2000MW (discretionary) | Outage | Qld
NV_0000 | 399.0028 | 0 | 1.0833 | 0 | Discretionary NSW to Vic transfer upper limit of 0 MW | Outage | NSW
N>>V-NIL_HJ | 394.2064 | 0 | 3.3333 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) O/L on Nil trip; Feedback | NIL | NSW
V>>V_LTMS_1 | 391.6754 | 0 | 1.8333 | 0 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage | Vic
T>T_CRNN_3 | 373.9716 | 0 | 0.83333 | 0 | Out= Creek Rd to New Norfolk 110 kV line, avoid O/L New Norfolk to Chapel St 110 kV line for loss of Waddamana to Palmerston 110 kV line, Feedback | Outage | Tas
S>>X_DVLK+LKCN_02 | 370.3961 | 0 | 1.3333 | 0 | Out= Davenport-Mt Lock-Canowie 275kV line (this offloads Hornsdale #1 & #2 &#3 WF & battery) OR Davenport-Mt Lock 275kV line O/S, avoid O/L Waterloo East-Waterloo 132kV line on trip of Belalie-Davenport 275kV line, Feedback | Outage | SA
CA_BRIS_4D0EE093_1 | 369.6861 | 0 | 0.083333 | 0 | Constraint Automation, O/L EPS_MBTS2_220:LEP2:Z:220@MBTS@VIC for CTG LVCY on trip of EPS-MBTS1 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage | Constraint Automation
V^SML_KGRC_4 | 367.6002 | 328.8384 | 5.3333 | 1.5 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Vic
S>X_DV-BR-PA_06 | 362.0959 | 0 | 0.083333 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Canowi-Robertstown 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_VS+65_66_RAD_R5 | 345.055 | 0 | 0.91667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS
V:T_SHGT_BL_1 | 337.4598 | 0 | 0.91667 | 0 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
V::S_BLKRG_MAXG_2 | 336.6304 | 7757.0674 | 0.83333 | 19.6667 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
F_T++CSGO_TG_R6 | 333.6329 | 0 | 0.083333 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS
N>>N-NIL_64 | 331.6039 | 0 | 0.16667 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | NSW
F_Q++8C_L5 | 330.6952 | 816.1684 | 2.1667 | 16.5 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage | FCAS
N>>V-LTMS_5 | 329.9665 | 966.2142 | 1.4167 | 0.91667 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L(15m rating) on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage | NSW
F_T+FARE_N-2_TG_R5 | 324.1627 | 139.6305 | 2.75 | 2.6667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS
S>>X_RBTU+CB_7 | 315.1002 | 0 | 1.3333 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, avoid O/L Robertstown 275/132kV #1 transformer on trip of Robertstown - Para line (this offloads Robertstown TX#2 132/275kV ) | Outage | SA
F_S+SNS_TG_R5 | 311.5798 | 0 | 0.66667 | 0 | Raise 5 min Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage | FCAS
S>>X_RBTU+CB_1 | 308.3141 | 0 | 0.16667 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) lines, Feedback | Outage | SA
S>>X_BLDV+WEMWP4_05 | 305.4943 | 0 | 0.16667 | 0 | Out= Out= Belalie-Davenport 275kV line + Waterloo East-MWP4-Robertstown 132kV line), avoid O/L Templers-Roseworthy 132k on trip of Templers West-Para 275kV line, Feedback | Outage | SA
V::S_PATU_MAXG | 305.1713 | 0 | 2.1667 | 0 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
V_S_NIL_ROCOF | 303.4329 | 161.1965 | 2.5833 | 2.4167 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | Vic
F_T+FASH1_2C_RREG | 302.8504 | 3460.0889 | 0.16667 | 16.3333 | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS | Outage | FCAS
N_BROKENHSF_FLT_26 | 302.0038 | 0 | 0.41667 | 0 | Limit Broken Hill Solar Farm upper limit to 26 MW to manage post contingent voltage oscillation | Outage | NSW
F_T++NIL_BLSPS_R60_2 | 292.106 | 0 | 4.5833 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL | FCAS
F_T+NIL_BB_TG_R60 | 260.75 | 26.7 | 9.3333 | 0.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
V>SMLMHNW2 | 259.5724 | 0 | 0.66667 | 0 | Out = Monash-North West Bend # 2 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 1 132kV line | Outage | SA
NQTE_-090 | 259.0062 | 0 | 1.3333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -90 MW | Outage | NSW
T_ROCOF_3 | 256.962 | 0 | 0.58333 | 0 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | Tas
F_S+RREG_0035 | 246.4974 | 382426.3315 | 0.33333 | 17.5833 | SA Raise Regulation FCAS Requirement greater than 35 MW | Outage | FCAS
T^T_LFWA_1 | 242.7006 | 0 | 0.33333 | 0 | Out = Lindisfarne to Waddamana 220 kV line, avoid voltage instability or violations for loss of the other Lindisfarne to Waddamana 220 kV line line | Outage | Tas
F_VST++65_66_RAD_R60 | 237.5842 | 0 | 6.6667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; VIC, SA and TAS Raise 60 sec Requirement | Outage | FCAS
V^SML_HORC_2 | 231.9672 | 4.5441 | 9.3333 | 0.25 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage | Vic
SV_070 | 227.4648 | 0 | 0.16667 | 0 | SA to Victoria on VicSA upper transfer limit of 70 MW | Outage | SA
Q^^N_AR_SVC_1 | 227.0083 | 0 | 1.5833 | 0 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Qld
V>>V_NIL_9 | 226.5974 | 0 | 0.33333 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Vic
N>N-ARKS_GITN_1 | 219.6342 | 0 | 5.4167 | 0 | Out= Armidale to Kempsey (965) and Glen Innes to Tenterfield (96R) avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 Directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
V>>V-JNWG_RADIAL_1A | 218.6558 | 0 | 0.66667 | 0 | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage | Vic
N>N-BAMB_132_OPEN_B | 217.8057 | 0 | 0.25 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage | NSW
F_T+FARE_N-2_TG_R60 | 211.2251 | 14.4905 | 5.1667 | 0.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T+FASH1_2C_TG_R5 | 210.0191 | 0 | 1.9167 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
V_GANWR_BAT_L_ISL_0 | 209.7165 | 0 | 0.16667 | 0 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
N>>V-MSUT_5 | 203.6962 | 0 | 1.3333 | 0 | Out= Murray-UpperTumut(65), avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage | NSW
S>>RB_275KV_N_BUS_3 | 200.5676 | 0 | 0.41667 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | SA
V>SMLARHO4 | 195.5158 | 1.1278 | 2.75 | 0.083333 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
F_VS++65_66_RAD_R5 | 195.4224 | 0 | 2.25 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_T++NIL_BLSPS_L6_2 | 192.7217 | 0 | 0.91667 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL | FCAS
T_T_FASH_8_N-2 | 191.7601 | 0 | 0.083333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation >= 90% of West Coast load | Outage | Tas
Q_STR_43239_SMSF_38 | 191.5651 | 0 | 0.16667 | 0 | Limit Sun Metals SF to 50% capacity (38 inverters), if (Kareeya >= 2 + Invicta on OR Kareeya=4) + Stanwell >=3 + Callide >=2 + Gladstone >=3 + (Stan+Cal+Glad >=9). Zero otherwise. | Outage | Qld
F_MAIN++NIL_BL_L60 | 181.3166 | 1.47 | 83.6667 | 2.3333 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS
N-SAPHWF_TX | 180.6202 | 0 | 0.083333 | 0 | Outage = One Sapphire wind farm 330/33kV transformer (1A or 1B), Sapphire WF Isolators 2415 and 2416 closed | Outage | NSW
F_WESTCOAST_RREG_0 | 180.2281 | 0 | 2.8333 | 0 | RREG FCAS of West Coast Generation limited to 0 MW | Outage | FCAS
T_LIPM2_SLOAD_1_N-2 | 176.9678 | 0 | 1.0833 | 0 | Out=Liapootah-Waddamana-Palmerston #2 220kV line and associated CBs at Waddamana I/S, loss of the #1 parallel 220kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Tas
S:V_550_HY_TEST_DYN | 172.0877 | 0 | 0.25 | 0 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
N^N_KKLS_1 | 171.0685 | 2767.3065 | 0.58333 | 20 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | NSW
F_T+FARE_N-2_RREG | 166.5153 | 560.1774 | 5.1667 | 0.58333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | FCAS
F_T++NIL_ML_L60 | 159.7304 | 2035.9827 | 271.6667 | 656.9167 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
F_T++FARE_N-2_TG_R5 | 159.7208 | 17.801 | 1.3333 | 0.083333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_S+PPT_R6_1 | 156.5247 | 14500 | 0.25 | 0.083333 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 1 | Outage | FCAS
F_Q_MEWV_823_R60 | 156.3252 | 0 | 1.5 | 0 | Out= Mt England to Wivenhoe (823) line, Raise 60 sec requirement of zero for Wivenhoe #1 | Outage | FCAS
Q_NIL_STRGTH_SMSF | 152.9288 | 0 | 0.16667 | 0 | Out = Nil, limit Sun Metal SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to TOA 393 | NIL | Qld
SVML_233 | 143.8312 | 1348.5425 | 0.5 | 3.5 | SA to Vic on ML upper transfer limit of 233 MW | NIL | SA
NSA_V_NPSD_100 | 143.1131 | 0 | 0.33333 | 0 | Newport unit >= 100 MW for Network Support Agreement | Outage | Vic
F_I+ML_L5_APD | 141.8727 | 41.79 | 32.8333 | 20.5 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage | FCAS
N>N-GITN_TE_C1 | 138.3954 | 95.0685 | 2.4167 | 0.75 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
T>T_GTSH_5K | 134.4974 | 0 | 0.16667 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L line terminal equipment of Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line, feedback | Outage | Tas
F_T+FASH1_2C_TG_R60 | 132.9342 | 0 | 0.33333 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
F_T+CSGO_TG_R5 | 131.6912 | 0 | 0.66667 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
F_T+NIL_BB_TG_R6 | 131.2 | 5.8 | 5.0833 | 0.33333 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
S-DLBAT-L_0 | 129.6855 | 0 | 0.25 | 0 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW | Outage | SA
QN_1000 | 128.2552 | 0 | 1 | 0 | Qld to NSW on QNI upper transfer limit of 1000 MW | Outage | Qld
F_ESTN+MG_R5 | 127.11 | 30 | 4.8333 | 0.083333 | Raise 5 min Service Requirement for Eastern Generation Event | Outage | FCAS
N>>V-JNWG_RADIAL_3 | 124.2495 | 0 | 0.58333 | 0 | Out = Jindera to Wagga(62), avoid O/L Upper Tumut to Murray (65) using 15 mins rating on trip of Lower Tumut to Murray (66) line, Feedback | Outage | NSW
T>T_NIL_BL_110_8_1 | 123.9994 | 0 | 0.33333 | 0 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
F_QNV++MG_R6 | 120.7411 | 0 | 0.41667 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS
F_S+PPT_R60 | 116.16 | 0 | 2.9167 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage | FCAS
S>>BWMP_TWPA_TPRS | 115.7733 | 0.01612 | 0.41667 | 0.16667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
V::N_MLMO_xxx | 109.5353 | 0 | 0.41667 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V:SS_820_HY_TEST_DYN | 109.4279 | 114.865 | 0.58333 | 0.16667 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
V::S_NIL_TBSE_1 | 108.5948 | 0 | 0.33333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
F_NQ++65_66_RAD_L60 | 105.8017 | 0 | 10.0833 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 60 sec Requirement | Outage | FCAS
Q>>LCCP_CLWU_BCCP_2 | 104.7485 | 589.8442 | 0.58333 | 1.6667 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
F_Q_MEWV_824_R60 | 103.3169 | 0 | 1.5833 | 0 | Out= Mt England to Wivenhoe (824) line, Raise 60 sec requirement of zero for Wivenhoe #2 | Outage | FCAS
T_PMPO_220 | 103.1449 | 0 | 0.16667 | 0 | Out=A single Palmerston-Poatina 220KV line. One line out of service only | Outage | Tas
F_T++FASH_N-2_TG_R60 | 93.419 | 129.4877 | 2.75 | 3.8333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
N>>N_65+66_N-2_5 | 91.5693 | 0 | 0.5 | 0 | Out= Nil, avoid O/L Wodonga to Jindera (060) on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL | NSW
S>>X_RBPA+BGTX_18 | 90.4725 | 0 | 0.083333 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo East-MWP4-Robertstown 132kV line, on trip of Brinkworth 132/275kV TX, Feedback | Outage | SA
V::N_X_HWSM_HWRO_xxx | 86.926 | 0 | 0.16667 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T>>T_NIL_BL_EXP_6E | 83.0987 | 0 | 0.25 | 0 | Out = Nil, avoid O/L a Sheffield to Georgetown 220 kV line (flow to Georgetown) for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
V::N_SMSY_xxx | 78.8149 | 0 | 0.16667 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_T++CSGO_TG_R5 | 73.5994 | 66.91 | 0.33333 | 0.58333 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS
N>>V-NIL_O | 73.3862 | 8134.8946 | 0.83333 | 21.75 | Out = Nil, avoid overloading Upper Tumut to Murray (65) using 15 mins rating line on trip of Lower Tumut to Wagga (051) + 970,990,99M (out of Yass) line, Feedback | NIL | NSW
F_T++CSGO_TG_R60 | 72.3653 | 0 | 0.33333 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS
T_LIPM_SLOAD_1_N-2 | 69.3457 | 0 | 0.83333 | 0 | Out=Liapootah-Waddamana-Palmerston 220kV line, loss of the remaining Liapootah to Waddamana to Palmerston 220kV line and 133 MW South load declared credible, limit Sth to Nth flow to rating of Palmerston-Waddamana 110kV line minus 133 MW, feedback | Outage | Tas
F_MAIN++ML_L5_APD | 68.5278 | 26.51 | 13.8333 | 9.9167 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
N>N_LSDU_9U6_2 | 67.8424 | 0 | 0.83333 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage | NSW
T>T_NIL_BL_220_6B | 67.3069 | 0 | 0.16667 | 0 | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
V_VS_MLMO_NETT | 67.2312 | 0 | 1.9167 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage | Vic
F_Q_W/HOE_R60 | 67.0682 | 0 | 0.58333 | 0 | Out= Nil, Wivenhoe Raise 60 services <= 0 MW when both units are online in gen mode | Outage | FCAS
F_T+NIL_BB_TG_R5 | 64.1678 | 9.4 | 1.1667 | 0.16667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
Q_NESTM_STRGTH_HAUSF | 60.7887 | 0 | 0.083333 | 0 | Out = 822, Limit Haughton SF to 50% of max capacity (#40 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
F_I+ML_L6_APD | 58.9 | 37.57 | 165.8333 | 172.9167 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
F_Q++BCDM_R6 | 57.3434 | 0.69868 | 1.25 | 0.083333 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage | FCAS
F_S++OSB_R60 | 57.04 | 0 | 1.3333 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA | Outage | FCAS
F_T++NIL_BLSPS_L60_1 | 54.76 | 0 | 72.25 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS
F_T+FARE_N-2_TG_R6_1 | 51.3519 | 1169.3009 | 2.8333 | 1.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage | FCAS
S>>NIL_TBCG_TBTU_1 | 49.9409 | 0 | 0.16667 | 0 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | SA
F_QNV++MG_R5 | 49.6798 | 0 | 1.25 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS
T^V_NIL_BL_6 | 49.1485 | 0 | 0.083333 | 0 | Outage = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
F_V+NIL_APD01_R6 | 48.9586 | 176.8579 | 0.25 | 3.5 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
F_V+NIL_APD01_R60 | 47.9618 | 228.95 | 0.25 | 3.5833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
F_T++FASH_N-2_TG_R5 | 45.9321 | 2366.8855 | 0.83333 | 2.4167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
CA_SPS_4B902E2A_01 | 45.7778 | 0 | 0.91667 | 0 | Constraint Automation, O/L 9U7/M @MULLUMB for CTG LNYI on trip of 9G5 EWINGSDL-MULLUMB 132KV LINE. Generated by STNET[NORFR] Host NOREEMP3(SP) | Outage | Constraint Automation
V>>N-JNWO_RADIAL_2 | 45.0487 | 19.2704 | 1.5 | 0.083333 | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Vic
F_T++NIL_BLSPS_L6_1 | 44.7121 | 0 | 72.1667 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS
F_MAIN++ML_L6_APD | 43.97 | 33.0199 | 35 | 109.5833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
S::V_NIL_TBSE_2 | 43.3094 | 0 | 0.66667 | 0 | Out = Nil(Note: with both Black Range series capacitors O/S); SA to VIC Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
F_T_FARC2_R6 | 42.0067 | 0 | 0.25 | 0 | Out=Farrell-Reece 2 220KV line. R6 <= 0MW | Outage | FCAS
N^N-X_96H_LS_SVC | 41.8451 | 0 | 0.91667 | 0 | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Coffs Harbour to Lismore (89) trip; TG formulation only | Outage | NSW
N>>N-MNYS5_01_15M | 37.9002 | 0 | 0.16667 | 0 | Out = Marulan-Yass(5), avoid O/L Marulan to Yass (4) using 15 mins rating on trip of Bannaby to Gullen Range (61) line, Feedback | Outage | NSW
S>>X_TPRS+TPDR_1 | 37.8639 | 0 | 0.083333 | 0 | Out= Templers-Roseworthy 132kV line + Templers-Dorrien 132kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | Outage | SA
F_QNV+MLMO_L60 | 37.0623 | 0 | 9.5 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_Q_MACKAYGT_R5 | 31.68 | 0 | 2.6667 | 0 | Out= NIL, Mackay GT R5 Requirement <= 0MW | Outage | FCAS
V:SS_820_HY_TEST | 28.6978 | 101.9453 | 0.16667 | 0.083333 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
F_I+ML_L5_0400 | 27.8 | 25.6064 | 35.8333 | 26.1667 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL | FCAS
V>>SML_NIL_6 | 25.9333 | 0 | 0.083333 | 0 | Out= Nil, Avoid pre-contingent overload of Waubra to Ballarat 220kV line, Feedback | NIL | Vic
F_S+SNS_TG_R60 | 25.64 | 0 | 0.58333 | 0 | Raise 60 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage | FCAS
N>N_LSDU_9U6_3 | 25.2443 | 0 | 0.66667 | 0 | Out= one of Lismore 132 to Mullumbimby 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line for trip of 9G5 (Mullumbimby to Ewingsdale) 132kV line | Outage | NSW
V>>N-BURC_2N | 25.1151 | 0 | 0.083333 | 0 | Out = Buronga to Red Cliffs(OX1), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
V::N_WBHO_xxx | 23.2774 | 9715.2701 | 0.083333 | 21.25 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_ESTN++MLTR_L60 | 22.23 | 0 | 28.1667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
S>>DVBL_LKDV_WEWT | 21.3413 | 0 | 0.25 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East- Waterloo 132kV on trip of Mt Lock-Davenport 275kV line, Feedback | Outage | SA
T>T_NIL_BL_IMP_5FF | 20.9172 | 0 | 0.083333 | 0 | Out = Nil, avoid O/L Hadspen to Georgetown No. 2 220 kV line (flow to North) for trip of the Hadspen to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V^^S_TBTX+CB_SETB_2 | 20.7693 | 137.7176 | 0.41667 | 1.3333 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
S>>TBTU_TBCG_TBMO | 20.4827 | 0 | 0.16667 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage | SA
F_T++NIL_BLSPS_L5 | 19.7 | 0 | 22.5 | 0 | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL | FCAS
F_NQ++65_66_RAD_L6 | 19.59 | 0 | 7 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 6 sec Requirement | Outage | FCAS
F_I+ML_L60_APD | 18.81 | 6.45 | 27 | 18.5833 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
NQTE_-040 | 17.696 | 0 | 0.58333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -40 MW | Outage | NSW
F_MAIN++WIP_N-2_MLL6 | 17.34 | 4.5614 | 9.6667 | 3.8333 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS
F_T++NIL_BLSPS_L60_2 | 17 | 0 | 0.83333 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL | FCAS
S>>DVBL_RBTU_WEWT | 16.3467 | 0 | 0.16667 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
F_I+ML_L6_0500 | 15.7704 | 0 | 13.9167 | 0 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 500 | Outage | FCAS
F_I+ML_L5_0500 | 15.664 | 0 | 9.5833 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 500 | Outage | FCAS
V>>V_KGWT_2 | 14.3755 | 0 | 0.083333 | 0 | Out = Kerang to Wemen 220kV line, avoid overloading Bulgana to Horsham 220kV line section for loss of Balranald to Buronga (X3) 220kV line | Outage | Vic
F_ESTN++HYTR_L60 | 14.0417 | 5.05 | 10.1667 | 2.4167 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
F_S+NIL_HPR_G+L_LREG | 14 | 0 | 0.083333 | 0 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS LowerReg ramping constraint | NIL | FCAS
F_V+NIL_APD01_R5 | 12.45 | 500.2766 | 0.25 | 3.5 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
F_T++COGT_TL_L6 | 12.3297 | 2203.9378 | 2.6667 | 12.5 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
N::V_WA_BUSA_MSDD | 12.0806 | 0 | 0.16667 | 0 | Out= Wagga 330kV A Bus, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | NSW
V^^SML_NIL_3 | 11.611 | 0 | 0.5 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Vic
F_T++NIL_BLSPS_R60_3 | 11 | 0 | 0.083333 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 3, FCSPS unavailable | NIL | FCAS
F_Q_MK_33BUS_R5 | 10.89 | 0 | 0.91667 | 0 | Out=T38 Mackay 33kV C Bus (R5 Requirement) | Outage | FCAS
F_MAIN+ML_L5_APD | 10.84 | 0.45 | 1.0833 | 0.083333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
V>>N-JNWO_RADIAL_1 | 10.4355 | 0 | 0.25 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
F_ESTN++MLTR_L5 | 9.7077 | 0 | 4.8333 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage | FCAS
F_I+ML_L60_0400 | 9.18 | 4.71 | 14.75 | 12.75 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS
F_MAIN++ML_L60_APD | 8.84 | 6.37 | 7.5 | 11.6667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
F_MAIN++ML_L5_0500 | 8.4019 | 0 | 2.8333 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage | FCAS
F_ESTN++MLMO_L60 | 7.81 | 0 | 14.0833 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
F_I+ML_L60_0500 | 7.67 | 0 | 8 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 500 | Outage | FCAS
N>>V-NIL_HC | 7.0009 | 0 | 0.083333 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; Feedback | NIL | NSW
F_I+TL_L5_0550 | 6.69 | 0 | 3.3333 | 0 | Lower 5 min Service Requirement for a NEM Network Event, TL = 550 | Outage | FCAS
F_I+WIP_N-2_ML_L6 | 6.67 | 13.4586 | 14 | 29.6667 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 6 sec requirement | Outage | FCAS
F_MAIN++ML_L6_0500 | 6.469 | 0 | 3 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage | FCAS
F_I+TL_L60_0550 | 6.14 | 0 | 3.3333 | 0 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 550 | Outage | FCAS
F_MAIN+ML_L5_0400 | 6.09 | 10.55 | 5.5833 | 3.9167 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_QNV++MLTR_L60 | 5.9 | 0 | 4.9167 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
S>>X_RBPA+BGTX_02 | 5.7725 | 0 | 0.16667 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Robertstown-MWP4-Waterloo East 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
N>>V-LTUT_J | 5.7219 | 0 | 0.16667 | 0 | Out = LowerTumut-UpperTumut(64), avoid Upper Tumut to Murray(65) O/L on Nil trip; Feedback | Outage | NSW
F_T++FARE_N-2_TG_R60 | 5.32 | 1.4 | 0.41667 | 0.083333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_MAIN++ML_L5_0400 | 5.07 | 4.2536 | 2.5833 | 3.25 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS
F_QNV+MLTR_L60 | 4.9955 | 0.74 | 1.4167 | 0.16667 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_MAIN+ML_L6_APD | 4.96 | 2.75 | 6.75 | 7.5 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_T++NIL_BLSPS_R5 | 4.7252 | 0 | 0.25 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL | FCAS
F_QNV+HYMO_L60 | 4.657 | 0 | 3.5 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_ESTN+ML_L60_0400 | 4.52 | 0.03 | 4.6667 | 0.083333 | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS
F_ESTN+ML_L6_0400 | 4.4 | 0.03 | 4.8333 | 0.083333 | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS
F_ESTN+ML_L5_0400 | 4.16 | 0 | 4.6667 | 0 | Lower 5 min requirement for a Eastern Load Event, ML = 400 | Outage | FCAS
F_MAIN+WIP_N-2_ML_L6 | 3.05 | 1.57 | 1.1667 | 1 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_MAIN++ML_L60_0500 | 2.75 | 0 | 2 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage | FCAS
F_ESTN++HYTR_L5 | 2.7206 | 4.93 | 1.5 | 2.4167 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage | FCAS
F_MAIN+ML_L60_APD | 2.39 | 0.12 | 1.1667 | 0.16667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_MAIN+ML_L5_0500 | 2.31 | 0 | 0.41667 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS | Outage | FCAS
T>T_NIL_BL_IMP_6E | 2.2839 | 0 | 0.16667 | 0 | Out = Nil, avoid O/L Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action, feedback | NIL | Tas
F_MAIN+ML_L60_0400 | 2.2 | 2.99 | 3.0833 | 3.5833 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_MAIN+ML_L6_0500 | 1.77 | 0 | 0.41667 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS | Outage | FCAS
F_MAIN++ML_L60_0400 | 1.48 | 0.53 | 1.4167 | 1.8333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS
VS_050 | 1.4748 | 1804.4761 | 0.16667 | 8.4167 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Vic
V>>V_KTS_TX_A3_3A_R | 1.3998 | 0 | 0.083333 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr for trip of ROTS A1 500/220 kV txfmr, radial mode, Yallourn W unit 1 on 500 kV network, feedback | Outage | Vic
F_MAIN++ML_L6_APD_LD | 1.26 | 0 | 0.58333 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage | FCAS
V>SML_NSWRB_10 | 1.0888 | 16487.4915 | 0.083333 | 2.6667 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL | Vic
F_T++COGT_TL_L60 | 1.0039 | 10.34 | 1.1667 | 12.5 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
V::S_RBTU_SETB | 0.89246 | 0 | 0.083333 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
F_QNV++HYTR_L60 | 0.83 | 0 | 0.66667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
S>>X_RBPA+CB_03 | 0.76566 | 446.8139 | 0.16667 | 8.6667 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
F_MAIN+ML_L60_0500 | 0.7 | 0 | 0.41667 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS | Outage | FCAS
F_I+WIP_N-2_ML_L5 | 0.56 | 5.7 | 0.16667 | 3.5833 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 5 Min requirement | Outage | FCAS
F_QNV+MLTR_L5 | 0.44 | 1 | 0.083333 | 0.16667 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T++COGT_TL_L5 | 0.43 | 63.65 | 0.41667 | 12.5 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
F_QNV++MLTR_L5 | 0.41 | 0 | 0.33333 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_QNV++HYTR_L5 | 0.3 | 0.02 | 0.16667 | 0.083333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_QNV+HYTR_L60 | 0.2 | 0 | 0.16667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_ESTN+APD_TL_L5 | 0.16 | 0 | 0.16667 | 0 | Lower 5 min requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
F_ESTN+APD_TL_L60 | 0.16 | 0 | 0.16667 | 0 | Lower 60 sec requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
F_QNV+MLMO_L6 | 0.16 | 0 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_QNV+HYMO_L5 | 0.15 | 0 | 0.16667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_QNV++MLMO_L60 | 0.13 | 0 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_I+WIP_N-2_ML_L60 | 0.09 | 2.69 | 0.16667 | 3.4167 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 60 sec requirement | Outage | FCAS
F_QNV++ML_L60_0400 | 0.09 | 0 | 0.16667 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage | FCAS
F_I+ML_L6_APD_LD | 0.08 | 0 | 0.33333 | 0 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage | FCAS
F_QNV+MLMO_L5 | 0.08 | 0 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS
T>T_LIPM_110_2B | 0.04 | 73059.7307 | 0.083333 | 126 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
T_PMPO_TWO_220 | 0.02 | 0 | 0.083333 | 0 | Out= two Palmerston to Poatina 220KV lines | Outage | Tas

## Summary By Region
Binding Hours
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019
Ad-Hoc |  |  |  |  | 0 | 0
Constraint Automation | 12.25 | 5.5 | 24.9167 | 4.75 | 1.3333 | 8.5833
Direction |  | 3.6 | 18.3333 | 1152.0833 | 8190.0833 | 4093.5833
FCAS
NSW | 3586.0833 | 3112.1667 | 2768.5 | 4260.0833 | 3057.8333 | 4993.6667
Negative Residue | 12.25 | 13.0833 | 46.8333 | 25.75 | 10.4167 | 24.1667
Non-Conformance | 358.5 | 228.6667 | 156.6667 | 97.3333 | 61.0833 | 93.75
Other | 35.5833 | 142.6667 | 50.5833 | 311.8333 | 115.25 | 64.3333
Outage Ramping | 162.5833 | 236.8333 | 251.8333 | 142.25 | 174.4167 | 475.0833
Qld | 2850.25 | 913.75 | 1756.6667 | 996.6667 | 511.3333 | 3120.5833
Quick | 132.3333 | 281.5 | 1000.0833 | 1918.25 | 12617.6667 | 10994.8333
SA | 2144.9167 | 3383.5833 | 3995.1667 | 2013.25 | 3285.75 | 3935.6667
Tas | 1247.1667 | 354.5833 | 895.9167 | 923.1667 | 1027.6667 | 966.5833
Vic | 3277.5833 | 5660.4167 | 6854 | 2618 | 1914.5 | 5095.75
Binding Impact
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019
Ad-Hoc | 0 | 0 | 0 | 0 | 0 | 0
Constraint Automation | 72630.7349 | 61543.4159 | 64122.5584 | 6287.0142 | 4494.9703 | 59181.5539
FCAS | 2312077.1775 | 11967737.2201 | 27702893.4048 | 24018595.0767 | 11563905.7935 | 14750181.9392
NSW | 2666446.6314 | 3008201.0876 | 2981579.7124 | 3811263.7887 | 4130424.9984 | 20853119.0897
Negative Residue | 193679.0393 | 133618.843 | 159141.1919 | 65879.5695 | 190929.9383 | 357086.6257
Other | 1327.1417 | 5944.8762 | 35445.6298 | 19441.5552 | 11515.5764 | 31229.546
Qld | 3351642.8339 | 17832407.3191 | 3412397.6405 | 1557960.0849 | 1092572.6105 | 14405785.5151
SA | 7308788.4534 | 7975370.452 | 19175976.6502 | 19603528.2545 | 49743082.8304 | 23177002.4614
Tas | 7917341.1843 | 2498349.5552 | 3312667.8479 | 4771966.3751 | 2671514.9731 | 5630711.8908
Vic | 6717447.0811 | 3149671.2278 | 6498415.4069 | 3681628.8597 | 3495766.3104 | 19701434.9435
Total | 30541380.2775 | 46632843.9969 | 63342640.0428 | 57536550.5786 | 72904208.0013 | 98965733.5652
Note on A6: FCAS excluded as it will swamp the graph

## NIL vs Outage
Binding Hours
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019
Commissioning | 36.3333 | 166.5 | 151.3333 | 501.9167 | 12116 | 10389.25
FCAS - NIL | 71339 | 78805.6667 | 98151.5 | 83335.5 | 89035.8333 | 86275.9167
FCAS - Outage | 5271.75 | 2785.8333 | 6213.6667 | 5623.9167 | 6087.5833 | 18781.8333
System Normal | 8116.3333 | 7848.6667 | 9089.4167 | 6047.6667 | 4947.25 | 8902
Network Support | 155.8333 | 204.5 | 128.3333 | 55.6667 | 210.3333 | 74.25
Negative Residues | 12.25 | 13.0833 | 46.8333 | 25.75 | 10.4167 | 24.1667
Outage | 5240.1667 | 5748.1667 | 7284.5833 | 5121.75 | 4817.0833 | 9302.6667
Total (non-FCAS) | 13560.9167 | 13980.9167 | 16700.5 | 11752.75 | 22101.0833 | 28692.3333
Binding Impact
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019
Commissioning | 23582.5681 | 1122946.4259 | 1067028.2274 | 933870.4383 | 48442546.0203 | 68138620.5509
FCAS - NIL | 1920731.4196 | 1523297.0635 | 4284769.1816 | 9691374.8176 | 8309289.3932 | 10234061.3339
FCAS - Outage | 391353.9579 | 10444462.1066 | 23418124.2233 | 14327220.2591 | 3254616.4004 | 4516120.6054
System Normal | 20601341.3495 | 7628472.3458 | 13101240.0894 | 16979263.4586 | 20382744.3293 | 37998718.3151
Network Support | 4678541.5594 | 22261395.2873 | 8878912.2779 | 965379.2057 | 30414067.7368 | 683796.7041
Negative Residues | 193679.0393 | 134581.6187 | 159141.1919 | 65879.5695 | 190929.9383 | 357086.6257
Outage | 2769291.9038 | 4643343.5874 | 13500453.0789 | 15507433.2681 | 10352560.2034 | 45175949.9811
Total | 30578521.7976 | 47758498.4352 | 64409668.2703 | 58470421.0169 | 121346754.0216 | 167104354.1161

## Interconnector Binding
Interconnector Direction | Constraint Equation ID | 2019 Hours | 2018 Hours | Description | Type
N-Q-MNSP1 Export | QNTE_SUPPORT | 82.6667 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage
N-Q-MNSP1 Export | NQTE_-060 | 79.8333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -60 MW | Outage
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 76.1667 | 38.6667 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
N-Q-MNSP1 Export | N_X_MBTE_3A | 36.5 | 57.1667 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Export | N^N_CHLS_1 | 29.5833 | 3.1667 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | NIL
N-Q-MNSP1 Export | N^^Q_NIL_A | 22.5833 | 4.25 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
N-Q-MNSP1 Export | N^N-LS_SVC | 22.3333 | 461.0833 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage
N-Q-MNSP1 Export | N>LSDU9U6_LSDU9U7 | 22.0833 | 3.5833 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 20.9167 | 109.25 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | QNTE_OSCILLATE | 19.4167 | 4.8333 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage
N-Q-MNSP1 Export | N>N-NIL_LSDU | 16.6667 | 3.5 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Export | N>N-ARKS_TE_A1 | 11.75 | 0 | Out= Armidale to Kempsey (965), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | NQTE_ROC | 11.75 | 72.8333 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Export | N_X_MBTE2_A | 11.3333 | 44.5833 | Out= two Directlink cables, NSW to Qld limit | Outage
N-Q-MNSP1 Export | NQTE_-070 | 10.1667 | 1.25 | NSW to Qld on Terranora Interconnector upper transfer limit of -70 MW | Outage
N-Q-MNSP1 Export | N>Q_LSLS_9U8 | 8.5833 | 0 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 directlink cable O/S. | Outage
N-Q-MNSP1 Export | N>N-LSTN_TE_C1 | 6.8333 | 0.16667 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | NQTE_-050 | 6.5 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -50 MW | Outage
N-Q-MNSP1 Export | N>N-NIL_TE_E1 | 6.1667 | 0 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST | NIL
N-Q-MNSP1 Export | N>N-ARKS_GITN_1 | 5.4167 | 0 | Out= Armidale to Kempsey (965) and Glen Innes to Tenterfield (96R) avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 Directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 3.0833 | 1 | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N>N-GITN_TE_C1 | 2.3333 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | N>N-96H+96R_TE_1 | 2.1667 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage
N-Q-MNSP1 Export | Q^^TR_CLHA_-250 | 2 | 0 | Nominated offset -250 MW, Tarong voltage stability limit, Calvale-Halys contingency equation | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_E_E | 1.4167 | 6.0833 | N-Q-MNSP1.ENERGY * 1 <= 100 (Wt = 35) | Other
N-Q-MNSP1 Export | N>>N-NIL__3_OPENED | 1.4167 | 2.6667 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL
N-Q-MNSP1 Export | NQTE_-090 | 1.3333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -90 MW | Outage
N-Q-MNSP1 Export | N^N-X_96H_LS_SVC | 0.91667 | 0 | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Coffs Harbour to Lismore (89) trip; TG formulation only | Outage
N-Q-MNSP1 Export | N^N_KKLS_1 | 0.83333 | 19.3333 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage
N-Q-MNSP1 Export | #R018324_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018768_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018776_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019035_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019040_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018794_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019475_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N>N-ARKS_GITN_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | NQTE_-040 | 0.58333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -40 MW | Outage
N-Q-MNSP1 Export | #R018923_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018324_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018444_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018768_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018776_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018923_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018928_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019040_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019247_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019866_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N>N-96H+96R_TE_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018331_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019079_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019212_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 27/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R018928_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019212_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 27/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R019247_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018264_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018337_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018444_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018809_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019035_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019082_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019146_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019633_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>N-96H+96R_TE_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R018281_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019158_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019258_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019475_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>N-ARKS_GITN_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R019662_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_A, Effective Date: 03/05/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R019886_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>N-96H+96R_TE_1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | N::Q_NIL_KC | 0.083333 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL
N-Q-MNSP1 Import | N_MBTE1_B | 466.0833 | 130.3333 | Out= one Directlink cable, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 204.8333 | 256.0833 | Out= two Directlink cables, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N_X_MBTE_3B | 137.5 | 196.25 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Import | N>N-NIL_MBDU | 61.8333 | 0 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Import | N>N-NIL_DC | 55.5833 | 46.4167 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
N-Q-MNSP1 Import | Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 19.0833 | 4.5 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL
N-Q-MNSP1 Import | QNTE_ROC | 18.25 | 71.0833 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | N_NIL_TE_B | 15.0833 | 12.5 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 11.0833 | 47.5 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 8.4167 | 0 | Negative Residue Management constraint for QLD to NSW flow | NIL
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 8 | 27.8333 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N>>N-NIL_1G | 4.1667 | 0 | Out= Nil, avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22) line, Feedback | NIL
N-Q-MNSP1 Import | N>>N-964_DC | 3.8333 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage
N-Q-MNSP1 Import | Q^^CS_-240 | 3.5 | 0 | Nominated Offset -240MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage
N-Q-MNSP1 Import | N_MBTE110_B | 2.3333 | 0 | Qld to NSW on Directlink upper transfer limit of -110 MW | Outage
N-Q-MNSP1 Import | N>>N-SNVP_03 | 1.8333 | 0 | Out = SydneyNorth-ValesPoint(22), avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25) line, Feedback | Outage
N-Q-MNSP1 Import | N>>N-X_AVMA_KCTX_11 | 1.0833 | 0 | Out= Avon to Macarthur (17) 330kV line and Kemps Creek No.2 or No.3 500/330kV transformer , avoid O/L Vales Point to Munmorah (23) on trip of remaining Kemps Creek transformer, Feedback | Outage
N-Q-MNSP1 Import | CA_SPS_4B902E2A_01 | 0.91667 | 0 | Constraint Automation, O/L 9U7/M @MULLUMB for CTG LNYI on trip of 9G5 EWINGSDL-MULLUMB 132KV LINE. Generated by STNET[NORFR] Host NOREEMP3(SP) | Outage
N-Q-MNSP1 Import | N>N_LSDU_9U6_2 | 0.83333 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage
N-Q-MNSP1 Import | Q>N-MUTE_758 | 0.83333 | 47.8333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | N>N_LSDU_9U6_3 | 0.66667 | 0 | Out= one of Lismore 132 to Mullumbimby 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line for trip of 9G5 (Mullumbimby to Ewingsdale) 132kV line | Outage
N-Q-MNSP1 Import | #R018549_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019146_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019258_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018337_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018439_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018549_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018809_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019158_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019496_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019603_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018281_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018444_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018618_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_MBTE1_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019487_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019591_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018264_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018331_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018331_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019481_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | N>N-BAMB_132_OPEN_B | 0.25 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage
N-Q-MNSP1 Import | #R018281_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018439_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018928_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019158_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019469_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019603_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | N::V_WA_BUSA_MSDD | 0.16667 | 0 | Out= Wagga 330kV A Bus, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
N-Q-MNSP1 Import | N>>N-NIL_64 | 0.16667 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
N-Q-MNSP1 Import | #R018337_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R019787_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_BCDM_A, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Export | Q>>WOPW_WOSP_WOGP_2 | 190.4167 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 100.8333 | 82 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
NSW1-QLD1 Export | Q>>CPPW_WOSP_WOGP_2 | 26.5 | 0 | Out= Calliope River to Palmwoods (813+815+810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_NIL_A | 24.4167 | 7 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
NSW1-QLD1 Export | Q>>BCCP_CLWU_RGLC_2 | 2.8333 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | Q>>WOSP_WOPW_WOGP_2 | 2.75 | 0 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage
NSW1-QLD1 Export | Q>>CLWU_BCRG_BCCP | 2.5833 | 0 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811), Feedback | Outage
NSW1-QLD1 Export | F_Q++BCDM_R60 | 2.0833 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | Q^^TR_CLHA_-250 | 2.0833 | 0 | Nominated offset -250 MW, Tarong voltage stability limit, Calvale-Halys contingency equation | Outage
NSW1-QLD1 Export | Q>>BCCP_CLWU_LCCP_2 | 1.9167 | 2.25 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | F_Q++BCDM_R6 | 1.5 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N>>N-NIL__3_OPENED | 1.4167 | 15.75 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL
NSW1-QLD1 Export | #R019876_002_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint Q>>WOPW_WOSP_WOGP_2, Effective Date: 29/05/2019, Version: 1 | Other
NSW1-QLD1 Export | #R019636_002_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint Q>>WOSP_WOPW_WOGP_2, Effective Date: 12/09/2019, Version: 1 | Other
NSW1-QLD1 Export | Q>>CPSP_WOPW_WOGP_2 | 0.5 | 0 | Out= Calliope River to South Pine (813+815+807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage
NSW1-QLD1 Export | Q>>LCCP_CLWU_BCCP_2 | 0.5 | 1.8333 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | #R019636_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q>>WOSP_WOPW_WOGP_2, Effective Date: 12/09/2019, Version: 1 | Other
NSW1-QLD1 Export | #R019655_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q>>CPSP_WOPW_WOGP_1, Effective Date: 16/09/2019, Version: 1 | Other
NSW1-QLD1 Export | Q>>PWSP_WOSP_PWCE | 0.33333 | 0.25 | Out= Palmwoods to South Pine (808) line, avoid O/L Palmwood to Caboolture (746/4) 110kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | Q>>WOPW_WOSP_WOGP_1 | 0.33333 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | #R019876_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q>>WOPW_WOSP_WOGP_2, Effective Date: 29/05/2019, Version: 1 | Other
NSW1-QLD1 Export | Q>>CPSP_WOSP_PWCE | 0.25 | 0 | Out= 808(Palmwoods to South Pine)+ 813 +815 (Calliope River to Woolooga) 275kV lines with 132kV/110kV network between Woolooga to Palmwoods network closed, avoid O/L Palmwood to Caboolture(746/4) on trip of Woolooga to South Pine (807)line, Feedback | Outage
NSW1-QLD1 Export | #R019655_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q>>CPSP_WOPW_WOGP_1, Effective Date: 16/09/2019, Version: 1 | Other
NSW1-QLD1 Export | N::Q_NIL_KC | 0.083333 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL
NSW1-QLD1 Import | Q^^NIL_QNI_SRAR | 770.75 | 0 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL
NSW1-QLD1 Import | Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 226.3333 | 142.25 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL
NSW1-QLD1 Import | F_Q++BCDM_L6 | 107.8333 | 46.25 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | N>N-NIL_DC | 63.1667 | 78.4167 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
NSW1-QLD1 Import | I_QNI_ONE_PHASE_N-2 | 34 | 1.4167 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage
NSW1-QLD1 Import | F_Q++BCDM_L5 | 32.25 | 36.6667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q:N_1078 | 25.6667 | 17.4167 | QNI oscillatory stability limit of 1078 MW | Outage
NSW1-QLD1 Import | F_Q++ARTW_L6 | 11.8333 | 52.5833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 9.25 | 0 | Negative Residue Management constraint for QLD to NSW flow | NIL
NSW1-QLD1 Import | F_Q++ARTW_L5 | 8.25 | 31 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q::N_ARSVC_AR_2L-G | 5.6667 | 14.5833 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | N>>N-NIL_1G | 4.1667 | 0 | Out= Nil, avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22) line, Feedback | NIL
NSW1-QLD1 Import | Q^^CS_-240 | 4 | 0 | Nominated Offset -240MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage
NSW1-QLD1 Import | QNI_SOUTH_1150_DYN | 3.6667 | 0 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL
NSW1-QLD1 Import | N>>N-964_DC | 3.1667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage
NSW1-QLD1 Import | F_Q++8C_L6 | 2.3333 | 17.75 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 2.1667 | 4.1667 | NSW1-QLD1 >= MIN(-421, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Import | F_Q++NIL_R5 | 1.8333 | 0.25 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | N>>N-SNVP_03 | 1.8333 | 0 | Out = SydneyNorth-ValesPoint(22), avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25) line, Feedback | Outage
NSW1-QLD1 Import | Q::N_DM_CB_AR_2L-G | 1.6667 | 0 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | Q^^N_AR_SVC_1 | 1.5833 | 0 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage
NSW1-QLD1 Import | F_Q++8C_L5 | 1.25 | 9.25 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | N>>N-X_AVMA_KCTX_11 | 1.0833 | 0 | Out= Avon to Macarthur (17) 330kV line and Kemps Creek No.2 or No.3 500/330kV transformer , avoid O/L Vales Point to Munmorah (23) on trip of remaining Kemps Creek transformer, Feedback | Outage
NSW1-QLD1 Import | QN_1000 | 1 | 0 | Qld to NSW on QNI upper transfer limit of 1000 MW | Outage
NSW1-QLD1 Import | QN_950 | 1 | 0 | Qld to NSW on QNI upper transfer limit of 950 MW | Outage
NSW1-QLD1 Import | #R018464_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q::N_DM_CB_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | N::V_WA_BUSA_MSDD | 0.16667 | 0 | Out= Wagga 330kV A Bus, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
NSW1-QLD1 Import | N>>N-NIL_64 | 0.16667 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
NSW1-QLD1 Import | #R018464_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q::N_DM_CB_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R018995_017_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q^^N_AR_SVC_1, Effective Date: 16/05/2019, Version: 1 | Other
NSW1-QLD1 Import | #R019720_013_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_ARSVC_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R019787_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_BCDM_A, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R019792_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q^^N_BCDM_1, Effective Date: 16/05/2019, Version: 1 | Other
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 1021.25 | 998.1667 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 526.8333 | 496.3333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 468.25 | 552 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 67.25 | 133.3333 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 53 | 225.1667 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 45.9167 | 187.8333 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
T-V-MNSP1 Export | F_T++NIL_BLSPS_L6_1 | 24.75 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
T-V-MNSP1 Export | F_T++NIL_BLSPS_L60_1 | 20.5833 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
T-V-MNSP1 Export | TV_150 | 19.9167 | 0 | Tas to Vic on Basslink upper limit of 150 MW | Outage
T-V-MNSP1 Export | T^V_NIL_9 | 18.5833 | 54.0833 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | F_T++LREG_0050 | 17.9167 | 85.9167 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++RREG_0220 | 11.6667 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | Other
T-V-MNSP1 Export | TVBL_ROC | 9.3333 | 7.1667 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Export | F_T++NIL_BLSPS_L5 | 7.1667 | 0 | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
T-V-MNSP1 Export | F_MAIN++RREG_0220 | 6.5 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | T_V_NIL_BL1 | 5.5 | 4.3333 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL
T-V-MNSP1 Export | T^V_NIL_8 | 4.3333 | 30.4167 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 4.3333 | 1.3333 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A3_2A_R | 4.25 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | T^V_NIL_11 | 3.5833 | 47.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL
T-V-MNSP1 Export | T_V_NIL_FCSPS | 3.5833 | 2.6667 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL
T-V-MNSP1 Export | F_VS++65_66_RAD_R60 | 3.1667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T^^V_GTSH_1 | 2.75 | 7.1667 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage
T-V-MNSP1 Export | F_QNV++MG_R60 | 2.5 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++RREG_0180 | 2.0833 | 0 | Mainland Raise Regulation Requirement greater than 180 MW, Basslink able transfer FCAS | Other
T-V-MNSP1 Export | F_T++COGT_TL_L6 | 2 | 2.6667 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_MAIN++RREG_0200 | 1.8333 | 0 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | Other
T-V-MNSP1 Export | F_MAIN++NIL_RREG | 1.6667 | 6.0833 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_VS++65_66_RAD_R5 | 1.0833 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_QNV++MG_R5 | 0.83333 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L60 | 0.5 | 2.25 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_T++NIL_BLSPS_L60_2 | 0.33333 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
T-V-MNSP1 Export | F_T++NIL_BLSPS_L6_2 | 0.33333 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
T-V-MNSP1 Export | F_QNV++MG_R6 | 0.25 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L5 | 0.16667 | 2.9167 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | T^V_NIL_BL_6 | 0.083333 | 0 | Outage = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL
T-V-MNSP1 Export | V>>V_KTS_TX_A3_3A_R | 0.083333 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr for trip of ROTS A1 500/220 kV txfmr, radial mode, Yallourn W unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 919.0833 | 758.9167 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V_T_NIL_FCSPS | 819.5 | 98.1667 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 378.1667 | 292.75 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 241.0833 | 111.5 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R5 | 63.1667 | 17.4167 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R6 | 50 | 45.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_HWSM_V2 | 48.1667 | 2.25 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V_T_NIL_BL1 | 45.9167 | 19.9167 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL
T-V-MNSP1 Import | T::T_NIL_2 | 45.1667 | 0 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL
T-V-MNSP1 Import | VT_000 | 44.3333 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 33.6667 | 18.25 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++RREG_0050 | 31.75 | 55.4167 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | VT_ZERO | 27.9167 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R60 | 27.4167 | 64.1667 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | T::T_NIL_4 | 26.8333 | 11.5 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0210 | 23 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0170 | 21.0833 | 0 | Mainland Lower Regulation Requirement greater than 170 MW, Basslink able transfer FCAS | Other
T-V-MNSP1 Import | V::N_HWSM_V1 | 17.0833 | 4.75 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_MAIN++LREG_0120 | 16 | 49.4167 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | T::T_NIL_3 | 15.9167 | 2 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 15.4167 | 32.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_SMSC_V2 | 14.25 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 14.1667 | 4.75 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 12.4167 | 20.6667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0210 | 11.5 | 0 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Other
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 11 | 0.083333 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | VTBL_ROC | 9.5 | 5.8333 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Import | V::N_KGRC_V2 | 9.1667 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 8.9167 | 0.16667 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0190 | 7.0833 | 0 | Mainland Lower Regulation Requirement greater than 190 MW, Basslink able transfer FCAS | Other
T-V-MNSP1 Import | V::N_DDSM_V2 | 6.5833 | 1 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_NILxxx | 6.5833 | 216.0833 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
T-V-MNSP1 Import | F_MAIN++ML_L5_APD | 5.9167 | 0.83333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | T::T_HA_GT_PM_4 | 5.3333 | 9.1667 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 4.9167 | 14.75 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 4.8333 | 19.6667 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V:T_NIL_BL_1 | 4.6667 | 1 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 4.5 | 8.75 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_SMSC_S2 | 4.3333 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | T_ROCOF_1 | 3.8333 | 17.6667 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL
T-V-MNSP1 Import | VT_050 | 3.5 | 0 | Vic to Tas on Basslink upper limit of 50 MW | Outage
T-V-MNSP1 Import | V::N_X_DDSM_SMSC_V2 | 3.3333 | 0 | Out = one Dederang to South Morang 330kV line AND series capbank on the parallel line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_QNV++MLTR_L60 | 2.4167 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T::T_GTSH_2 | 2.4167 | 0 | Out = George Town to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage
T-V-MNSP1 Import | V::N_ESTN_HYSE_VA | 2.25 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | V::N_HORC_V2 | 2 | 4.75 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_KTSY_V2 | 1.8333 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_BLSPS_R6_2 | 1.6667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
T-V-MNSP1 Import | F_T++NIL_BLSPS_R60_2 | 1.5 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S1 | 1.1667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | F_MAIN++ML_L5_0500 | 1.0833 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_SMF2_V2 | 1.0833 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++WIP_N-2_MLL6 | 1 | 0.25 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 0.91667 | 0.83333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L60_APD | 0.91667 | 0.16667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HWSM_S1 | 0.91667 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
T-V-MNSP1 Import | V:T_SHGT_BL_1 | 0.91667 | 0 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R5 | 0.83333 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | T>>T_GTSH_EXP_3H | 0.83333 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_0500 | 0.66667 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V:T_HAGT_BL_1 | 0.66667 | 0 | Out = Hadspen to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to George Town 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R5 | 0.58333 | 1.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R6 | 0.58333 | 0.66667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 0.58333 | 1.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_5F | 0.58333 | 0.33333 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | #R018320_006_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 0.5 | 0.083333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | #R018315_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
T-V-MNSP1 Import | #R018395_006_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HORC_V1, Effective Date: 20/02/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018441_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 20/02/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018911_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 01/05/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018992_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 04/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019408_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | V::N_MLMO_V2 | 0.41667 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R018942_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019408_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019442_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R020010_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 0.33333 | 0.33333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S3 | 0.33333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | #R018320_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
T-V-MNSP1 Import | #R018395_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 20/02/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018987_006_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018992_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 04/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019038_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019236_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019236_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019685_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTR_V1, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++HYTR_L60 | 0.25 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_6E | 0.25 | 0 | Out = Nil, avoid O/L a Sheffield to Georgetown 220 kV line (flow to Georgetown) for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | T_ROCOF_3 | 0.25 | 0 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL
T-V-MNSP1 Import | #R018294_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V2, Effective Date: 21/11/2018, Version: 1 | Other
T-V-MNSP1 Import | #R018315_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
T-V-MNSP1 Import | #R018318_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
T-V-MNSP1 Import | #R018466_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint T::T_GTSH_2, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R018942_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018987_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019095_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWG_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019095_018_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWG_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019103_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_DDSM_SMSC_V2, Effective Date: 28/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R020035_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ML_L60_0500 | 0.16667 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD_LD | 0.16667 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++MLTR_L5 | 0.16667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R5 | 0.16667 | 0.41667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R60 | 0.16667 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | V::N_HORC_S2 | 0.16667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R018466_052_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V:T_SHGT_BL_1, Effective Date: 20/10/2014, Version: 1 | Other
T-V-MNSP1 Import | #R018911_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 01/05/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018934_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018942_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 01/05/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018942_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 01/05/2019, Version: 1 | Other
T-V-MNSP1 Import | #R018993_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 04/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019095_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_JNWG_S2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019095_015_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWG_S2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019188_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019188_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019188_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019236_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019236_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019442_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R019903_015_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 26/06/2019, Version: 1 | Other
T-V-MNSP1 Import | #R020037_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint T::T_GTSH_2, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R020076_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S1, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++WIPN-2_MLL60 | 0.083333 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 60 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++HYTR_L5 | 0.083333 | 0.083333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S2 | 0.083333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 500kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | V::N_SMSY_SD | 0.083333 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_X_HWSM_12_V1 | 0.083333 | 0 | Out= Hazelwood - South Morang No.1 and No.2 500kV lines, prevent transient instability for loss of ROTS-SMTS 500kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_X_HWSM_ROSM_V1 | 0.083333 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WEWT | 172.5833 | 22.3333 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V^^N_NIL_1 | 160.75 | 71.9167 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
V-S-MNSP1 Export | V^SML_HORC_3 | 78 | 17 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V>>N-NIL_HA | 69.3333 | 19.5833 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
V-S-MNSP1 Export | V^^SML_NSWRB_2 | 58.9167 | 0 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL
V-S-MNSP1 Export | V::N_HWSM_V2 | 55.0833 | 2.5833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 47.5 | 169.9167 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-S-MNSP1 Export | S>>PARB_RBTU_WTTP | 43.75 | 6 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V^SML_BUDP_3 | 42.5833 | 5.5 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | VSML_ZERO | 33.1667 | 488.3333 | Vic to SA on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | VSML_ROC_80 | 31.5 | 43.0833 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Export | V::N_HWSM_V1 | 28.3333 | 5 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V^SML_BAWB_3 | 26.75 | 0 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | S>>PATW_BWPA_TPRS | 19.75 | 35.3333 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_SMSC_V2 | 16.5833 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_NILxxx | 16.25 | 216.25 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-S-MNSP1 Export | V>>N-NIL_HG | 15.1667 | 6.9167 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | S>>X_DVBR_BRTW_05 | 14.75 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX), avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_5 | 13 | 1.75 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Export | V::N_KGRC_V2 | 11.9167 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V^SML_ARWB_3 | 10.5 | 0 | Out = Ararat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V^SML_HORC_2 | 9.3333 | 0.25 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 9.0833 | 0.58333 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | S>>X_RBTU+CB_2 | 8.3333 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) | Outage
V-S-MNSP1 Export | S>>X_RBPA+BGTX_04 | 8.0833 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | N>>N_65+66_N-2_2 | 7.4167 | 0 | Out= Nil, avoid O/L Dederang to Wodonga on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL
V-S-MNSP1 Export | V::N_DDSM_V2 | 7.1667 | 1.3333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>V_NIL_8 | 7.1667 | 12 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL
V-S-MNSP1 Export | S>>PARB_RBTU_RBMWP4 | 6.8333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HORC_V2 | 6.6667 | 5.6667 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V^SML_NSWRB_2 | 6.5833 | 58.5 | Out = NSW Murraylink runback scheme, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | NIL
V-S-MNSP1 Export | V>SMLARHO1 | 5.4167 | 49 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V^SML_KGRC_4 | 4.9167 | 1.5 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage
V-S-MNSP1 Export | V::N_SMSC_S2 | 4.75 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>SMLMHNW1 | 4.5833 | 0 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 4.1667 | 1.75 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-S-MNSP1 Export | V::N_X_DDSM_SMSC_V2 | 3.9167 | 0 | Out = one Dederang to South Morang 330kV line AND series capbank on the parallel line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_SMF2_V2 | 3.8333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | VSML_220 | 3.5833 | 25 | Vic to SA on ML upper transfer limit of 220 MW | NIL
V-S-MNSP1 Export | S>>X_RBPA+BGTX_05 | 2.9167 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>SMLARHO4 | 2.75 | 0.083333 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WEWT | 2.6667 | 0.16667 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_KTSY_V2 | 2.6667 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | CA_MQS_4C1211CB_02 | 2.1667 | 0 | Constraint Automation, O/L WATTEM_1 @W_LOO for CTG LSIT on trip of R_TOWN - PARA 275KV LINE. Generated by STNET[MANFL] Host MANEEMP1(MQ) | Outage
V-S-MNSP1 Export | S>>RBTU_RBPA_WEWT | 2 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>N-MSUT_4 | 2 | 0 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
V-S-MNSP1 Export | V>>V_LTMS_1 | 1.8333 | 0 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage
V-S-MNSP1 Export | VSML_-050 | 1.4167 | 0 | Vic to SA on ML upper transfer limit of -50 MW | Outage
V-S-MNSP1 Export | S>>X_DVLK+LKCN_02 | 1.3333 | 0 | Out= Davenport-Mt Lock-Canowie 275kV line (this offloads Hornsdale #1 & #2 &#3 WF & battery) OR Davenport-Mt Lock 275kV line O/S, avoid O/L Waterloo East-Waterloo 132kV line on trip of Belalie-Davenport 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>V-MSUT_1 | 1.25 | 1.9167 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback | Outage
V-S-MNSP1 Export | V>>DDSH_DDGN_N-2 | 1.1667 | 1.0833 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
V-S-MNSP1 Export | V>>SML_NSWRB_11 | 1.1667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Wemen to Red Cliffs 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL
V-S-MNSP1 Export | S>>RBTU_TWPA_TPRS | 1 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_S1 | 1 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-S-MNSP1 Export | S>>NIL_BWMP_TWPA | 0.83333 | 0 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_HWSM_S1 | 0.83333 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-S-MNSP1 Export | #R018320_006_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-S-MNSP1 Export | V^SML_NIL_3 | 0.75 | 0.083333 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL
V-S-MNSP1 Export | #R019093_014_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S>>X_DVLK+LKCN_15, Effective Date: 14/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020226_013_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | V>SMLMHNW2 | 0.66667 | 0 | Out = Monash-North West Bend # 2 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 1 132kV line | Outage
V-S-MNSP1 Export | #R018441_007_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 20/02/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018566_018_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | V>>BABE_DDGN_N-2 | 0.58333 | 0.16667 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage
V-S-MNSP1 Export | #R018315_006_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-S-MNSP1 Export | #R019059_009_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R020181_013_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S>>RBTU_RBPA_WEWT, Effective Date: 21/10/2019, Version: 1 | Other
V-S-MNSP1 Export | N>>N_65+66_N-2_5 | 0.5 | 0 | Out= Nil, avoid O/L Wodonga to Jindera (060) on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL
V-S-MNSP1 Export | V:SS_820_HY_TEST_DYN | 0.5 | 0.083333 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-S-MNSP1 Export | V^^SML_NIL_3 | 0.5 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL
V-S-MNSP1 Export | #R018249_026_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 01/06/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018315_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-S-MNSP1 Export | #R018395_006_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HORC_V1, Effective Date: 20/02/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018441_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 20/02/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018552_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R018559_018_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018566_018_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018911_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 01/05/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018971_009_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018992_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 04/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019336_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R019354_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R019408_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019908_019_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R019918_019_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R020116_012_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V^SML_HORC_2, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020121_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_2, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020226_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | S>>BWMP_TWPA_TPRS | 0.41667 | 0.083333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_S3 | 0.41667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-S-MNSP1 Export | V::N_MLMO_V2 | 0.41667 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>RBTU_BWMP_TWPA | 0.41667 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | #R018436_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 07/01/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018571_018_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018942_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018987_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019059_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R019408_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019442_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019535_018_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R020116_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_2, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020157_018_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | V::N_HORC_V1 | 0.33333 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | #R018318_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-S-MNSP1 Export | #R018320_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-S-MNSP1 Export | #R018395_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 20/02/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018436_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 07/01/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018489_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 07/01/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018571_018_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018573_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 07/01/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018992_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 04/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019038_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019236_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019339_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R019685_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTR_V1, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020121_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_HORC_2, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020157_018_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R020181_013_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S>>RBTU_RBPA_WEWT, Effective Date: 21/10/2019, Version: 1 | Other
V-S-MNSP1 Export | S>>DVBL_LKDV_WEWT | 0.25 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East- Waterloo 132kV on trip of Mt Lock-Davenport 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HORC_S2 | 0.25 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | #R018249_026_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 01/06/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018254_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_2, Effective Date: 07/01/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018294_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-S-MNSP1 Export | #R018387_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_HORC_2, Effective Date: 07/01/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018489_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 07/01/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018559_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018805_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R018942_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018971_009_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018987_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019095_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWG_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019095_018_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWG_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019103_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_DDSM_SMSC_V2, Effective Date: 28/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019143_009_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R019236_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019236_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019236_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R019535_018_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R019540_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R019897_019_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R019903_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019918_019_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R020035_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #V-S-MNSP1_E_E | 0.16667 | 0.16667 | V-S-MNSP1.ENERGY * 1 <= 60 (Wt = 360) | Other
V-S-MNSP1 Export | S>>BRTW_BWPA_WTTP | 0.16667 | 0.083333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_BLDV+WEMWP4_05 | 0.16667 | 0 | Out= Out= Belalie-Davenport 275kV line + Waterloo East-MWP4-Robertstown 132kV line), avoid O/L Templers-Roseworthy 132k on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBPA+BGTX_02 | 0.16667 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S, avoid O/L Robertstown-MWP4-Waterloo East 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+CB_1 | 0.16667 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) lines, Feedback | Outage
V-S-MNSP1 Export | #R018208_029_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 01/06/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018911_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 01/05/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018934_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018942_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 01/05/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018942_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 01/05/2019, Version: 1 | Other
V-S-MNSP1 Export | #R018993_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 04/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019067_027_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 01/06/2017, Version: 1 | Other
V-S-MNSP1 Export | #R019093_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>X_DVLK+LKCN_15, Effective Date: 14/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019095_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_JNWG_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019095_015_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWG_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019188_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019188_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019188_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019236_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019442_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-S-MNSP1 Export | #R019630_030_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 03/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020076_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S1, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | NRM_VIC1_SA1 | 0.083333 | 0.083333 | Negative Residue Management constraint for VIC to SA flow | NIL
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_S2 | 0.083333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 500kV. Only applied during Heywood SA->VIC | Outage
V-S-MNSP1 Export | V::N_WBHO_V2 | 0.083333 | 10.5 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_12_V1 | 0.083333 | 0 | Out= Hazelwood - South Morang No.1 and No.2 500kV lines, prevent transient instability for loss of ROTS-SMTS 500kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_ROSM_V1 | 0.083333 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>V_KGWT_2 | 0.083333 | 0 | Out = Kerang to Wemen 220kV line, avoid overloading Bulgana to Horsham 220kV line section for loss of Balranald to Buronga (X3) 220kV line | Outage
V-S-MNSP1 Export | V>SML_NSWRB_10 | 0.083333 | 2.3333 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL
V-S-MNSP1 Import | SVML_ZERO | 619.4167 | 287.25 | SA to Vic on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Import | S>V_NIL_NIL_RBNW | 403.8333 | 338.75 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | S>VMLMHNW1 | 104.3333 | 0.083333 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-S-MNSP1 Import | S>NIL_NIL_NWMH2 | 77.3333 | 14.6667 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>VMLMHNW2 | 29.5 | 0 | Out=Monash-North West Bend #2 132kV line, SA-V on ML avoid overload on North West Bend-Monash #1 132kV line, feedback | Outage
V-S-MNSP1 Import | SVML_ROC_80 | 27 | 49.9167 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Import | S>RB_275KV_N_BUS_1 | 18.25 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage
V-S-MNSP1 Import | S>NWCB6024+25_TX3 | 14.3333 | 0 | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage
V-S-MNSP1 Import | S>RB_275KV_S_BUS_9 | 14.3333 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage
V-S-MNSP1 Import | S:VS_650_HY_TEST | 13.9167 | 3.9167 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-S-MNSP1 Import | S:VS_650_HY_TEST_DYN | 12.3333 | 5.5 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-S-MNSP1 Import | S>>MKRB_CNRB_WEMWP4 | 10.0833 | 14.1667 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage
V-S-MNSP1 Import | S>V_NWRB2_RBNW1 | 9.9167 | 0 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage
V-S-MNSP1 Import | S>V_NWRB_RBMWP3 | 9.3333 | 0 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage
V-S-MNSP1 Import | SVML_FLT_150 | 8 | 0 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage
V-S-MNSP1 Import | V>>V_NIL_3 | 7.25 | 0.5 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Import | V>>V_BUDP_6 | 5.5 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | V>>V_KGWT_3 | 5 | 0 | Out= Kerang to Wemen 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Balranald to Darlington Point (X5) 220kV line, Feedback | Outage
V-S-MNSP1 Import | S>>CNLK_MKRB_WEMWP4 | 4.75 | 0 | Out= Canowie-Mt Lock 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV on trip of Mokota-Robertstown 275kV line( this offloads Belalie-Mokota 275kV line and trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | S>>X_MKRB+WTTP_14 | 4.25 | 0 | Mokota - Robertstown 275kV line(i.e. Line ONLY O/S, line CBs I/S) + Waterloo-Templers 132kV line O/S, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kVline (this trips Hallet GT + WF), Feedback | Outage
V-S-MNSP1 Import | S>NWBCB6025_TX2 | 4 | 0 | Out= North West Bend 132kV CB6025 , avoid O/L of North West Bend 132/66kV TX2 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage
V-S-MNSP1 Import | S:V_580 | 2.1667 | 0 | Out = One Heywood 500/275 kV txfmr (two remain in service), maintain maximum SA to VIC transfer limit of 580 MW on Heywood and Murraylink combined to avoid oscillatory instability | Outage
V-S-MNSP1 Import | S>>X_MKRB+WTTP_06 | 2 | 0 | Out= Mokota-Robertstown 275kV line (note:associated line CBs assumed I/S) + Waterloo-Templers 132kV line, avoid O/L Waterloo East-MWp4-Robertstown 132kV line on trip Nil trip, Feedback | Outage
V-S-MNSP1 Import | CA_MQS_4C6B1A92_01 | 1.9167 | 0 | Constraint Automation, O/L N_W_B TRANSF T_1 for CTG LS5K on trip of R_TOWN-N_W_B132KV 2LN VIA1 2&3MWPS. Generated by STNET[MANFL] Host MANEEMP2(MQ) | Outage
V-S-MNSP1 Import | N>>V-NIL_HJ | 1.75 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Import | S>>MKRB_NIL_WEMWP4 | 1.5833 | 1 | Out= Mokota-Robertstown 275kV line,, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>>PATW_NIL_WEMWP4 | 1.5 | 0.91667 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>NWBCB6225_TX1 | 1.5 | 0 | Out= North West Bend 132kV CB6225, avoid O/L of North West Bend 66/132kV TX1 on trip of North West Bend-Monash #2 132kV line, Feedback | Outage
V-S-MNSP1 Import | CA_MQS_4C1211CB_01 | 1.3333 | 0 | Constraint Automation, O/L R_TOWN TRANSF T_1 for CTG LSIT on trip of R_TOWN - PARA 275KV LINE. Generated by STNET[MANFL] Host MANEEMP1(MQ) | Outage
V-S-MNSP1 Import | #R019791_001_RAMP_F | 1 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R018805_001_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019897_011_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R018552_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019245_012_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S>>X_MKRB+WTTP_14, Effective Date: 18/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R019336_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019354_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019755_018_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S>>X_RBTU+CB_7, Effective Date: 02/10/2019, Version: 1 | Other
V-S-MNSP1 Import | #R019779_018_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S>>X_RBTU+CB_7, Effective Date: 02/10/2019, Version: 1 | Other
V-S-MNSP1 Import | #R019783_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019903_011_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019908_011_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | S>>X_RBTU+CB_7 | 0.58333 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, avoid O/L Robertstown 275/132kV #1 transformer on trip of Robertstown - Para line (this offloads Robertstown TX#2 132/275kV ) | Outage
V-S-MNSP1 Import | S>>X_RBTU_CB_3 | 0.58333 | 0 | Out= Robertstown-Tungkillo 275kV line& RB 275kV CBs 6571 & 6572 O/S, avoid O/L Waterloo East-MWP4-RB 132kV line on trip of Mokota-Robertstown 275kV line(trips Willalo-Mokota 275kV line and Hallet Hill WF. The contingency SPLITS Robertstown bus) | Outage
V-S-MNSP1 Import | V>>V_NIL_9 | 0.58333 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | #R019013_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019918_011_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | N>>N-NIL_DPTX_2 | 0.5 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
V-S-MNSP1 Import | S>>X_DVBR+BRTW_15 | 0.5 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX), avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | Outage
V-S-MNSP1 Import | #R019608_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>VMLMHNW2, Effective Date: 14/04/2015, Version: 1 | Other
V-S-MNSP1 Import | #R019755_018_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>>X_RBTU+CB_7, Effective Date: 02/10/2019, Version: 1 | Other
V-S-MNSP1 Import | #R019783_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019903_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R019957_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S>VMLMHNW1, Effective Date: 17/05/2019, Version: 1 | Other
V-S-MNSP1 Import | CA_MQS_4C47A69C_01 | 0.41667 | 0 | Constraint Automation, O/L BATS_WBTS_220 @WBTS for CTG LNAB on trip of DARL-BAL-BURONGA X5/1&/3 220KV LNS. Generated by STNET[NORFL] Host MANEEMP2(MQ) | Outage
V-S-MNSP1 Import | SVML_FLT_070 | 0.41667 | 0 | SA to Vic on ML upper transfer limit of 70 MW to manage system stability on the next contingency due to fault level issue | Outage
V-S-MNSP1 Import | #R019245_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>X_MKRB+WTTP_14, Effective Date: 18/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R019779_018_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>X_RBTU+CB_7, Effective Date: 02/10/2019, Version: 1 | Other
V-S-MNSP1 Import | V>>SML_NIL_6 | 0.33333 | 0 | Out= Nil, Avoid pre-contingent overload of Waubra to Ballarat 220kV line, Feedback | NIL
V-S-MNSP1 Import | #R019412_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S>NWBCB6225_TX1, Effective Date: 02/08/2017, Version: 1 | Other
V-S-MNSP1 Import | S>>PATW_BWPA_WEMWP4 | 0.25 | 0 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Import | #R019013_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | SVML_120 | 0.16667 | 0 | SA to Vic on ML upper transfer limit of 120 MW | Outage
V-S-MNSP1 Import | #R019412_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>NWBCB6225_TX1, Effective Date: 02/08/2017, Version: 1 | Other
V-S-MNSP1 Import | #R019608_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>VMLMHNW2, Effective Date: 14/04/2015, Version: 1 | Other
V-S-MNSP1 Import | CA_BRIS_4D0EE093_1 | 0.083333 | 0 | Constraint Automation, O/L EPS_MBTS2_220:LEP2:Z:220@MBTS@VIC for CTG LVCY on trip of EPS-MBTS1 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage
V-S-MNSP1 Import | NRM_SA1_VIC1 | 0.083333 | 4.5 | Negative Residue Management constraint for SA to VIC flow | NIL
V-S-MNSP1 Import | V>>V_KTS_TX_A3_3A_R | 0.083333 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr for trip of ROTS A1 500/220 kV txfmr, radial mode, Yallourn W unit 1 on 500 kV network, feedback | Outage
V-SA Export | V::N_HWSM_V2 | 67.4167 | 2.5833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V_VS_LB_CAN_50 | 43 | 0 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage
V-SA Export | V::N_HWSM_V1 | 34.8333 | 4.9167 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V:S_600_HY_TEST | 20.0833 | 27.0833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL
V-SA Export | V_MLMO_VS_LB_CAN_50 | 17.9167 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS/DUNDWF generating. | Outage
V-SA Export | V::N_NILxxx | 17 | 247.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-SA Export | V::N_SMSC_V2 | 16.5833 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_ESTN++MLTR_L60 | 15.6667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_ESTN++MLMO_L60 | 13.5833 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::N_KGRC_V2 | 12 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V:S_600_HY_TEST_DYN | 11.4167 | 31.25 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-SA Export | V::N_HORC_V2 | 7.25 | 5.6667 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_SMSC_S2 | 4.75 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_ESTN++HYTR_L60 | 4.5833 | 1.1667 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_QNV+MLMO_L60 | 4.5 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::S_NIL_MAXG_xxx | 4.4167 | 13.9167 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | S>>NIL_TBTU_TBMO_1 | 3.8333 | 0 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL
V-SA Export | V::N_SMF2_V2 | 3.8333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V^^S_NIL_MAXG_xxx | 3.6667 | 9.4167 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V::N_KTSY_V2 | 2.75 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_QNV+HYMO_L60 | 2.4167 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | SA_HYSE1 | 2.1667 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage
V-SA Export | F_QNV++MLTR_L60 | 1.9167 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V_VS_MLMO_NETT | 1.9167 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage
V-SA Export | V::N_BYPASS_HW_SY_S1 | 1.3333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V::S_PATU_MAXG_2 | 1.1667 | 0 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V>>DDSH_DDGN_N-2 | 1.1667 | 1.0833 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
V-SA Export | V::N_ESTN_HYSE_VA | 1 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | V::S_PATU_MAXG | 1 | 0 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V::N_EPMB_V2 | 0.91667 | 2.9167 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_QNV+MLTR_L60 | 0.83333 | 0.16667 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | #R018320_006_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-SA Export | V::N_HWSM_S1 | 0.75 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-SA Export | #R019697_010_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R018441_007_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 20/02/2019, Version: 1 | Other
V-SA Export | #R020054_015_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R018315_006_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-SA Export | #R019607_015_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R018315_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-SA Export | #R018395_006_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HORC_V1, Effective Date: 20/02/2019, Version: 1 | Other
V-SA Export | #R018434_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R018441_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 20/02/2019, Version: 1 | Other
V-SA Export | #R018911_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 01/05/2019, Version: 1 | Other
V-SA Export | #R019408_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R020054_015_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R020055_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V_MLMO_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | F_ESTN++HYTR_L5 | 0.41667 | 0.58333 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | F_ESTN++MLTR_L5 | 0.41667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | V::N_BYPASS_HW_SY_S3 | 0.41667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V^^S_TBTX+CB_SETB_2 | 0.41667 | 1.3333 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage
V-SA Export | V::N_HORC_V1 | 0.41667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | #R018942_006_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 01/05/2019, Version: 1 | Other
V-SA Export | #R018987_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
V-SA Export | #R018992_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 04/06/2019, Version: 1 | Other
V-SA Export | #R019259_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R019408_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019442_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019697_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R020055_008_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V_MLMO_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | V::N_MLMO_V2 | 0.33333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_NIL_TBSE_1 | 0.33333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Export | #R018318_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-SA Export | #R018320_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-SA Export | #R018395_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 20/02/2019, Version: 1 | Other
V-SA Export | #R018801_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R018992_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 04/06/2019, Version: 1 | Other
V-SA Export | #R019038_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
V-SA Export | #R019095_018_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_JNWG_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019236_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019236_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019615_015_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R019685_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTR_V1, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #V-SA_RAMP_I_F | 0.25 | 0 | V-SA >= MIN(-126, InitialFlow + 50) (Wt=35) | Other
V-SA Export | V::N_HORC_S2 | 0.25 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_BLKRG_MAXG_2 | 0.25 | 15.8333 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | VS_050 | 0.25 | 7.1667 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage
V-SA Export | #R018294_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V2, Effective Date: 21/11/2018, Version: 1 | Other
V-SA Export | #R018942_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
V-SA Export | #R018987_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
V-SA Export | #R019095_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWG_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019149_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R019615_015_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R019737_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R019903_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019932_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R020035_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | S>>NIL_TBCG_TBTU_1 | 0.16667 | 0 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL
V-SA Export | S>>TBTU_TBCG_TBMO | 0.16667 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | #R018911_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 01/05/2019, Version: 1 | Other
V-SA Export | #R018934_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
V-SA Export | #R018942_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
V-SA Export | #R018942_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 01/05/2019, Version: 1 | Other
V-SA Export | #R018992_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
V-SA Export | #R018993_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 04/06/2019, Version: 1 | Other
V-SA Export | #R019095_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_JNWG_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019188_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019188_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019188_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019236_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019236_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019292_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R019419_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_PATU_MAXG_2, Effective Date: 05/08/2019, Version: 1 | Other
V-SA Export | #R019442_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R019442_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_VS_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Export | #R019622_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R019729_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R019737_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R019903_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V1, Effective Date: 26/06/2019, Version: 1 | Other
V-SA Export | #R020035_008_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_MLMO_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R020076_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S1, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #V-SA_RAMP_E_F | 0.083333 | 0 | V-SA <= MAX(49, InitialFlow - 30) (Wt=35) | Other
V-SA Export | F_QNV++HYTR_L60 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++MLMO_L60 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++MLTR_L5 | 0.083333 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+HYMO_L5 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+HYTR_L60 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+MLMO_L6 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | NRM_VIC1_SA1 | 0.083333 | 0.25 | Negative Residue Management constraint for VIC to SA flow | NIL
V-SA Export | V::N_BYPASS_HW_SY_S2 | 0.083333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 500kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V::N_WBHO_V2 | 0.083333 | 10.6667 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_X_HWSM_12_V1 | 0.083333 | 0 | Out= Hazelwood - South Morang No.1 and No.2 500kV lines, prevent transient instability for loss of ROTS-SMTS 500kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_X_HWSM_ROSM_V1 | 0.083333 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_RBTU_SETB | 0.083333 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | V_S_NIL_ROCOF | 0.083333 | 0.25 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL
V-SA Import | F_S++HYSE_L60 | 226.6667 | 4.25 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
V-SA Import | F_S++HYSE_L6_1 | 184.5 | 5.1667 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
V-SA Import | S:V_500_HY_TEST | 164.5833 | 24.5 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | S:V_500_HY_TEST_DYN | 150.0833 | 49 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | V_SV_MLMO_NETT | 102.4167 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW. Swamp out when MOPS/DUNDWF not generating | Outage
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 46.0833 | 199.9167 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-SA Import | F_S++HYSE_L5 | 44.6667 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
V-SA Import | SV_100 | 33.25 | 0 | SA to Victoria on VicSA upper transfer limit of 100 MW | Outage
V-SA Import | SV_250 | 28.4167 | 0 | SA to Victoria on Heywood upper transfer limit of 250 MW | Outage
V-SA Import | S:VS_650_HY_TEST_DYN | 19.9167 | 8.0833 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | #V-SA_RAMP_I_F | 19.4167 | 0.66667 | V-SA >= MIN(-126, InitialFlow + 50) (Wt=35) | Other
V-SA Import | S:VS_650_HY_TEST | 16.5833 | 4.5833 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | S>V_460 | 15.8333 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage
V-SA Import | S>V_460_DYN | 7.4167 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Import | V::N_DDSM_V2 | 7.1667 | 1 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Import | S>>TBTU_CGTB_MOTB | 5.9167 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of Cherry Gardens-Tailem Bend 275kV line, Feedback | Outage
V-SA Import | S:V_PA_SVC_420 | 5.5 | 1.8333 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage
V-SA Import | V>>V_KTS_TX_A2_2A_R | 4.3333 | 1.75 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | V>>V_KTS_TX_A3_2A_R | 4.25 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | V::N_X_DDSM_SMSC_V2 | 4 | 0 | Out = one Dederang to South Morang 330kV line AND series capbank on the parallel line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Import | F_S++HYSE_L6_2 | 3.1667 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage
V-SA Import | S::V_PWSE_TBSE_2 | 2.25 | 0 | Out = Penola West - South East #1 132KV line (NOTE: with both Black Range series capacitors O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | SA_HYSE2 | 1.8333 | 0.41667 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage
V-SA Import | S::V_NIL_TBSE_2 | 0.66667 | 0 | Out = Nil(Note: with both Black Range series capacitors O/S); SA to VIC Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Import | #R019380_007_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R020150_010_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Import | S:V_550_HY_TEST | 0.58333 | 0 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | S:V_580 | 0.58333 | 0 | Out = One Heywood 500/275 kV txfmr (two remain in service), maintain maximum SA to VIC transfer limit of 580 MW on Heywood and Murraylink combined to avoid oscillatory instability | Outage
V-SA Import | #R018631_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S>>TBTU_CGTB_MOTB, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R019414_007_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019491_007_RAMP_V | 0.5 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019582_009_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R020133_010_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Import | #R019395_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019442_007_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019473_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S::V_PWSE_TBSE_2, Effective Date: 05/08/2019, Version: 1 | Other
V-SA Import | #R019582_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019969_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R020035_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R020133_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Import | #V-SA_RAMP_E_F | 0.41667 | 0 | V-SA <= MAX(49, InitialFlow - 30) (Wt=35) | Other
V-SA Import | #R018631_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>TBTU_CGTB_MOTB, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R019414_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019491_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019575_009_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019575_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019729_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R020061_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Import | #R019389_007_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019395_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019595_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint SV_250_DYN, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R020061_010_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Import | #R020150_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Import | #R019103_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_DDSM_SMSC_V2, Effective Date: 28/06/2019, Version: 1 | Other
V-SA Import | #R019269_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint SV_250_DYN, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R019389_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019408_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019442_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019473_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S::V_PWSE_TBSE_2, Effective Date: 05/08/2019, Version: 1 | Other
V-SA Import | #R020035_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | NRM_SA1_VIC1 | 0.16667 | 7.5833 | Negative Residue Management constraint for SA to VIC flow | NIL
V-SA Import | S:V_550_HY_TEST_DYN | 0.16667 | 0 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | SV_070 | 0.16667 | 0 | SA to Victoria on VicSA upper transfer limit of 70 MW | Outage
V-SA Import | #R018634_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250_DYN, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R018641_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250_DYN, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R019190_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R019249_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250_DYN, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R019408_007_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V_SV_MLMO_NETT, Effective Date: 07/08/2019, Version: 1 | Other
V-SA Import | #R019712_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R019757_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | V>>V_KTS_TX_A3_3A_R | 0.083333 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr for trip of ROTS A1 500/220 kV txfmr, radial mode, Yallourn W unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | V^^N_NIL_1 | 164.4167 | 72.6667 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
VIC1-NSW1 Export | V>>N-NIL_HA | 73.6667 | 21.0833 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
VIC1-NSW1 Export | V::N_HWSM_V2 | 67 | 2.5833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 48.1667 | 197.3333 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
VIC1-NSW1 Export | V::N_HWSM_V1 | 34.4167 | 5 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_NILxxx | 16.8333 | 249.1667 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
VIC1-NSW1 Export | V::N_SMSC_V2 | 16.5833 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HG | 15.4167 | 7 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | V>>V_NIL_5 | 14 | 2 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | NRM_VIC1_NSW1 | 11.9167 | 0 | Negative Residue Management constraint for VIC to NSW flow | NIL
VIC1-NSW1 Export | V::N_KGRC_V2 | 11.8333 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | N>>N_65+66_N-2_2 | 7.5 | 0 | Out= Nil, avoid O/L Dederang to Wodonga on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL
VIC1-NSW1 Export | V::N_HORC_V2 | 7.25 | 5.6667 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_DDSM_V2 | 7.1667 | 1.3333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMSC_S2 | 4.75 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A3_2A_R | 4.25 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | N>>N-NIL_1G | 4.1667 | 0 | Out= Nil, avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22) line, Feedback | NIL
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2A_R | 4.0833 | 1.75 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | V::N_X_DDSM_SMSC_V2 | 4 | 0 | Out = one Dederang to South Morang 330kV line AND series capbank on the parallel line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_V2 | 3.8333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_KTSY_V2 | 2.6667 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_ESTN_HYSE_VA | 2.25 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V>>N-MSUT_4 | 2 | 0 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
VIC1-NSW1 Export | N>>N-SNVP_03 | 1.8333 | 0 | Out = SydneyNorth-ValesPoint(22), avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25) line, Feedback | Outage
VIC1-NSW1 Export | V>>V_LTMS_1 | 1.8333 | 0 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage
VIC1-NSW1 Export | V>>N-JNWO_RADIAL_2 | 1.5 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S1 | 1.3333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V>>V-MSUT_1 | 1.25 | 5.1667 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback | Outage
VIC1-NSW1 Export | N>>N-X_AVMA_KCTX_11 | 1.0833 | 0 | Out= Avon to Macarthur (17) 330kV line and Kemps Creek No.2 or No.3 500/330kV transformer , avoid O/L Vales Point to Munmorah (23) on trip of remaining Kemps Creek transformer, Feedback | Outage
VIC1-NSW1 Export | V::N_EPMB_V2 | 0.91667 | 2.9167 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_HWSM_S1 | 0.91667 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
VIC1-NSW1 Export | N>>N-KVCW_10_15M | 0.83333 | 0 | Out = KangarooValley-Capital(3W), avoid O/L Canberra to Yass (9) on trip of Lower Tumut to Yass (3) line, Feedback | Outage
VIC1-NSW1 Export | #R018320_006_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
VIC1-NSW1 Export | #R018441_007_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 20/02/2019, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_DPTX_2 | 0.58333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
VIC1-NSW1 Export | V>>BABE_DDGN_N-2 | 0.58333 | 0.16667 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage
VIC1-NSW1 Export | #R018315_006_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL__B_15M | 0.5 | 0 | Out= Nil, avoid O/L Upper Tumut to Canberra (01) using 15 mins rating on trip of Lower Tumut to Canberra (07) line, Feedback | NIL
VIC1-NSW1 Export | N>>N_65+66_N-2_5 | 0.5 | 0 | Out= Nil, avoid O/L Wodonga to Jindera (060) on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL
VIC1-NSW1 Export | V::N_HORC_V1 | 0.5 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | #R018315_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
VIC1-NSW1 Export | #R018395_006_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HORC_V1, Effective Date: 20/02/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018441_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 20/02/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018911_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 01/05/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018992_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 04/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019408_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S3 | 0.41667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V::N_MLMO_V2 | 0.41667 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | #R018942_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018987_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019408_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019442_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018318_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
VIC1-NSW1 Export | #R018320_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 21/11/2018, Version: 1 | Other
VIC1-NSW1 Export | #R018395_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 20/02/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018992_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 04/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019038_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019236_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019685_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTR_V1, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL__H_15M | 0.25 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL
VIC1-NSW1 Export | V::N_HORC_S2 | 0.25 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-JNWO_RADIAL_1 | 0.25 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Export | #R018294_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V2, Effective Date: 21/11/2018, Version: 1 | Other
VIC1-NSW1 Export | #R018942_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018987_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 04/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019095_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWG_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019095_018_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWG_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019103_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_DDSM_SMSC_V2, Effective Date: 28/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019236_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019236_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019903_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R020035_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_64 | 0.16667 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
VIC1-NSW1 Export | N^^N_NIL_1 | 0.16667 | 1.5 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL
VIC1-NSW1 Export | V::N_SMSY_SD | 0.16667 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | #R018911_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 01/05/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018934_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_S2, Effective Date: 01/05/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018942_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V2, Effective Date: 01/05/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018942_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 01/05/2019, Version: 1 | Other
VIC1-NSW1 Export | #R018993_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 04/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019095_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_JNWG_S2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019095_015_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWG_S2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019188_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019188_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019188_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019236_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019442_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R019903_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_V1, Effective Date: 26/06/2019, Version: 1 | Other
VIC1-NSW1 Export | #R020076_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S1, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S2 | 0.083333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 500kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V::N_WBHO_V2 | 0.083333 | 10.25 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_X_HWSM_12_V1 | 0.083333 | 0 | Out= Hazelwood - South Morang No.1 and No.2 500kV lines, prevent transient instability for loss of ROTS-SMTS 500kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_X_HWSM_ROSM_V1 | 0.083333 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A3_3A_R | 0.083333 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr for trip of ROTS A1 500/220 kV txfmr, radial mode, Yallourn W unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Import | N^^V_NIL_1 | 2056.9167 | 1114.4167 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
VIC1-NSW1 Import | N^^V_BUDP_1 | 35.1667 | 1.5833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_DDSM1 | 32.8333 | 6.25 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage
VIC1-NSW1 Import | N^^V_MSUT_1 | 20.3333 | 2.1667 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_CNCW_1 | 16.3333 | 11.5833 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_SMTXF2_1 | 11.1667 | 1.3333 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V_NIL_3 | 6.6667 | 0.33333 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Import | N^^V_LTWG_1 | 5.5 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_GRYS_1 | 5.1667 | 0 | Out = Gullen Range to Yass (3J), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V-LTWG_RADIAL_2 | 3.0833 | 0 | Outage = Lower Tumut to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload Murray to Dederang No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings; Feedback | Outage
VIC1-NSW1 Import | N>>V-NIL_HJ | 3 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 2.75 | 2.5 | Negative Residue Management constraint for NSW to VIC flow | NIL
VIC1-NSW1 Import | F_NQ++65_66_RAD_L5 | 2.4167 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 5 min Requirement | Outage
VIC1-NSW1 Import | F_VST++65_66_RAD_R5 | 2 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; VIC, SA and TAS Raise 5 min Requirement | Outage
VIC1-NSW1 Import | F_NQ++65_66_RAD_L60 | 1.6667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 60 sec Requirement | Outage
VIC1-NSW1 Import | N>>V-LTMS_5 | 1.3333 | 0.91667 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L(15m rating) on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage
VIC1-NSW1 Import | N>>V-MSUT_5 | 1.25 | 0 | Out= Murray-UpperTumut(65), avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage
VIC1-NSW1 Import | V>>DDSH_DDGN_N-2 | 1.1667 | 1.0833 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
VIC1-NSW1 Import | #R018778_019_RAMP_F | 1.0833 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other
VIC1-NSW1 Import | F_VST++65_66_RAD_R60 | 1.0833 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; VIC, SA and TAS Raise 60 sec Requirement | Outage
VIC1-NSW1 Import | F_NQ++65_66_RAD_L6 | 0.91667 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; NSW and Qld Lower 6 sec Requirement | Outage
VIC1-NSW1 Import | NV_0000 | 0.83333 | 0 | Discretionary NSW to Vic transfer upper limit of 0 MW | Outage
VIC1-NSW1 Import | #R018604_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018703_010_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018721_010_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | N^^V_DDWG | 0.66667 | 3.6667 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V-JNWG_RADIAL_1A | 0.66667 | 0 | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage
VIC1-NSW1 Import | N>>V-JNWG_RADIAL_3 | 0.58333 | 0 | Out = Jindera to Wagga(62), avoid O/L Upper Tumut to Murray (65) using 15 mins rating on trip of Lower Tumut to Murray (66) line, Feedback | Outage
VIC1-NSW1 Import | N>>V-NIL_O | 0.58333 | 20.25 | Out = Nil, avoid overloading Upper Tumut to Murray (65) using 15 mins rating line on trip of Lower Tumut to Wagga (051) + 970,990,99M (out of Yass) line, Feedback | NIL
VIC1-NSW1 Import | #R018350_010_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | F_VS++65_66_RAD_R60 | 0.5 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS | Outage
VIC1-NSW1 Import | #R018313_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018359_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018604_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018657_010_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R019067_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019133_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R018657_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R019133_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019181_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_GRYS_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019436_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019479_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | F_VS+65_66_RAD_R60 | 0.33333 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 60 sec Requirement, Basslink unable to transfer FCAS | Outage
VIC1-NSW1 Import | #R018208_013_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_DDWG, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018351_010_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018362_019_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018650_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018683_010_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018703_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018709_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018721_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018785_019_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018881_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R018881_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019067_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019424_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019436_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019441_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019441_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019484_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | F_VS+65_66_RAD_R5 | 0.25 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration; Vic and SA Raise 5 min Requirement, Basslink unable to transfer FCAS | Outage
VIC1-NSW1 Import | N>>V-LTUT_J | 0.25 | 0 | Out = LowerTumut-UpperTumut(64), avoid Upper Tumut to Murray(65) O/L on Nil trip; Feedback | Outage
VIC1-NSW1 Import | V>>V-LTWG_RADIAL_1 | 0.25 | 0 | Outage = Lower Tumut to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings; Feedback | Outage
VIC1-NSW1 Import | #R018208_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DDWG, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018357_008_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>>V-MSUT_5, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018359_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018362_019_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018683_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018785_019_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other
VIC1-NSW1 Import | #R019479_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R020058_019_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | N::V_WA_BUSA_MSDD | 0.16667 | 0 | Out= Wagga 330kV A Bus, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
VIC1-NSW1 Import | N>>N-MNYS5_01_15M | 0.16667 | 0 | Out = Marulan-Yass(5), avoid O/L Marulan to Yass (4) using 15 mins rating on trip of Bannaby to Gullen Range (61) line, Feedback | Outage
VIC1-NSW1 Import | #R018350_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018351_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018357_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018650_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018654_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018709_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R019126_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019432_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | #R019484_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 15/05/2019, Version: 1 | Other
VIC1-NSW1 Import | CA_BRIS_4D0EE093_1 | 0.083333 | 0 | Constraint Automation, O/L EPS_MBTS2_220:LEP2:Z:220@MBTS@VIC for CTG LVCY on trip of EPS-MBTS1 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage
VIC1-NSW1 Import | N>>V-NIL_HC | 0.083333 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; Feedback | NIL

## Outages
Constraint Set ID | 2019 Days | 2018 Days | Description
N-STWF1_WT_MW | 365 | 48.2535 | Limit number of turbines online and upper MW for Silverton wind farm
T-PMPO_220 | 238.6944 | 0 | Out=A single Palmerston-Poatina 220KV line. One line out of service only
N-MBTE_1 | 187.2778 | 284.9201 | Out= one Directlink cable
Q-810_PARALLEL_CLOSE | 101.8993 | 0.079861 | Out= 810 H9 Palmwoods to H5 Woolooga 275 kV feeder with parallel 132 kV network intact
T-FATI | 58.5486 | 26.8299 | Out=Farrell-Tribute 220KV line
V-HWSM | 51.7535 | 11.8264 | Outage = Hazelwood to South Morang 500kV line
S-X_BC_CP | 48.5 | 25.4201 | Out = both Black Range series capacitors bypassed
S-RBPA | 41.5347 | 11.5694 | Out= Robertstown - Para 275 kV line
V-MTGBRAND_33WT | 41.5 | 31 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 33
V-MURRAWRWF_WT_MW | 40.4549 | 0 | Limit MW output of Murra Warra wind farm to hold point levels during day/night
N-LSTN_96L | 38.2153 | 1.9757 | Out= Lismore to Tenterfield (96L)
Q-NESTM | 38.0347 | 0.60069 | Out= one H11 Nebo to H35 Strathmore 275kV line (822 / 878 / 8845)
Q-X_CPGG2_GGWO2 | 36.3368 | 0 | Out = H67 Calliope River to H6 Gin Gin 275kV line (814) and H6 Gin Gin to H5 Woolooga 275kV line (816)
N-ARKS_965 | 35.1667 | 8.1597 | Out= Armidale-Kempsey (965) 132kV line
Q-X_CPWO_BI_INTACT | 34.0382 | 0 | Out= 813+815 or 814, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104 and 7105 (T022 Callide A to T152 Gladstone S) 132 kV lines open with 132 kV intact/split btw T022 Callide A and H015 Lilyvale, Feedback
Q-WUBI | 31.5278 | 1.4549 | Out= 865 or 866 H40 Wurdong to H8 Boyne Island 275kV feeder, CQ-SQ voltage stability limit, 2008/2009 implementation
Q-BSNE | 29.25 | 37.0208 | Out = any one of either 834, 8846, or 8847 275kV fdr H20 Broadsound - H11 Nebo
S-MHNW_1 | 28.9618 | 0.48958 | Out = Monash to North West Bend line 1, runback On
N-X_MBTE_2 | 27.6007 | 55.7882 | Out= two Directlink cables
S-PATU | 26.6215 | 0 | Out = Para to Tungkillo 275 kV line(Note: with both Black Range series caps I/S)
Q-NESTM_STRGTH | 25.7569 | 0 | Out= 822, (H11 Nebo to H35 Strathmore) 275kV line, restrict Haughton, Sun Metal and Mt Emerald Solar farms to meet system strength requirements
I-ML_ZERO | 24.9479 | 35.3646 | Limit Murraylink to zero in either direction
Q-STBS | 23.1354 | 26.4167 | Out= 856 or 8831 H29 Stanwell to H20 Broadsound 275 kV line
I-VS_050 | 22.6146 | 1.0208 | Victoria to SA on VicSA upper transfer limit of 50 MW
S-PATW | 21.3715 | 12.9896 | Out = Para - Templers West 275kV line
Q-MKG_0 | 20.941 | 0 | Discretionary, Mackay GT =< 0MW
V-KTTX_A2_OR_A4_R | 17.9826 | 2.8958 | Outage = Keilor 500/220kV A2 or A4 transformer, Radial
N-LSLS_9U8 | 17.6146 | 0.11806 | Outage= 9U8 or 9U9 or 9W1 132kV line
V-HYTX_M12 | 15.4583 | 1.0035 | Out = Heywood (HYTS) M1 or M2 500/275 kV txfmr
S-X_DVBR+BRTW+TWPA | 14.1979 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line
V-MLTR | 14.1285 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) No. 1 500kV line, MOPS 500kV centre CB fail timer set to zero
Q-BCCP_CAGS_CLOSED | 13.6528 | 21.1111 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, thermal limit equations for 811, 871 and 8859.
T-FARC2 | 13.2292 | 0.40972 | Out=Farrell-Reece 2 220KV line
F-I_ML_APD | 13.0729 | 17.4896 | Out=Nil, Dymanic FCAS for APD Load Event
T-FARC1 | 12.934 | 0.28125 | Out=Farrell-Reece 1 220KV line
S-PATU_BC-2CP | 12.1944 | 0 | Para to Tungkillo 275kV line O/S (NOTE: with both Black Range series caps O/S)
T-BUSH_220_WCP_OPEN | 12.0035 | 0 | Out = Burnie to Sheffield No.1 220kV line O/S, West Coast 110/220KV parallel open, either 110 kV CB at Hampshire open or parallel opened at Farrell, Burnie 110 kV bus NOT split
Q-HACL | 11.9549 | 0.09375 | Out= 8810 or 8811 H24 Calvale to S2 Halys 275 kV feeder
S-X_DVBR+BRTW | 11.375 | 0 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX)
Q-LILYSF1_ZERO | 11.3576 | 0 | Lilyvale Solar Farm upper limit of 0 MW
Q-X_CPGG1_GGWO1 | 11.2743 | 0 | Out= 813 (H67 Calliope River to H6 Gin Gin) and 815 (H6 Gin Gin to H5 Woolooga) 275kV lines
Q-CLST_STRGTH | 11.1597 | 0 | Out= 8874, (H24 Calvale to H29 Stanwell) 275kV line, restrict Haughton, Sun Metal and Mt Emerald Solar farms to meet system strength requirements
S-RB_275KV_N_BUS | 11.1042 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, CBs 6616, 6573, 6005 and 6188 O/S) (Note:with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S)
Q-X_WOPW_CPWO2_CL | 11.0799 | 0 | Out = 810 (H5 Woolooga to H9 Palmwoods) 275kV line, 813 (H67 Calliope River to H6 Gin Gin) 275kV line and 815 (H6 Gin Gin to H5 Woolooga) 275kV lines with 132kV and 110kV network between Woolooga to Palmwoods network closed
Q-GB_VC | 10.3854 | 5.5278 | Out= S3 Greenbank SVC
T-BWLF | 9.684 | 0.027778 | Out = Bridgewater to Lindisfarne OR Bridgewater to Waddamana 110kV line
N-LS_VC1 | 9.4514 | 110.1528 | Out= Lismore SVC
T-PMPO_TWO_220 | 9.0417 | 0 | Out= two Palmerston to Poatina 220KV lines
V-KTTX_A3_R | 8.6736 | 4.1528 | Outage = Keilor 500/220kV A3 transformer, Radial
V-HORC | 8.6736 | 5.434 | Out = Horsham to Murra Warra to Redcliffs 220kV line
T-LIPM | 8.4549 | 14.4757 | Out = Liapootah to Waddamana to Palmerston 220kV line, with associated 220kV CB I/S at Waddamana
Q-CPWO_B_CAGS_CALV_C | 8.3819 | 0 | Out= 813+815 or 814+816,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104 and/or 7105(T022 Callide A to T152 Gladstone S)132 kV lines close with 132 kV intact between T022 Callide A and H015 Lilyvale, Feedback
S-MHNW_2 | 8.2396 | 0 | Out = Monash to North West Bend line 2
S-RB_275KV_S_BUS | 8.2188 | 0 | Out= Robertstown 275kV South Bus (i.e. CBs 6572, 6575, 6148 & 6149 OPEN and Robertstown 275/132 TX2 O/S).
N-TAPM_964 | 7.9722 | 185.4167 | Out = Taree to Port Macquarie (964) 132kV line
V-SMSC | 7.809 | 0.097222 | Outage = one South Morang 330kV series capacitor
S-TBTX4 | 7.7778 | 0 | Out= Tailembend 275/132kV #4 TX (Note: transformer ONLY O/S, with all associated transformer CBs I/S), (Note: with both Black Range series caps I/S)
V-YENDONWF_WT_MW | 7.5556 | 0 | Limit MW output of Yendon wind farm to hold point levels during day/night
N-X_MBTE_3 | 7.3507 | 10.6215 | Out= all three Directlink cables
V-MLMO | 7.2014 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN
Q-STBS_8831_STRGTH | 7.191 | 0 | Out= 8831, (H29 Stanwell to H20 Broadsound) 275kV line, restrict Haughton, Sun Metal and Mt Emerald Solar farms to meet system strength requirements
V-MRRC | 7.1354 | 0 | Out = Murra Warra to Redcliffs 220kV line
V-KGWT | 7.0521 | 0 | Outage = Kerang to Wemen 220 kV line section
Q-RSTVS | 6.8507 | 0 | Out= one H13 Ross to T56 Townsville South 132kV line (7156/7249)
S-BRTW | 6.4722 | 14.4306 | Out= Brinkworth- Templers West 275kV line
S-MKRB | 6.3785 | 18.0347 | Out= Mokota-Robertstown 275kV line (Note: with both Black Range series caps I/S)
Q-LCCP_CAGS_CLOSED | 6.3299 | 19.1979 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, thermal limit equations for 812 and 871.
Q-810_PARALLEL_OPEN | 6.2083 | 0.28819 | Out= 810 H9 Palmwoods to H5 Woolooga 275 kV feeder with parallel 132 kV and 110kV network open
S-DVBL | 6.1806 | 21.2778 | Out = Davenport - Belalie 275kV line (Note: with both Black Range series caps I/S)
N-BUDP | 5.816 | 0.31944 | Out = Buronga to Darlington Point (X5) 220kV line
S-X_CNRB+CB | 5.6354 | 0.25694 | Out = Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S(Note:both Black Range series capacitors I/S)
T-LIPM_PMWA_N-3 | 5.5139 | 0 | Out=Nil, loss of both Liapootah to Waddamana to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line declared credible
S-TB2_TX | 5.2014 | 0 | Torrens B unit 2 Transformer O/S; TB2 <= 0MW
I-VT_000 | 5.1701 | 0 | Vic to Tas on Basslink upper limit of 0 MW
Q-STBS_NESTM_STRGTH | 4.8958 | 0 | Out= 822 or 8845 or 878 (H11 Nebo to H35 Strathmore) 275 kV line and 856 or 8831 (H29 Stanwell to H20 Broadsound) 275kV line, restrict Haughton, Sun Metal and Mt Emerald Solar farms to meet system strength requirements
S-X_RBTU+CB | 4.7882 | 0.48958 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, (Note: with Both Black Range series caps I/S)
I-NQTE_-060 | 4.5035 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -60 MW
S-DLBAT-G_0 | 4.4757 | 0.28819 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW
S-DLBAT-L_0 | 4.4757 | 0.28819 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW
S-PA_VC1 | 4.4722 | 1.1632 | Out= One Para SVC , (Note: with both Black Range Series caps I/S)
S-HUBG | 4.3472 | 0 | Out= Hummocks-Bungama 132kV line (Note: this offloads Snowtown WF)
N-STWF1_ZERO | 4.3299 | 2.3264 | Silverton wind farm upper limit of 0 MW
N-SAPHWF_TX | 4.316 | 0.50694 | Outage = One Sapphire wind farm 330/33kV transformer (1A or 1B), Sapphire WF Isolators 2415 and 2416 closed
V-SMSY | 4.1354 | 1.2986 | Out = Either South Morang-Sydenham 500 kV line, Radial mode
N-BAMB_132_OPEN | 4.0972 | 2.9757 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path.
S-SE_TX_1 | 4.0799 | 1.5799 | Out = One South East 275/132kV transformer (NOTE: associated CBs I/S)
V-HM_VIC_ZERO | 4.066 | 1.809 | Hume VIC unit upper limit of 0MW
S-EMTX1 | 4.0625 | 0 | Out = Emeroo 132/33kV TX1 transformer
V-EL_TX_R2 | 4.0382 | 0.3125 | Out = Elaine R2 220/132kV transformer
S-LBMY_2B | 4.0278 | 0 | Out= Mayura-Lake Bonney WF 2B 33kV line (OR Mayura CB4565 and CB4674 OPEN)
V-MTMERCER_ZERO | 3.7986 | 0.086806 | Mt Mercer Windfarm upper limit of 0 MW
S-RBTU | 3.7569 | 0 | Out= Robertstown - Tungkillo 275 kV line (Note: Line ONLY O/S with associated line CBs I/S); (NOTE: with both Black Range series caps I/S)
V-X_HY_MO_ML | 3.5972 | 0 | Out = Heywood to Mortlake to Moorabool No.2 500kV lines
V-KTSY_R | 3.5243 | 0.64236 | Outage = Keilor to Sydenham 500kV line, Radial mode
S-SECB6161 | 3.5139 | 7.6215 | Out = South East 132kV CB6161 ONLY O/S
Q-X_STBS_STMVC | 3.5104 | 0 | Out= 856 or 8831 (H29 Stanwell to H20 Broadsound) 275kV line and H35 Strathmore SVC, Stanwell Broadsound SIPS armed and enabled
V-HYTR | 3.3681 | 0.097222 | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line
N-COLEASF1_ZERO | 3.2986 | 0.82639 | Coleambally solar farm upper limit of 0 MW
S-NWRB | 3.2917 | 0 | Out = North West Bend to Robertstown
N-X_ARKS_LITN | 3.2222 | 0 | Out= Armidale to Kempsey (965) and Lismore to Tenterfield (96L)
N-X_96H_96R | 3.1528 | 0 | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line
V-DDSM | 3.1042 | 2.7812 | Out = Dederang to South Morang (DDTS-SMTS) 330 kV line
V-MACARTHUR_ZERO | 3.0833 | 0.020833 | Macarthur Wind Farm upper limit of 0 MW
S-NW_CB6025 | 3.0139 | 0.15625 | Out= North West Bend 132kV CB6025
Q-H11NE_SVC | 3.0069 | 1.3021 | Out= H11 Nebo SVC OOS
S-DVLK | 3.0035 | 4.3056 | Out = Davenport-Mt Lock 275kV line (Note:both Black Range series capacitors I/S)
N-MOREESF1_ZERO | 2.9479 | 0 | Moree Solar Farm upper limit of 0 MW
I-MSUT | 2.8542 | 0.78125 | Out= Murray - Upper Tumut (65) line
N-DEFI_9R3_C | 2.8368 | 0 | Out= Finley to Deniliquin (9R3); X5 Trip Scheme Disarmed, 132 kV parallel Solid, option c OM521
I-LTMS | 2.6944 | 0.32639 | Out= Lower Tumut - Murray (66) line
S-KNPW | 2.6354 | 16.2049 | Kincraig to Penola West 132kV O/S, (Note: with both Black Range series caps I/S)
S-CNLK_BC-2CP | 2.5417 | 0 | Out= Canowie-Mt Lock 275kV line (Note: with both Black Range series caps O/S)
S-X_RBPA+CB6574+75 | 2.5417 | 1.3056 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575
V-AR_WB_BA | 2.4861 | 0 | Out = Ballarat to Waubra 220kV line (with Waubra WF OFF which offloads Ararat to Waubra 220kV line) or Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S)
I-X_BURC_MRRC | 2.4688 | 0 | Out = Buronga - Red Cliffs and Murra Warra - Red Cliffs 220kV lines
S-HALWF2_0 | 2.4653 | 2.4757 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW
N-AR_TX | 2.4549 | 0.79514 | Out= Armidale No.3 or 6 330/132kV transformer
N-WRWSF_055 | 2.4236 | 0.20486 | Upper limit of 55 MW on total generation of White Rock wind and solar farms
S-WIMK | 2.4167 | 3.8993 | Out= Willalow-Mokota 275kV line (Note: WITH/WITHOUT associated line CBs I/S); (Note: with both Black Range series caps I/S)
Q-MEWV_824 | 2.3785 | 0.19097 | Out= Mt England to Wivenhoe (824) line
S-PA_W_BUS_R | 2.3333 | 0 | Out= Para 275kV West bus Right section(i.e.CBs 6601,8033,6510,6514 6542,6541, TX8 O/S),(NOTE: BW-MP 275kV line will also be taken O/S as per Electranet's OI 5.17 issued 19/07/2017),(Note: with both Para SVC 1 & 2 inservice and connected to Para East bus)
S-MWP3RB | 2.2188 | 0 | Morgan-Whyalla Pipeline Pump No.3-Robertstown 132kV line O/S, with Murraylink runback scheme ON.
V-HOTS_SVC | 2.1806 | 0 | Out = Horsham 220kV SVC
T-LFWA | 2.066 | 0 | Out = One Lindisfarne to Waddamana 220 kV line
S-PWSE_BC-2CP | 2.0208 | 0 | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps O/S)
V-RCWT | 1.9688 | 0 | Outage = Red Cliffs to Wemen 220 kV line section
V-WEMENSF_ZERO | 1.9688 | 1.8924 | Wemen Solar Farm upper limit of 0 MW
N-LSDU_9U6 | 1.9549 | 1.0938 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L on the remaining 132kV line, Feedback
N-SNVP_22 | 1.9375 | 2.4861 | Out= Sydney North - Vales Point (22)
N-DPWG_63_X5 | 1.8715 | 0.27778 | Out = Darlington Point to Wagga (63) 330kV line + line X5 opened
Q-CHWK | 1.8056 | 0 | Out= 876 H32 Chalumbin to H60 Walkamin 275kV line
I-SV_100 | 1.7917 | 0 | SA to Victoria on VicSA upper transfer limit of 100 MW
I-SV_250 | 1.7743 | 0 | SA to Victoria on VicSA upper transfer limit of 250 MW
N-JNWG_RADIAL | 1.6944 | 1.0417 | Outage = Jindera - Wagga (62) line, Wagga-Yass 132kV network Split, X5 opened and with 2 Yass Transformer in service
V-CWHO | 1.6354 | 0.67014 | Out = Crowlands to Horsham 220kV line
V-EPMB | 1.5938 | 2.7917 | Outage = Eildon to Mt Beauty 220kV line
T-TU_LE_WA1 | 1.5833 | 0 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line
S-X_MKRB+WTTP | 1.5833 | 0 | Out= Mokota-Robertstown 275kV line (note:associated line CBs assumed I/S) + Waterloo-Templers 132kV line; (Note: with both Black Range series caps I/S)
N-AR_VC1 | 1.5729 | 6.3299 | Out = Armidale SVC
N-DM_CB | 1.566 | 0.29514 | Out = one Dumaresq 330kV CB (5312, 5322, 5332 or 5342) O/S
N-X_96H_LS_SVC | 1.5035 | 0 | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode
S-BLNBH_0 | 1.4688 | 0 | Out = Belalie - North Brown Hill 275kV line O/S (i.e. North Brown Hill WF <= 0 MW)
S-HALWF_0 | 1.4514 | 0 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW
V-WETS_BTX | 1.4479 | 0 | Out = Wemen 220/66kV B1 or B2 txfmr
N-BROKENH1_ZERO | 1.4375 | 0.045139 | Broken Hill Solar Farm upper limit of 0MW
S-X_RBPA+BGTX | 1.434 | 0 | Out= Para-Robertstown 275kV line(i.e. Line ONLY O/S with line CBs I/S)+Bungama 275/132kV TX O/S
S-LB2_0 | 1.4306 | 2.5 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW
S-LB3_0 | 1.4306 | 2.5 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW
N-GITN_96R | 1.3958 | 0.61111 | Out= Glen Innes to Tenterfield (96R) line
S-X_RBTU+CB_BC-2CP | 1.3785 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, (Note: with Both Black Range series caps O/S)
N-BABU | 1.3715 | 0 | Out = Balranald to Buronga (X3) 220kV line
N-FLUR_99A | 1.3576 | 0 | Out = Finley to Uranquinty (99A)
S-NWBCB6024+6025 | 1.3438 | 0 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2)
S-X_KNPW+SEVC | 1.3299 | 0 | Out= One South East SVC + KinCraig-Penola West 132kV line O/S (Note: with both Black Range series caps I/S)
V-MURRAWR_ZERO | 1.3229 | 0 | Murra Warra wind farm upper limit of 0 MW
N-GULLRWF1_ZERO | 1.309 | 0 | Gullen Range WF upper limit of 0 MW
V-BUHO | 1.2951 | 0 | Out = Bulgana to Horsham 220kV line
V-HWYP2 | 1.2812 | 3.2743 | Out = Hazelwood to Yallourn No. 2 220 kV line, radial mode
I-BL_ZERO | 1.1632 | 0 | Limit Basslink to zero in either direction
V-KGTS_SVC | 1.1597 | 0 | Out = Kerang 220kV SVC
S-MKRB_BC-2CP | 1.1285 | 0.60069 | Out= Mokota-Robertstown 275kV line (Note: with both Black Range series caps O/S)
V-SALTCREEK_ZERO | 1.1146 | 0 | Salt Creek wind farm upper limit of 0 MW
T-NWSD | 1.1111 | 0.30903 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752
V-KG_WE_RC | 1.1111 | 0 | Outage = Kerang to Wemen to Red Cliffs 220 kV line section, entire line section
S-TB275_E_BUS_BC-2CP | 1.1042 | 0.64583 | Out = Tailem Bend 275kV East Bus WITH/WITHOUT associated bus 275kV CBs O/S (Note: or Tailembend 132/275kV TX4 transformer + associated tx 275kV CBs O/S); (Note: all other 275kV CBs & lines at Tailembend I/S), (Note: with both Black Range series capsO/S)
T-GTSH | 1.0938 | 1.1458 | Out = One George Town to Sheffield 220kV line
S-CNHL_HAL | 1.0799 | 0 | Out = Canowie Hallett 275kV line
Q-808_PARALLEL_OPEN | 1.0174 | 0 | Out= 808 (H9 Palmwoods to H2 South Pine ) 275 kV feeder with parallel 132 kV and 110kV network open
S-TBTX4_BC-2CP | 1.0174 | 0 | Out =Tailem Bend 132/275 kV #4 Transformer O/S (Note: transformer ONLY O/S, with all associated transformer CBs I/S), (Note: with both BlackRange Series Caps O/S)
N-X_AVMA_KCTX | 0.94444 | 1.4792 | Out= Avon to Macarthur (17) 330kV line and Kemps Creek No.2 or No.3 500/330kV transformer O/S
N-LTWG_RADIAL | 0.88889 | 0 | Out= Lower Tumut - Wagga (051) line, Wagga-Yass 132kV network Split, X5 opened and with 2 Yass Transformer in service
V-SMTS_BYPASS_HW_SY | 0.88194 | 1.7812 | Outage = SMTS 500kV bus or CB outages or SMTS bus bypass that creates risk of HWTS-SMTS and SMTS-SYTS combined line trip, Radial or Parallel
N-BODWF1_ZERO | 0.87847 | 0.35417 | Bodangora wind farm upper limit of 0 MW
T-LIWY | 0.86111 | 0.43403 | Out=Liapootah-Wayatinah 220KV line
S-DVBL_BC-2CP | 0.83333 | 0 | Out = Davenport - Belalie 275kV line (Note: with both Black Range series caps O/S)
I-CTRL_ISSUE_TE | 0.82986 | 4.6215 | DC Link Control Issue Constraint for Terranora
S-X_BLDV+WERB | 0.80208 | 0 | Out= Belalie-Davenport 275kV line + Waterloo East-MWP4-Robertstown 132kV line(or any line segment between Waterloo East and Robertstown), (Note: with both Black Range series capacitors I/S)
F-I-BCDM_ONE | 0.79861 | 0.26736 | Out = one Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line 330kV line - FCAS Requirements
I-JNWO_RADIAL | 0.77431 | 1.25 | Out = Jindera to Wodonga (060) line, Wagga-Yass 132kV network Split, X5 opened and with 2 Yass Transformer in service
N-ARIV_96N | 0.73958 | 0 | Out = Armidale to Inverell (96N) 132kV line
Q-RRSF1_ZERO | 0.72222 | 1.3403 | Ross River solar farm upper limit of 0 MW
T-TU_WA2 | 0.71528 | 0.090278 | Out = Tungatinah to Waddamana No.2 110kV line
F-I_ML_0500 | 0.70486 | 0 | Out=Nil, FCAS for a NEM Load Event, ML = 500
N-MBTE_110 | 0.68403 | 0 | NSW <-> QLD on Directlink upper transfer limit of 110 MW in either direction
V-ARCW | 0.66319 | 1.3333 | Out = Ararat to Crowlands 220kV line
N-WAGGA_330_BUSA | 0.64583 | 0 | Out=Wagga 330kV bus A. Wagga-Yass 132kV network split, X5 opened and with 2 Yass Transformer in service
Q-MEWV_823 | 0.63889 | 0.42361 | Out= Mt England to Wivenhoe (823) line
T-HAPM_220 | 0.60764 | 30.1111 | Out = One Hadspen to Palmerston (No.1 or No.2) 220kV line
S-LFTI | 0.59028 | 1.2222 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S)
N-KKLS_967 | 0.58333 | 4.0764 | Out= Koolkhan to Lismore (967) 132kV line
F-T-CSGO | 0.56944 | 12.8472 | Out = one Chapel St to Gordon 220kV line, FCAS Requirements
N-GUNNING1_ZERO | 0.54861 | 0 | Gunning unit upper limit of 0 MW
V-X_HWSM_12 | 0.54514 | 0 | Out = Both Hazelwood to South Morang No.1 and No.2 500kV lines
N-WOODLWN1_ZERO | 0.53472 | 0 | Woodlawn unit upper limit of 0 MW
Q-KMBG_7184 | 0.53125 | 0.069444 | Out= 7184 Kamerunga Barron Gorge PS 132kV line
Q-RGBYRSF1_ZERO | 0.52431 | 0 | Rugby Run Solar Farm upper limit of 0 MW
S-DVLK_BC-2CP | 0.50347 | 0 | Out = Davenport-Mt Lock 275kV line (Note:both Black Range series capacitorsO/S)
N-TARALGAWF_ZERO | 0.49306 | 0 | Taralga WF upper limit of 0 MW
S-TBTU | 0.48264 | 0 | Out= Tailem Bend - Tungkillo 275kV line (Note: WITH/WITHOUT associated line CBs I/S), (NOTE: with both Black Range series caps I/S)
N-WRWSF_ZERO | 0.46528 | 4.4618 | Upper limit of zero MW on total generation of White Rock wind and solar farms
Q-CS_1600 | 0.46181 | 0 | Qld Central to Qld South upper transfer limit of 1600 MW
Q-SMRS | 0.45833 | 13.9583 | Out = 8857 or 8858 (H35 Strathmore to H13 Ross) 275kV line, CQ-NQ limits.
N-DPGF-99K-A | 0.44792 | 0 | Out= Darlington Point to Griffith (99K) 132kV line. X5 trip scheme Armed and Wagga to Darlington Point network Solid, option a on OM521
N-FLML_9R4 | 0.44097 | 0 | Out = Finley to Mulwala (9R4) or Mulwala to Corowa(997/2) or Corowa to Albury (997/1)
F-I-X_65_66_0X1 | 0.42361 | 0 | Out = 65 (Murray to Upper Tumut) and 66 (Murray to Lower Tumut) 330kV lines in Radial configuration (0X1 out; see OM527) - FCAS Requirements
I-NQTE_-070 | 0.41319 | 0.10069 | NSW to Qld on Terranora Interconnector upper transfer limit of -70 MW
S-SE_CB6186_CB6187 | 0.40972 | 0.27778 | Out= South East 132kV CB 6186 Or CB 6187
V-HOMR | 0.40625 | 0 | Out = Horsham to Murra Warra 220kV line
S-PW-CB6156 | 0.39583 | 2.5694 | Out= Penola West 132kV CB 6156 Or CB 6260 Or CB 6157 O/S; (Note: with Penola West 132kV CB 6158 CLOSED)
S-BG_CB6246 | 0.39583 | 0.94792 | Out = Bungama 132kV CB6246
T-TU_MB_NN1 | 0.38889 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line
F-WESTCOAST_REG_0 | 0.37847 | 0 | Regulation FCAS of West Coast Generation limited to 0 MW
S-WTE_0 | 0.375 | 0 | Discretionary upper limit for Waterloo generation of 0 MW
T-WIND_100 | 0.375 | 0 | Discretionary 100 MW upper limit on TAS Wind Generation. NOTE - Direction may also be required to manage this limit, if constraint violates
I-CTRL_ISSUE_ML | 0.36458 | 0.017361 | DC Link Control Issue Constraint for Murraylink
V-MB_BUS2 | 0.35764 | 0 | Outage of Mt Beauty No. 2 220 kV Bus
N-FLML_9R4_ARMED | 0.34375 | 0 | Out = Finley to Mulwala (9R4) or Mulwala to Corowa(997/2) or Corowa to Albury (997/1) And Finley Transfer Trip Scheme Armed
S-X_PLN_03 | 0.32639 | 0 | Out = Cultana to Yadnarie 132kV line (via Middleback), Port Lincoln PS islanded
T-CRNN | 0.32292 | 0.26042 | Out = Creek Road to New Norfolk 110kV line
V-X_DDSM_SMSC | 0.29514 | 0 | Out = one Dederang to South Morang 330kV line AND series capbank on the parallel Dederang to South Morang 330kV line
T-PMWA | 0.27778 | 27.3924 | Out = Palmerston to Waddamana 110kV line; suitable for associated CBs at WA either open or close
I-NQTE_-050 | 0.26389 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -50 MW
T-SH_TX_WCP_OPEN | 0.24653 | 0.27778 | Out = one Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open
N-LTUT_64_15M | 0.24306 | 0.88194 | Out= Lower to UpperTumut (64), 15/30_min ratings for 65, 66 lines auto-switch on prior loading
V-ARARAT_ZERO | 0.23958 | 0.47917 | Ararat Wind Farm upper limit of 0 MW
S-WIWG | 0.22222 | 0 | Out = Willalo - Willogoleche 275kV line (i.e. Willogoleche WF <=0 MW)
Q-CLWU | 0.21875 | 0 | Out = 871 H24 Calvale to H40 Wurdong 275kV line
F-T-COGT | 0.20833 | 0.89583 | Out = one Comalco to George Town 220kV line OR loss of both Comalco to Georgetown 220 kV lines or all Comalco potlines declared credible
Q-WHITSF1_ZERO | 0.20486 | 0 | Whitsunday solar farm upper limit of 0 MW
Q-HAMISF1_ZERO | 0.20486 | 0 | Hamilton solar farm upper limit of 0 MW
F-SA_ISLE | 0.19792 | 0.013889 | SA separation between Heywood and South East (HYTS - SESS) - FCAS Requirements
SA_ESTN_ISLE | 0.19792 | 0.013889 | SA / Eastern separation between Heywood and South East (HYTS - SESS)
F-SA_ESTN_ISLE_REG | 0.19792 | 0.013889 | SA / Eastern separation between Heywood and South East (HYTS - SESS) - Regulation FCAS Requirements
F-ESTN_ISLE | 0.19792 | 0.013889 | Eastern separation between Heywood and South East (HYTS - SESS) - FCAS Requirements
I-MUTE_758 | 0.1875 | 2.5764 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line
S-HDLK | 0.1875 | 0 | Out = Hornsdale - Mt Lock 275kV line
I-VT_050 | 0.18056 | 0 | Vic to Tas on Basslink upper limit of 50 MW
F-N-8C_ONE | 0.14583 | 1.5382 | Out = Armidale to Dumaresq (8C) 330kV line - FCAS Requirements
S-NWB_CB6225 | 0.14236 | 0 | Out= North West Bend 132kV CB6225
Q-807_PARALLEL_CLOSE | 0.13889 | 0 | Out= 807 H2 South Pine to H5 Woolooga 275 kV feeder with parallel 132 kV network intact
F-I_TL_0550 | 0.13542 | 0 | FCAS Lower Requirements for a NEM Network Event, TL = 550
I-QN_1000 | 0.12847 | 0 | Qld to NSW on QNI limited to 1000 MW, includes constraint with dynamic headroom
N-CLDP_99T | 0.125 | 0 | Out = Coleambally to Darlington Point (99T) 132kV line
V-X_HWSM_HWRO3 | 0.11458 | 2.25 | Out = One Hazelwood to South Morang and Hazelwood to Rowville 500kV lines
S-PWLG | 0.10764 | 1.2014 | Outage of Penola West to Ladbroke Grove 132kV circuit, LG O/S
N-COLEASF1_100 | 0.09375 | 0 | Coleambally solar farm upper limit of 100 MW
S-TBL_0 | 0.083333 | 0 | Discretionary upper limit for The Bluff generation of 0 MW
S-LB_1+2+3_110 | 0.076389 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=110 MW
N-FLUR-99A-A | 0.076389 | 0 | Out = Finley to Uranquinty (99A), X5 trip scheme armed and Wagga - Darlington point parallel solid, option a on OM521
Q-HASMME_RAMP_ZERO | 0.069444 | 0 | Ramp Haughton, Sun Metals and Mt Emerald generators to zero and hold at zero.
N-BADP | 0.052083 | 0 | Out = Balranald to Darlington Point (X5) 220kV line
I-NQTE_-090 | 0.048611 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -90 MW
Q-X_PWSP_CPWO2 | 0.045139 | 0 | Out= 808 (H2 South Pine to H9 Palmwoods), 813 (H67 Calliope River to H6 Gin Gin) 275kV line and 815 (H6 Gin Gin to H5 Woolooga) 275kV lines(132 and 110 kV parallel between South Pine and Woolooga closed)
Q-PWSP_808 | 0.045139 | 4.5382 | Out= 808 H2 South Pine to H9 Palmwoods 275 kV feeder (132 and 110 kV parallel between South Pine and Woolooga closed)
I-NV_0000 | 0.041667 | 0 | Discretionary NSW to Vic transfer limit zero
I-QN_950 | 0.038194 | 0 | Qld to NSW on QNI limited to 950 MW, includes constraint with dynamic headroom
Q-MK_33BUS | 0.034722 | 0 | Out=T38 Mackay 33kV C Bus
Q-CS_1650 | 0.034722 | 0 | Qld Central to Qld South upper transfer limit of 1650 MW
F-I_ML_APD_LOAD | 0.020833 | 0 | Out=Nil, Dynamic FCAS for APD Load Event, excluding Portland WF
I-NQTE_-040 | 0.020833 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -40 MW
Q-X_WOSP_CPWO2_CL | 0.017361 | 0 | Out = 807 (H5 Woolooga to H2 South Pine) 275kV line, 813 (H67 Calliope River to H6 Gin Gin) 275kV line and 815 (H6 Gin Gin to H5 Woolooga) 275kV lines with 132kV and 110kV network between Woolooga to Palmwoods network closed
V-OAKLANDSHILL_42 | 0.010417 | 0 | Oaklands Hill Windfarm upper limit of 42 MW
Q-CS_1550 | 0.010417 | 0 | Qld Central to Qld South upper transfer limit of 1550 MW
I-SVML_120 | 0.0069444 | 0 | SA to Vic on ML upper transfer limit of 120 MW
I-SV_070 | 0.0034722 | 0 | SA to Victoria on VicSA upper transfer limit of 70 MW
Q-CS_1000 | 0 | 0 | Qld Central to Qld South upper transfer limit of 1000 MW
V-X_HWSM_ROSM | 0 | 0 | Out = One Hazelwood to South Morang and Rowville to South Morang 500kV lines
Q-CS_0800 | 0 | 0 | Qld Central to Qld South upper transfer limit of 800 MW
Q-CS_0900 | 0 | 0 | Qld Central to Qld South upper transfer limit of 900 MW

## Outage stats
Column1 | Unplanned | Short Notice | ≤ 30 days | > 30 days
APT 2015 | 27 | 60 | 8 | 2
2016 | 24 | 36 | 7 | 1
2017 | 20 | 33 | 5 | 4
2018 | 21 | 74 | 15 | 3
2019 | 17 | 58 | 24 | 1
ElectraNet 2015 | 447 | 918 | 1003 | 231
2016 | 110 | 266 | 309 | 176
2017 | 281 | 687 | 907 | 426
2018 | 417 | 863 | 973 | 804
2019 | 352 | 852 | 1077 | 835
Essential E 2015 | 0 | 17 | 59 | 0
2016 | 3 | 26 | 40 | 0
2017 | 4 | 28 | 61 | 0
2018 | 8 | 5 | 29 | 0
2019 | 4 | 17 | 39 | 0
Powerlink 2015 | 1076 | 3173 | 6415 | 100
2016 | 273 | 885 | 2265 | 17
2017 | 1796 | 5071 | 11266 | 195
2018 | 2020 | 5841 | 13383 | 222
2019 | 2040 | 5250 | 8042 | 2334
AusNet 2015 | 197 | 1119 | 918 | 86
2016 | 170 | 876 | 695 | 97
2017 | 316 | 1484 | 1208 | 80
2018 | 304 | 1467 | 970 | 54
2019 | 364 | 1387 | 1588 | 69
TasNetworks 2015 | 128 | 629 | 993 | 302
2016 | 19 | 88 | 166 | 32
2017 | 89 | 472 | 602 | 323
2018 | 171 | 577 | 637 | 238
2019 | 198 | 500 | 1069 | 340
TransGrid 2015 | 161 | 678 | 1290 | 764
2016 | 116 | 472 | 973 | 506
2017 | 277 | 911 | 1365 | 856
2018 | 326 | 820 | 1730 | 522
2019 | 327 | 1066 | 1868 | 837

## NEM Changes
PROJECT | DATE | REGION | NOTES
Childers Solar Farm | 25 January 2019 | Qld | New Generator
Tailem Bend Solar Farm | 5 February 2019 | SA | New Generator
Lilyvale Solar Farm | 6 February 2019 | Qld | New Generator
Bulgana Terminal Station | 19 February 2019 | Victoria | A new substation cut-in between Crowlands and Horsham 220 kV to form Bulgana to Crowlands 220 kV line and Bulgana to Horsham 220 kV line
Gin Gin bypass project (feeder 814 & 816 bypassed) | 2019-03-01 | Qld | Feeder 814 from Calluope river to Gin Gin joined feeder 816 from Gin Gin to Woolooga.to form one feeder
Murra Warra Terminal Station | 2019-03-07 | Victoria | A new substation cut-in between Horsham and Red Cliffs 220 kV to form Murra Warra to Horsham 220 kV line and Murra Warra to Red Cliffs 220 kV line
Oakey 1 Solar Farm | 12 March 2019 | Qld | New Generator
Lincoln Gap Wind Farm (MW) | 19 March 2019 | SA | New Generator
Murra Warra Wind Farm Stage 1 | 19 March 2019 | Victoria | New Generator
Beryl Solar Farm | 11 April 2019 | NSW | New Generator
Gin Gin 275 kV Cap removal | 2019-05-01 | Qld | Bridgewater to Waddamana 110kV Line
Numurkah Solar Farm | 7 May 2019 | Victoria | New Generator
Haughton Solar Farm | 28 May 2019 | Qld | New Generator
Rugby Run Solar Farm | 28 May 2019 | Qld | New Generator
Coopers Gap Wind Farm | 4 June 2019 | Qld | New Generator
Clermont Solar Farm | 18 June 2019 | Qld | New Generator
Yendon Wind Farm | 19 June 2019 | Victoria | New Generator
Finley Solar Farm | 30 July 2019 | NSW | New Generator
Oakey 2 Solar Farm | 3 September 2019 | Qld | New Generator
Two 220 kV CBs at Balranald Substation | 2019-09-04 | NSW | New CBs installed at Balranald. Previous X5/1 and X5/3 lines to become X5 and X3 220 kV transmission lines respectively.
Waddamana - Wild Cattle Hill 220 kV line | 2019-09-25 | Tasmania | New transmission line
Lake Bonney Battery (Generation Mode) | 8 October 2019 | SA | New Generator
Lake Bonney Battery (Load Mode) | 8 October 2019 | SA | New Generator
Barker Inlet generator | 15 October 2019 | SA | New Generator
Grafton East Substation | 2019-10-25 | NSW | New substation Grafton East cut into existing Coffs Harbour – Koolkhan 96H 132kV line forming Coffs Harbour – Grafton East 96H line and Koolkhan – Grafton East 9W0
Haunted Gully Terminal Station | 2019-10-30 | Victoria | Haunted Gully Terminal Station cut into existing Moorabool-Tarrone No 1 500kV line to form Moorabool – Haunted Gully No 1 500 kV line and Haunted Gully – Moorabool No 1 500kV line
Nevertire Solar Farm | 2 December 2019 | NSW | New Generator
Granville Harbour Wind Farm | 3 December 2019 | Tasmania | New Generator
Limondale 2 Solar Farm | 24 December 2019 | NSW | New Generator

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.