## Cover
2020 Wholesale Eelectricity Market (WEM) Electricity Statement of Opportunities (ESOO): tables and data
This spreadsheet contains the tables and data included in the 2020 WEM ESOO publication.
Contact
For further information about the data and graphs contained in this spreadsheet, please contact the Reserve Capacity (WA) team as follows:
| Phone: | (08) 9469 9936
| Email: | wa.capacity@aemo.com.au
Unit of measure
| GW | Gigawatt
| GWh | Gigawatt hour
| kV | Kilovolt
| kW | Kilowatt
| kWh | Kilowatt hour
| MW | Megawatt
| MWh | Megawatt hour
Abbreviations
| ABS | Australian Bureau of Statistics
| AEMO | Australian Energy Market Operator
| APR | Annual Planning Report
| AQP | Applications and Queuing Policy
| BIS Oxford | Bis Oxford Economics
| BOM | Bureau of Meteorology
| CDD | Cooling degree day
| CRC | Certified Reserve Capacity
| CSIRO | Commonwealth Scientific and Industrial Research Organisation
| DER | Distributed energy resources
| DMO | Distribution Market Operator
| DSM | Demand Side Management
| DSO | Distribution System Operator
| DSP | Demand Side Programme
| EDDQ | Expected DSM Dispatch Quantity
| EOI | Expressions of Interest
| ERA | Economic Regulation Authority
| ESOO | Electricity Statement of Opportunities
| ESS | Essential System Service
| EUE | Expected unserved energy
| EV | Electric vehicle
| GEM | Green Energy Markets
| GIA | Generator Interim Access
| GSP | Gross state product
| HDD | Heating degree day
| INSG | Intermittent Non-Scheduled Generator
| IRCR | Individual Reserve Capacity Requirement
| LDC | Load duration curve
| LFAS | Load Following Ancillary Service
| NEM | National Electricity Market
| NCS | Network Control Services
| NSG | Non-Scheduled Generator
| PASA | Projected Assessment of System Adequacy
| POE | Probability of exceedance
| PV | Photovoltaic
| RBP | Robinson Bowmaker Paul
| RCM | Reserve Capacity Mechanism
| RCP | Reserve Capacity Price
| RCR | Reserve Capacity Requirement
| RCT | Reserve Capacity Target
| SG | Scheduled Generator
| SWIS | South West interconnected system
| TSOG | Total Sent Out Generation
| WEM | Wholesale Electricity Market

## Table of contents
Table of contents
Table 1 Reserve Capacity TargetsA
Table 2 Peak demand forecasts for different weather scenarios, expected demand growth (MW)
Table 3 Operational consumption forecastsA for different demand growth scenarios (GWh)
Table 4 Comparison of annual peak demand days, 2012-13 to 2019-20
Table 5 Comparison of underlying peak demand days, 2012-13 to 2019-20
Table 6 Comparison of winter peak demand days, 2012-13 to 2018-19
Table 7 Comparison of minimum demand days, 2014-15 to 2019-20
Table 8 Definitions for key demand and consumption terms in the forecast methodology
Table 9 Key assumptions for low, expected and high demand forecasts
Table 10 Consultant DER forecast to scenario mapping
Table 11 Forecast total number of EVs, 2020-21 to 2029-30 financial years
Table 12 WA GSP (%) forecasts for different economic growth scenarios, 2020-21 to 2029-30 financial years
Table 13 Forecast residential connections growth (%) scenarios, 2020-21 to 2029-30 financial years
Table 14 Reconciliation between actual and forecast 2019-20 summer peak demand (MW)
Table 15 Difference between 10% POE expected scenario forecasts, 2019 WEM ESOO and 2020 WEM ESOO (MW)
Table 16 Residential annual operational consumption forecasts under different growth scenarios, 2020‑21 to 2029-30
Table 17 Business annual operational consumption forecasts under different growth scenarios, 2020‑21 to 2029-30
Table 18 Difference between operational consumption expected scenario forecasts, 2019 WEM ESOO and 2020 WEM ESOO (GWh)
Table 19 Descriptions and methodology for the defined scenario components
Table 20 Reserve Capacity Targets (MW)A
Table 21 Availability Classes (MW)A
Table 22 Capacity outlook in the SWIS, 2020-21 to 2022-23 Capacity Years (MW)A
Table 23 New capacity offered through the EOI compared to capacity certified, 2015-16 to 2022-23 (MW)
Table 24 List of large-scale energy storage trials
Table 25 DER Roadmap actions to be delivered by AEMO during 2020
Table 26 EDDQ, 2020-21 to 2029-30 Capacity Years
Table 27 EDDQ and DSM RCP, 2020-21 to 2029-30 Capacity Year
Table 28 Supply-demand balance, high demand growth scenario (MW)
Table 29 Supply-demand balance, expected demand growth scenario (MW)
Table 30 Supply-demand balance, low demand growth scenario (MW)
Table 31 EUE assessment results
Table 32 Summer peak demand forecasts under the expected demand growth scenario (MW)
Table 33 Summer peak demand forecasts under the high demand growth scenario (MW)
Table 34 Summer peak demand forecasts under the low demand growth scenario (MW)
Table 35 Winter peak demand forecasts under the expected demand growth scenario (MW)
Table 36 Winter peak demand forecasts under the high demand growth scenario (MW)
Table 37 Winter peak demand forecasts under the low demand growth scenario (MW)
Table 38 Minimum demand forecasts under the expected demand growth scenario (MW)
Table 39 Minimum demand forecasts under the high demand growth scenario (MW)
Table 40 Minimum demand forecasts under the low demand growth scenario (MW)
Table 41 Operational consumption forecasts (financial year basis) (GWh)
Table 42 Operational consumption forecasts (Capacity Year basis) (GWh)
Table 43 Scheduled Generators in the SWIS, 2018-19 Capacity Year
Table 44 Non-Scheduled Generators in the SWIS, 2018-19 Capacity Year
Table 45 Registered generation Facilities – existing and committed (MW)
Table 46 Registered DSM Facilities – capability and availability (MW)
Table 47 Amending WEM Rules made by the WA Minister for Energy over the past 12 months
Table 48 WEM Rules commenced over the past 12 months

## Table 1
Table 1 - Reserve Capacity Targets (MW)A
| Capacity Year | 10% POE Peak demand | Intermittent Loads | Reserve margin | Load followingB | Total
| 2020-21C | 4008 | 3 | 331 | 85 | 4427
| 2021-22 C | 4018 | 3 | 331 | 85 | 4437
| 2022-23 | 4002 | 3 | 331 | 85 | 4421
| 2023-24 | 3913 | 3 | 331 | 85 | 4332
| 2024-25 | 3923 | 3 | 331 | 85 | 4342
| 2025-26 | 3964 | 3 | 331 | 85 | 4383
| 2026-27 | 3942 | 3 | 331 | 85 | 4361
| 2027-28 | 3959 | 3 | 331 | 85 | 4378
| 2028-29 | 3908 | 3 | 331 | 85 | 4327
| 2029-30 | 3937 | 3 | 331 | 85 | 4356
A. All figures have been rounded to the nearest integer.
B. See Section 6.2 for further information.
C. With increasing levels of behind-the-meter PV, and large and small scale renewable generation connecting to the SWIS, AEMO expects the Load Following Ancillary Services (LFAS) requirement to increase. Any changes will be reflected in future WEM ESOOs. The new Essential System Services framework (which is part of the WA Government’s Energy Transformation Strategy) is underway, and this may also change the LFAS requirement.
D. Figures have been updated to reflect the current forecasts. However, the RCR of 4,581 MW set in the 2018 WEM ESOO for the 2018 Reserve Capacity Cycle and the RCR of 4,482 MW set in the 2019 WEM ESOO for the 2019 Reserve Capacity Cycle do not change.

## Table 2
Table 2 - Peak demand forecasts for different weather scenarios, expected demand growth (MW)
| Scenario | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 5-year average annual growth | 2029-30 | 10-year average annual growth
| 10% POE | 4008 | 4018 | 4002 | 3913 | 3923 | -0.5% | 3937 | -0.2%
| 50% POE | 3774 | 3782 | 3758 | 3707 | 3684 | -0.6% | 3720 | -0.2%
| 90% POE | 3544 | 3525 | 3520 | 3465 | 3438 | -0.8% | 3492 | -0.2%

## Table 3
Table 3 - Operational consumption forecastsA for different demand growth scenarios (GWh)
| Scenario | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 5-year average annual growth | 2029-30 | 10-year average annual growth
| High | 18000 | 17987 | 17889 | 17966 | 18144 | 0.2% | 19778 | 1.1%
| Expected | 17589 | 17467 | 17208 | 17009 | 16841 | -1.1% | 17029 | -0.4%
| Low | 17082 | 16868 | 16580 | 16289 | 16079 | -1.5% | 15846 | -0.8%
A. Operational consumption forecasts are by financial year.

## Table 4
Table 4 - Comparison of peak demand days, 2012-13 to 2019-20
| Capacity Year | Date | Trading Interval commencing | Peak demand (MW) | Daily maximum temperature (°C) | Time of temperature peak | Rank of dayA
| 2019-20 | 4 February 2020 | 17:30 | 3919 | 43.3 | 14:30 | 1
| 2018-19 | 7 February 2019 | 17:30 | 3256 | 35.8 | 15:00 | 21
| 2017-18 | 13 March 2018 | 17:30 | 3616 | 38.5 | 14:00 | 2
| 2016-17 | 21 December 2016 | 17:00 | 3543 | 42.8 | 14:30 | 2
| 2015-16 | 8 February 2016 | 17:30 | 4004 | 42.6 | 15:00 | 3
| 2014-15 | 5 January 2015 | 15:30 | 3744 | 44.2 | 13:30 | 1
| 2013-14 | 20 January 2014 | 17:30 | 3702 | 38.7 | 15:00 | 7
| 2012-13 | 12 February 2013 | 16:30 | 3739 | 41.1 | 13:00 | 2
A. A rank of 1 indicates the hottest day in the Capacity Year, 2 indicates the second hottest day, and so on.
Source: AEMO, Solcast and BOM.

## Table 5
Table 5 - Comparison of underlying peak demand days, 2012-13 to 2019-20
| Capacity Year | Date of underlying peak | Estimated underlying peak Trading Interval | Estimated underlying peak demand (MW) | Peak demand Trading Interval | Peak demand (MW) | Reduction in peak from PV generation (MW)A | Reduction in peak demand from peak time shift (MW)A | Rank of dayB
| 2019-20 | 4 February 2020 | 17:00 | 4098 | 17:30 | 3919 | 157 | 22 | 1
| 2018-19 | 20 January 2019 C | 14:00 | 3543 | 17:30 | 3256 | 149 | 139 | 1
| 2017-18 | 13 March 2018 | 16:30 | 3750 | 17:30 | 3616 | 65 | 68 | 2
| 2016-17 | 21 December 2016 | 15:30 | 3725 | 17:00 | 3543 | 115 | 67 | 2
| 2015-16 | 8 February 2016 | 16:30 | 4146 | 17:30 | 4004 | 75 | 67 | 3
| 2014-15 | 5 January 2015 | 15:30 | 3862 | 15:30 | 3744 | 118 | 0 | 1
| 2013-14 | 21 January 2014C | 16:30 | 3784 | 17:30 | 3702 | 48 | 34 | 11
| 2012-13 | 12 February 2013 | 16:00 | 3797 | 16:30 | 3739 | 52 | 6 | 2
A. Estimated behind-the-meter PV generation differs from estimations shown in previous ESOOs due to methodology improvements in estimating the solar capacity factor traces. These traces are now sourced from Solcast.
B. A rank of 1 indicates it was the hottest day in the Capacity Year, 2 indicates the second hottest day, and so on.
C. Underlying peak occurred on a different day to peak demand.
Source: AEMO, Solcast and BOM.

## Table 6
Table 6 - Comparison of winter peak demand days, 2012-13 to 2018-19
| Capacity Year | Date | Trading Interval commencing | Peak demand (MW) | Daily minimum temperature (°C) | Daily median temperature (°C) | Daily maximum temperature (°C)
| 2018-19 | 10 June 2018 | 18:00 | 3199 | 8.5 | 14.7 | 19.1
| 2017-18 | 9 August 2018 | 18:30 | 3256 | 7 | 12.8 | 16.8
| 2016-17 | 31 July 2017 | 18:00 | 3419 | 7.5 | 11.2 | 15.7
| 2015-16 | 7 June 2016 | 18:00 | 3366 | 6.5 | 11.3 | 14.9
| 2014-15 | 23 June 2015 | 18:00 | 3135 | 1.8 | 7.5 | 16.8
| 2013-14 | 23 June 2014 | 18:00 | 3217 | 1.3 | 7 | 16
| 2012-13 | 8 July 2013 | 18:00 | 3071 | 2.5 | 7.8 | 18.5
Source: AEMO and BOM.

## Table 7
Table 7 - Comparison of minimum demand days, 2014-15 to 2019-20
| Capacity Year | Date | Trading Interval commencing | Minimum demand (MW) | Estimated impact of PV at time of minimum (MW) | Estimated PV installed capacity (MW) | Estimated PV capacity factor at time of minimum (%)
| 2019-20A | 4 January 2020 | 11:00 | 1138 | 896 | 1305 | 69
| 2018-19 | 29 September 2019 | 11:30 | 1179 | 814 | 1224 | 66
| 2017-18 | 30 September 2018 | 12:30 | 1282 | 612 | 9,89 | 62
| 2016-17 | 23 October 2016 | 3:30 | 1451 | - | 622 | 0
| 2015-16 | 25 October 2015 | 5:30 | 1397 | - | 506 | 0
| 2014-15 | 19 April 2015 | 3:30 | 1444 | - | 455 | 0
A. 2019-20 Capacity Year includes up to 29 February 2020 (maximum data available at time of publication).
Source: AEMO, Solcast and BOM.

## Table 8
Table 8 - Definitions for key demand and consumption terms in the forecast methodology
| Term | Definition
| Demand | The amount of power (in MW) that is consumed on a ‘sent-out’ basis (excluding electricity used by a generatorA) and averaged over a 30-minute period.
| Operational demandB | Demand that is met by all utility-scale generation, excluding the impacts of behind-the-meter PV generation and battery storage. Operational demand includes demand from EVs.
| Underlying demand | Operational demand plus an estimation of behind-the-meter PV generation and the impacts of battery storage.
| Consumption | The amount of electricity (in MWh or gigawatt hours [GWh]) that is used over a period of time, reported on a “sent‑out” basis (excluding electricity used by a generator).
| Operational consumptionC | Electricity consumption that is met by all utility-scale generation. Consumption met by behind‑the‑meter PV generation is not included in this value. Operational consumption includes consumption from EVs.
| Underlying consumption | Operational consumption plus an estimation of behind-the-meter PV generation.
A. This may be called ‘auxiliary load’, ‘parasitic load’, or ‘self-load’, referring to energy generated for use within power stations.
B. Historical operational demand is calculated as the TSOG multiplied by two, to convert non-network-loss-adjusted MWh to MW for a 30‑minute Trading Interval. The historical operational peak demand and minimum demand are identified as the highest and lowest operational demand calculated for a Trading Interval in a Capacity Year, respectively.
C. Historical operational consumption is equal to the TSOG data.

## Table 9
Table 9 - Key assumptions for low, expected and high demand forecasts
|  | Expected | Low | High
Demand drivers
| Economic and population growth forecasts | Expected | Low | High
Developed by BIS Oxford – see Section 4.3.1
| New LILs forecast | Expected | Low | High
Determined by AEMO – see Section 4.3.2
| Residential connections | Expected | Low | High
| Energy efficiency | Expected | Low | High
DER uptake
| Behind-the-meter PV systemsA | Expected | Expected | Expected
| Behind-the-meter battery storage systemsA | Expected | Expected | Expected
| EVsB | Expected | Low | High
A. The behind-the-meter PV and batteries forecasts were developed by the Commonwealth Scientific and Industrial Research Organisation (CSIRO)[1] and Green Energy Markets (GEM)[2]. See Sections 4.2.1 and 4.2.2 for further information.
B. The EV forecasts were developed by CSIRO. See Section 4.2.3 for further information.

## Table 10
Table 10 - Consultant DER forecast to scenario mapping
|  | Expected | Low | High
| Behind-the-meter PV | Average of CSIRO and GEM expected | CSIRO low | GEM high
| Behind-the-meter battery storage | Average of CSIRO and GEM expected | CSIRO low | GEM high
| EVs | CSIRO expected | CSIRO low | CSIRO high

## Table 11
Table 11 - Forecast total number of EVs, 2020-21 to 2029-30 financial years
| Scenario | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
| Expected | 1022 | 1168 | 1373 | 1671 | 3416 | 8002 | 18474 | 36618 | 63382 | 99125
| Low | 988 | 1003 | 1021 | 1043 | 1200 | 1548 | 2281 | 3700 | 6378 | 11261
| High | 1044 | 2741 | 8754 | 31105 | 63311 | 111869 | 177593 | 258399 | 367650 | 506933
Source: CSIRO.

## Table 12
Table 12 - WA GSP (%) forecasts for different economic growth scenarios, 2020-21 to 2029-30 financial years
| Scenario | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
| High | -0.2 | 9.2 | 4.4 | 2.4 | 2.2 | 2.7 | 2.8 | 2.8 | 2.9 | 3
| Expected | -1.1 | 8.1 | 3 | 2.7 | 2.4 | 2.6 | 2.6 | 2.7 | 2.7 | 2.8
| Low | -1.8 | 6.8 | 2.6 | 2.5 | 2.1 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Source: BIS Oxford.

## Table 13
Table 13 - Forecast residential connections growth (%) scenarios, 2020-21 to 2029-30 financial years
| Scenario | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
| High | 1.6 | 1.6 | 2 | 1.9 | 1.9 | 2 | 2.1 | 2 | 2 | 2
| Expected | 1.3 | 1.3 | 1.4 | 1.5 | 1.5 | 1.6 | 1.8 | 1.7 | 1.7 | 1.7
| Low | 1.1 | 1.1 | 0.9 | 1.1 | 1.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2

## Table 14
Table 14 - Reconciliation between actual and forecast 2019-20 summer peak demand (MW)
|  | Forecast peak | Temperature effects | Behind-the-meter PV | Economic/GSP effects | Residuals | Actual peak
| 50% POE | 3758 | 322 | -61 | -6.2 | -94 | 3919
| 10% POE | 4007 | 172 | -61 | -6.2 | -193 | 3919
Source: ACIL Allen and AEMO.

## Table 15
Table 15 - Difference between 10% POE expected scenario forecasts, 2019 WEM ESOO and 2020 WEM ESOO (MW)
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29
| 2020 WEM ESOO forecast | 4008 | 4018 | 4002 | 3913 | 3923 | 3964 | 3942 | 3959 | 3908
| 2019 WEM ESOO forecast | 4063 | 4075 | 4074 | 4078 | 4079 | 4092 | 4117 | 4128 | 4152
| Difference | -55 | -57 | -72 | -165 | -155 | -127 | -175 | -169 | -243

## Table 16
Table 16 - Residential annual operational consumption forecasts under different growth scenarios, 2020 21 to 2029-30 (GWh)
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
| Expected | 4620 | 4515 | 4364 | 4233 | 4114 | 4031 | 3980 | 3972 | 3976 | 3999
| Low | 4609 | 4498 | 4335 | 4185 | 4048 | 3943 | 3855 | 3791 | 3723 | 3661
| High | 4651 | 4561 | 4438 | 4383 | 4354 | 4392 | 4485 | 4633 | 4838 | 5110

## Table 17
Table 17 - Business annual operational consumption forecasts under different growth scenarios, 2020 21 to 2029-30 (GWh)
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
| Expected | 12969 | 12952 | 12845 | 12776 | 12727 | 12741 | 12769 | 12830 | 12918 | 13030
| Low | 12473 | 12370 | 12246 | 12105 | 12031 | 12049 | 12059 | 12089 | 12134 | 12185
| High | 13349 | 13426 | 13450 | 13583 | 13790 | 13819 | 13895 | 14065 | 14396 | 14668

## Table 18
Table 18 - Difference between operational consumption expected scenario forecasts, 2019 WEM ESOO and 2020 WEM ESOO (GWh)
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29
| 2019 WEM ESOO forecast | 18289 | 18151 | 18008 | 17864 | 17775 | 17694 | 17629 | 17569 | 17543
| 2020 WEM ESOO forecast | 17589 | 17467 | 17208 | 17009 | 16841 | 16773 | 16749 | 16803 | 16894
| Difference | -700 | -684 | -800 | -855 | -934 | -921 | -880 | -766 | -649
Source: ACIL Allen and AEMO.

## Table 19
Table 19 - Descriptions and methodology for the defined scenario components
| Component | Description | Methodology
| 10% POE expected peak demand forecast | The level of electricity demand expected to be exceeded once in every 10 years under the expected demand growth scenario. | Described in Chapter 4.
| Reserve margin | Accounts for both of the following: | Calculated as the greater of:
|  | · Annual variability of peak demand in the SWIS. | · 7.6% of the sum of the 10% POE forecast peak demand and the Intermittent Load allowance.
|  | · The failure of the largest generating unit. | · The maximum sent out capacity (measured at 41°C) of the largest generating unitA.
| Intermittent Load allowance | An estimation of the capacity required to cover the forecast cumulative needs of Intermittent Loads, which are excluded from the 10% POE expected peak demand forecast. | An iterative process is used to calculate the forecast maximum possible Intermittent Load levels, which is then adjusted based on the ratio of the RCT to the 10% POE expected peak demand forecast.
| Frequency control allowance | Additional capacity required to provide Minimum Frequency Keeping Capacity and ensure that load following ancillary services (LFAS) are maintained. | LFAS requirementsB are set for the 2019-20 financial year as followsC:
· 85 MW between 5:30 and 19:30.
· 50 MW between 19:30 and 5:30.
AEMO has used 85 MW for the frequency control allowance, since peak demand is expected to fall in the 5:30 to 19:30 period.
A. AEMO considers NewGen Neerabup (330.6 MW, calculated on a sent out basis at 41°C) to be the largest generating unit in the SWIS.
B. With increasing levels of behind-the-meter PV, and large and small scale renewable generation connecting to the SWIS, AEMO expects the LFAS requirement to increase. Any changes will be reflected in future WEM ESOOs. The new Essential System Services framework (which is part of the WA Government’s ETS) is underway, and this may also change the LFAS requirement.
C. LFAS requirements are set annually in the Ancillary Services Report for the WEM. The 2019 Ancillary Services Report for the WEM is available at https://aemo.com.au/-/media/‌files/‌electricity/‌‌wem/data/system-management-reports/2019-ancillary-services-report.pdf?la=en&hash=8C5E02BDCDA8A‌0D54B617627‌00E79AF2.

## Table 20
Table 20 - Reserve Capacity Targets (MW)A
| Capacity Year | 10% POE peak demand | Intermittent LoadsB | Reserve margin | Load followingB,C | Total
| 2020-21D | 4008 | 3 | 331 | 85 | 4427
| 2021-22D | 4018 | 3 | 331 | 85 | 4437
| 2022-23 | 4002 | 3 | 331 | 85 | 4421
| 2023-24 | 3913 | 3 | 331 | 85 | 4332
| 2024-25 | 3923 | 3 | 331 | 85 | 4342
| 2025-26 | 3964 | 3 | 331 | 85 | 4383
| 2026-27 | 3942 | 3 | 331 | 85 | 4361
| 2027-28 | 3959 | 3 | 331 | 85 | 4378
| 2028-29 | 3908 | 3 | 331 | 85 | 4327
| 2029-30 | 3937 | 3 | 331 | 85 | 4356
A. All figures have been rounded to the nearest MW.
B. See Section 6.2 for further information.
C. With increasing levels of behind-the-meter PV, and large and small scale renewable generation connecting to the SWIS, AEMO expects the LFAS requirement to increase. Any changes will be reflected in future WEM ESOOs. The new Essential System Services framework (which is part of the WA Government’s ETS) is underway, and this may also change the LFAS requirement.
D. Figures have been updated to reflect the current forecasts. However, the RCR of 4,581 MW set in in the 2018 WEM ESOO for the 2018 Reserve Capacity Cycle and the RCR of 4,482 MW set in the 2019 WEM ESOO for the 2019 Reserve Capacity Cycle do not change.

## Table 21
Table 21 - Availability Classes (MW)A
|  | 2021-22B | 2022-23
| Minimum capacity required to be provided from Availability Class 1 | 3557 | 3371
| Capacity associated with Availability Class 2 | 880 | 1050
| RCT | 4437 | 4421
A. In general, Availability Class 1 capacity is associated with generation capacity and Availability Class 2 capacity is associated with DSM capacity. See Section 6.4 for further information.
B. These figures reflect the current forecasts. The RCT of 4,482 MW as determined in the 2019 WEM ESOO for the 2021-22 Capacity Year, which set the RCR for the 2019 Reserve Capacity Cycle, remains unchanged. This comprised capacity requirements of 3,657 MW of Availability Class 1 and 825 MW of Availability Class 2.
Source: AEMO and RBP.

## Table 22
Table 22 - Capacity outlook in the SWIS, 2020-21 to 2022-23 Capacity Years (MW)A
| Capacity category | 2020-21 | 2021-22 | 2022-23B
| Generation capacity | 4900 | 4840 | 4645
| · ExistingD | 4808 | 4,807C | 4645
| · CommittedE | 92 | 33 | 0
| DSM capacity | 66 | 85 | 85
| · ExistingD | 66 | 85 | 85
| · CommittedE | 0 | 0 | 0
| Total capacity | 4966 | 4925 | 4730
| RCR | 4581 | 4482 | 4421
| Excess capacity | 385 (8.4%) | 443 (9.9%) | 309 (7.0%)
A. All capacity values are in terms of Capacity Credits, rounded to the nearest integer. Values for the 2020-21 and 2021-22 Capacity Years are Capacity Credits assigned for the 2018 and 2019 Reserve Capacity Cycles, respectively.
B. The capacity outlook for the 2022-23 Capacity Year excludes MUJA_G5 (195 MW of Capacity Credits). All other Facilities are assumed to receive the same quantity of Capacity Credits as for the 2019 Reserve Capacity Cycle.
C. The reduction in existing generation capacity between the 2020-21 and 2021-22 Capacity Years is largely due to year-on-year variation in Relevant Level for Intermittent Non-Scheduled Generators.
D. Existing generation and DSM capacity holds Capacity Credits for the relevant Capacity Year and has held Capacity Credits for a previous Reserve Capacity Cycle.
E. Committed capacity refers to new generation or DSM capacity that holds Capacity Credits for the relevant Capacity Year but has not held Capacity Credits for a previous Reserve Capacity Cycle.

## Table 23
Table 23 - New capacity offered through the EOI compared to capacity certified, 2015-16 to 2022-23 (MW)
|  | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22A, B | 2022-23A
| New capacity offered | 59 | 56 | 0 | 42 | 323 | 10 | 32.4 | 62
| New capacity offered and certified | 0.4 | 0 | 0 | 0 | 65 | 0 | 33 | TBD
| Total other capacity certifiedC | 35 | 18 | 12 | 16 | 0 | 93 | 0 | TBD
A. Estimated Capacity Credit assignment provided by the project proponent.
B. One Facility that was offered through the EOI received a higher level of Capacity Credits than the estimate provided in the EOI.
C. New capacity that was not offered through an EOI but received Capacity Credits for the relevant Capacity Year.

## Table 24
Table 24 - List of large-scale energy storage trials
| Methodology under review | Launch date and storage capacity
| Meadow Springs, Mandurah | October 2018 – 105 kW (420 kWh)
| East Village, Knutsford, Fremantle | March 2019 – 100 kW (670 kWh)
| Falcon, Mandurah | November 2019 – 116 kW (464 kWh)
| Ellenbrook PowerBank 2 trial | February 2020 – 116 kW (464 kWh)

## Table 25
Table 25- DER roadmap actions to be delivered by AEMO during 2020
| Element | Action | Delivery date
| Inverter standards | Deliver improved inverter functions through the Standards Australia national review process for AS/NZS 4777. | October 2020
| Grid response | Review Under Frequency Load Shedding arrangements, and assess implications for AA5 investment program. | June 2020
| Power system operations | Revise system restart arrangements to consider DER. | June 2020
| Distribution network visibility | Deliver a register of static DER data for the SWIS, with processes to support data collection and future DSO functionality. | September 2020
| Distribution System Operator (DSO)/Distribution Market Operator (DMO) | Develop a plan for the establishment of a DSO and DMO in the SWIS, including the identification of roles, functions, costs and practical operations. This plan should include an assessment of the costs and benefits to the system for the establishment of these functions. | December 2020
| DSO/DMO | Identify legislation and regulatory framework requirements including timeframes for development and implementation to establish DSO and DMO functions. | December 2020

## Table 26
Table 26 - EDDQ, 2020-21 to 2029-30 Capacity Years
| Capacity Year | EUE no DSM dispatched (MWh) | EUE DSM dispatched for 200 hours (MWh) | DSM Capacity Credits (MW) | EDDQ (MWh)
| 2020-21 | 0.0000 | 0 | 66 | 0
| 2021-22 | 0.0000 | 0 | 84.5 | 0
| 2022-23 | 0.0605 | 0 | 86 | 0.0007
| 2023-24 | 0.6623 | 0.1611 | 86 | 0.0058
| 2024-25 | 5.1361 | 2.4442 | 86 | 0.0313
| 2025-26 | 0.3123 | 0 | 86 | 0.0036
| 2026-27 | 1.2895 | 0.1491 | 86 | 0.0133
| 2027-28 | 4.1792 | 1.0681 | 86 | 0.0362
| 2028-29 | 5.3643 | 1.5083 | 86 | 0.0448
| 2029-30 | 8.1427 | 2.0894 | 86 | 0.0704
Source: RBP.

## Table 27
Table 27 - EDDQ and DSM RCP, 2020-21 to 2029-30 Capacity Year
| Capacity Year | EUE no DSM dispatched (MWh) | EUE DSM dispatched for 200 hours (MWh) | DSM Capacity Credits (MW) | EDDQ (MWh) | DSM RCP ($/MW)
| 2020-21 | 0.0000 | 0 | 66 | 0 | 16730
| 2021-22 | 0.0000 | 0 | 84.5 | 0 | 16730
| 2022-23 | 0.0605 | 0 | 86 | 0.0007 | 16753.53
| 2023-24 | 0.6623 | 0.1611 | 86 | 0.0058 | 16924.99
| 2024-25 | 5.1361 | 2.4442 | 86 | 0.0313 | 17777.33
| 2025-26 | 0.3123 | 0 | 86 | 0.0036 | 16851.49
| 2026-27 | 1.2895 | 0.1491 | 86 | 0.0133 | 17173.69
| 2027-28 | 4.1792 | 1.0681 | 86 | 0.0362 | 17940.42
| 2028-29 | 5.3643 | 1.5083 | 86 | 0.0448 | 18230.26
| 2029-30 | 8.1427 | 2.0894 | 86 | 0.0704 | 19085.14
Source: RBP.

## Table 28
Table 28 - Supply-demand balance, high demand growth scenario (MW)
| Capacity Year | RCTA | Committed capacity | Balance
| 2020-21 | 4,472 | 4,966 | 494
| 2021-22 | 4,444 | 4,925 | 481
| 2022-23 | 4,445 | 4,730 | 285
| 2023-24 | 4,408 | 4,730 | 322
| 2024-25 | 4,402 | 4,537 | 135
| 2025-26 | 4,463 | 4,537 | 74
| 2026-27 | 4,466 | 4,537 | 71
| 2027-28 | 4,520 | 4,537 | 17
| 2028-29 | 4,499 | 4,537 | 38
| 2029-30 | 4,557 | 4,537 | -20
A. The RCT is calculated based on the 10% POE peak demand forecasts under the high demand growth scenario.

## Table 29
Table 29 - Supply-demand balance, expected demand growth scenario (MW)
| Capacity Year | RCTA | Committed capacity | Balance
| 2020-21B | 4,427 | 4,966 | 539
| 2021-22B | 4,437 | 4,925 | 488
| 2022-23 | 4,421 | 4,730 | 309
| 2023-24 | 4,332 | 4,730 | 398
| 2024-25 | 4,342 | 4,537 | 195
| 2025-26 | 4,383 | 4,537 | 154
| 2026-27 | 4,361 | 4,537 | 176
| 2027-28 | 4,378 | 4,537 | 159
| 2028-29 | 4,327 | 4,537 | 210
| 2029-30 | 4,356 | 4,537 | 181
A. The RCT is calculated based on the 10% POE peak demand forecasts under the expected demand growth scenario.
B. Figures have been updated to reflect the current forecasts. However, the RCR of 4,581 MW set in in the 2018 WEM ESOO for the 2018 Reserve Capacity Cycle and the RCR of 4,482 MW set in the 2019 WEM ESOO for the 2019 Reserve Capacity Cycle do not change.

## Table 30
Table 30 - Supply-demand balance, low demand growth scenario (MW)
| Capacity Year | RCTA | Committed capacity | Balance
| 2020-21 | 4,425 | 4,966 | 541
| 2021-22 | 4,397 | 4,925 | 528
| 2022-23 | 4,402 | 4,730 | 328
| 2023-24 | 4,304 | 4,730 | 426
| 2024-25 | 4,288 | 4,537 | 249
| 2025-26 | 4,329 | 4,537 | 208
| 2026-27 | 4,311 | 4,537 | 226
| 2027-28 | 4,306 | 4,537 | 231
| 2028-29 | 4,269 | 4,537 | 268
| 2029-30 | 4,263 | 4,537 | 274
A. The RCT is calculated based on the 10% POE peak demand forecasts under the low demand growth scenario.

## Table 31
Table 31 - EUE assessment results
| Capacity Year | Operational consumption (MWh)A | 0.002% of operational consumption (MWh) | EUE (MWh) | EUE (%)
| 2020-21 | 17,935,419 | 359 | 0 | 0
| 2021-22 | 17,539,137 | 351 | 0 | 0
| 2022-23 | 17,253,793 | 345 | 0 | 0
| 2023-24 | 16,986,658 | 340 | 0.15 | <0.002
| 2024-25 | 16,828,732 | 337 | 2.22 | <0.002
| 2025-26 | 16,746,365 | 335 | 0 | 0
| 2026-27 | 16,743,152 | 335 | 0 | 0
| 2027-28 | 16,793,621 | 336 | 1.06 | <0.002
| 2028-29 | 16,888,850 | 338 | 1.45 | <0.002
| 2029-30 | 17,033,731 | 341 | 1.92 | <0.002
A. These values are the operational consumption forecasts developed under the expected demand growth scenario; see Chapter 5 for more information.
Source: AEMO and RBP.

## Table 32
Table 32 - Summer peak demand forecasts under the expected demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 4008 | 3774 | 3544
| 2021-22 | 4018 | 3782 | 3525
| 2022-23 | 4002 | 3758 | 3520
| 2023-23 | 3913 | 3707 | 3465
| 2024-25 | 3923 | 3684 | 3438
| 2025-26 | 3964 | 3727 | 3498
| 2026-27 | 3942 | 3719 | 3482
| 2027-28 | 3959 | 3733 | 3491
| 2028-29 | 3908 | 3683 | 3451
| 2029-30 | 3937 | 3720 | 3492
| Average growth | -0.2% | -0.2% | -0.2%

## Table 33
Table 33 - Summer peak demand forecasts under the high demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 4053 | 3804 | 3571
| 2021-22 | 4025 | 3796 | 3545
| 2022-23 | 4026 | 3805 | 3566
| 2023-23 | 3989 | 3752 | 3515
| 2024-25 | 3983 | 3753 | 3519
| 2025-26 | 4044 | 3812 | 3553
| 2026-27 | 4047 | 3844 | 3592
| 2027-28 | 4101 | 3880 | 3620
| 2028-29 | 4080 | 3863 | 3613
| 2029-30 | 4138 | 3940 | 3685
| Average growth | 0.2% | 0.4% | 0.3%

## Table 34
Table 34 - Summer peak demand forecasts under the low demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 4006 | 3768 | 3531
| 2021-22 | 3978 | 3734 | 3490
| 2022-23 | 3983 | 3726 | 3482
| 2023-23 | 3885 | 3658 | 3433
| 2024-25 | 3869 | 3648 | 3404
| 2025-26 | 3910 | 3668 | 3406
| 2026-27 | 3892 | 3657 | 3418
| 2027-28 | 3887 | 3660 | 3415
| 2028-29 | 3850 | 3606 | 3350
| 2029-30 | 3844 | 3615 | 3366
| Average growth | -0.5% | -0.5% | -0.5%

## Table 35
Table 35 - Winter peak demand forecasts under the expected demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 3096 | 3012 | 2929
| 2021-22 | 3092 | 3011 | 2923
| 2022-23 | 3085 | 2997 | 2924
| 2023-23 | 3063 | 2978 | 2892
| 2024-25 | 3062 | 2971 | 2883
| 2025-26 | 3076 | 2988 | 2904
| 2026-27 | 3081 | 2998 | 2916
| 2027-28 | 3089 | 3006 | 2920
| 2028-29 | 3102 | 3019 | 2930
| 2029-30 | 3120 | 3028 | 2949
| Average growth | 0.1% | 0.1% | 0.1%

## Table 36
Table 36 - Winter peak demand forecasts under the high demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 3106 | 3032 | 2954
| 2021-22 | 3121 | 3039 | 2956
| 2022-23 | 3131 | 3042 | 2958
| 2023-23 | 3130 | 3050 | 2964
| 2024-25 | 3163 | 3068 | 2985
| 2025-26 | 3203 | 3114 | 3027
| 2026-27 | 3232 | 3152 | 3068
| 2027-28 | 3282 | 3200 | 3125
| 2028-29 | 3344 | 3248 | 3168
| 2029-30 | 3411 | 3326 | 3233
| Average growth | 1% | 1% | 1%

## Table 37
Table 37 - Winter peak demand forecasts under the low demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 3077 | 2993 | 2914
| 2021-22 | 3056 | 2973 | 2894
| 2022-23 | 3043 | 2959 | 2877
| 2023-23 | 3025 | 2937 | 2845
| 2024-25 | 3009 | 2927 | 2836
| 2025-26 | 3022 | 2936 | 2859
| 2026-27 | 3014 | 2930 | 2850
| 2027-28 | 3015 | 2933 | 2849
| 2028-29 | 3010 | 2926 | 2841
| 2029-30 | 3043 | 2934 | 2844
| Average growth | -0.1% | -0.2% | -0.3%

## Table 38
Table 38 - Minimum demand forecasts under the expected demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 1102 | 997 | 908
| 2021-22 | 991 | 900 | 813
| 2022-23 | 878 | 785 | 699
| 2023-23 | 785 | 697 | 615
| 2024-25 | 680 | 591 | 507
| Average growth | -11.4% | -12.3% | -13.6%

## Table 39
Table 39 - Minimum demand forecasts under the high demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 1115 | 1016 | 925
| 2021-22 | 1013 | 934 | 840
| 2022-23 | 917 | 830 | 738
| 2023-23 | 843 | 753 | 668
| 2024-25 | 756 | 658 | 574
| Average growth | -9.2% | -10.3% | -11.2%

## Table 40
Table 40 - Minimum demand forecasts under the low demand growth scenario (MW)
| Capacity year | 10% POE | 50% POE | 90% POE
| 2020-21 | 1065 | 965 | 878
| 2021-22 | 939 | 860 | 781
| 2022-23 | 825 | 740 | 660
| 2023-23 | 723 | 638 | 563
| 2024-25 | 624 | 533 | 454
| Average growth | -12.5% | -13.8% | -15.2%

## Table 41
Table 41 - Operational consumption forecasts (financial year basis) (GWh)
| Financial year | Expected | High | Low
| 2020-21 | 17589 | 18000 | 17082
| 2021-22 | 17467 | 17987 | 16868
| 2022-23 | 17208 | 17889 | 16580
| 2023-24 | 17009 | 17966 | 16289
| 2024-25 | 16841 | 18144 | 16079
| 2025-26 | 16773 | 18211 | 15993
| 2026-27 | 16749 | 18379 | 15914
| 2027-28 | 16803 | 18698 | 15880
| 2028-29 | 16894 | 19234 | 15857
| 2029-30 | 17029 | 19778 | 15846
| Average growth | -0.4% | 1.1% | -0.8%

## Table 42
Table 42 - Operational consumption forecasts (Capacity Year basis) (GWh)
| Capacity year | Expected | High | Low
| 2020-21 | 17935 | 18025 | 17065
| 2021-22 | 17539 | 17987 | 16812
| 2022-23 | 17254 | 17886 | 16520
| 2023-24 | 16987 | 18037 | 16246
| 2024-25 | 16829 | 18168 | 16064
| 2025-26 | 16746 | 18257 | 15977
| 2026-27 | 16743 | 18456 | 15908
| 2027-28 | 16794 | 18848 | 15874
| 2028-29 | 16889 | 19498 | 15850
| 2029-30 | 17034 | 20120 | 15849
| Average growth | -0.6% | 1.2% | -0.8%

## Table 43
Table 43 - Scheduled Generators in the SWIS, 2018-19 Capacity Year
| Participant | Power station (units included) | Classification | Energy generated |  | Capacity Credits
|  |  |  | GWh | Share (%) | MW | Share (%)
| Alcoa | Alcoa Wagerup | Baseload | 105.09 | 0.61 | 26 | 0.53953
| Alinta Energy | Pinjarra (1 and 2) | Baseload | 1988.19 | 11.52 | 270.5 | 5.6132
|  | Alinta Wagerup (1 and 2) | Mid-merit | 551.17 | 3.19 | 392 | 8.1345
| Bluewaters | Bluewaters (1 and 2) | Baseload | 3143.54 | 18.22 | 434 | 9.006
| Goldfields Power | Parkeston | Mid-merit | 15.89 | 0.09 | 59.4 | 1.2326
| Landfill Gas & Power | Kalamunda | Peaking | 0.01 | 0 | 1.3 | 0.026977
| Merredin Energy | Merredin | Peaking | 0.26 | 0 | 82 | 1.7016
| NewGen | NewGen Neerabup | Mid-merit | 158.8 | 0.92 | 330.6 | 6.8603
|  | NewGen Kwinana | Baseload | 1988.4 | 11.52 | 327.8 | 6.8022
| Southern Cross Energy | Southern Cross | Baseload | 167.93 | 0.97 | 20 | 0.41502
| Synergy | Cockburn | Peaking | 83.73 | 0.49 | 240 | 4.9803
|  | Collie | Baseload | 1278.93 | 7.41 | 317.2 | 6.5823
|  | Kemerton (11 and 12) | Peaking | 47.36 | 0.27 | 310 | 6.4329
|  | Kwinana GT (2 and 3) | Baseload | 872.42 | 5.06 | 197.7 | 4.1025
|  | Muja CD (5 to 8) | Baseload | 3411.25 | 19.77 | 810 | 16.8085
|  | Mungarra (1 and 3)A | Peaking/Mid-merit | 4.11 | 0.02 | 0 | 0
|  | Pinjar (1 to 5, 7) | Peaking | 26.28 | 0.15 | 210 | 4.3577
|  | Pinjar (9 to 11) | Mid-merit | 458.92 | 2.66 | 345 | 7.1592
|  | Perth Power Partnership Kwinana | Baseload | 541.65 | 3.14 | 80.4 | 1.6684
|  | West Kalgoorlie (2 and 3)A | Peaking | 2.5 | 0.01 | 0 | 0
| Tesla | Tesla Picton | Peaking | 0.03 | 0 | 9.9 | 0.20544
|  | Tesla Geraldton | Peaking | 0.05 | 0 | 9.9 | 0.20544
|  | Tesla Kemerton | Peaking | 0.02 | 0 | 9.9 | 0.20544
|  | Tesla Northam | Peaking | 0.02 | 0 | 9.9 | 0.20544
| Tronox | Tiwest Cogeneration | Baseload | 220.75 | 1.28 | 36 | 0.74704
| Western Energy | Perth Energy Kwinana | Mid-merit | 83.56 | 0.48 | 109 | 2.2619
A. Registered Facilities that did not participate in the RCM for the 2018-19 Capacity Year.
B. The Capacity Credits Share (%) is calculated from a total of 4,761.607 MW of Capacity Credits assigned to Scheduled and Intermittent Non-scheduled Generators for the 2018-19 Capacity Year. A total of 4,819.033 MW of Capacity Credits were assigned for the 2018-19 Capacity Year, including 57.426 MW of Capacity Credits assigned to Demand Side Programmes.

## Table 44
Table 44 - Non-Scheduled Generators in the SWIS, 2018-19 Capacity Year
| Participant | Power Station (units included) | Energy Source | Nameplate Capacity (MW) | Energy Generated |  | Capacity Credits
[5 empty] | GWh | Share (%) | MW | Share (%)B
| Alinta Energy | Walkaway | Wind | 89.1 | 346.37 | 2.01 | 26.096 | 0.54152
|  | BadgingarraA | Wind | 130 | 346.08 | 2.01 | 0 | 0
| Blairfox | Karakin | Wind | 5 | 6.17 | 0.04 | 0.824 | 0.017099
|  | Beros Road Wind FarmA | Wind | 9.25 | 0.88 | 0.01 | 0 | 0
|  | WesthillsA | Wind | 5 | 2.24 | 0.01 | 0 | 0
| Clean Tech Energy | Richgro Biogas | Biogas | 2 | 3.21 | 0.02 | 1.654 | 0.034322
| Collgar Wind Farm | Collgar | Wind | 206 | 669.51 | 3.88 | 20.567 | 0.42679
| Denmark Community Windfarm | Denmark Wind Farm | Wind | 1.44 | 5.01 | 0.03 | 0.695 | 0.014422
| EDFW Manager | Emu Downs | Wind/solar | 80 | 280.62 | 1.63 | 28.037 | 0.5818
| Landfill Gas & Power | Red Hill | Biogas | 3.64 | 22.19 | 0.13 | 2.776 | 0.057605
|  | Tamala Park | Biogas | 4.8 | 35.17 | 0.2 | 4.213 | 0.087424
| Merredin Solar Farm | MerredinA | Solar | 100 | 0 | 0 | 0 | 0
| Metro Power Company | Ambri SolarA | Solar | 0.96 | 2.06 | 0.01 | 0 | 0
| Mt. Baker Power Company | Mount Baker | Wind | 2.43 | 5.97 | 0.03 | 0.766 | 0.015895
| Mumbida Wind Farm | Mumbida | Wind | 55 | 195.29 | 1.13 | 10.631 | 0.2206
| Northam Solar Project | Northam | Solar | 9.8 | 11.75 | 0.1 | 4.101 | 0.0851
| Perth Energy | Rockingham | Biogas | 4 | 16.03 | 0.09 | 2.022 | 0.041959
|  | South Cardup | Biogas | 4.16 | 27.39 | 0.16 | 2.954 | 0.061299
| Synergy | Albany | Wind | 21.6 | 44.75 | 0.26 | 7.757 | 0.16097
|  | Grasmere | Wind | 13.8 | 36.02 | 0.21 | 5.074 | 0.10529
|  | Greenough River | Solar | 40 | 22.82 | 0.13 | 2.528 | 0.052459
|  | Bremer Bay | Wind | 0.6 | 1.56 | 0.01 | 0.151 | 0.0031334
|  | Kalbarri | Wind | 1.6 | 3.96 | 0.02 | 0.323 | 0.0067026
| Waste Gas Ressources | Henderson | Biogas | 3 | 13.9 | 0.08 | 1.938 | 0.040216
A. Registered Facilities that did not participate in the RCM for the 2018-19 Capacity Year.
B. The Capacity Credits Share (%) is calculated from a total of 4,761.607 MW of Capacity Credits assigned to Scheduled and Intermittent Non-scheduled Generators for the 2018-19 Capacity Year. A total of 4,819.033 MW of Capacity Credits were assigned for the 2018-19 Capacity Year, including 57.426 MW of Capacity Credits assigned to Demand Side Programmes.

## Table 45
Table 45 - Registered generation Facilities – existing and committed (MW)
| Market Participant | Facility | Capacity Credits (2021-22) | Maximum Capacity
| Alcoa of Australia | ALCOA_WGP | 26 | 26
| Alinta Sales | ALINTA_PNJ_U1 | 136.962 | 143
| Alinta Sales | ALINTA_PNJ_U2 | 136.962 | 143
| Alinta Sales | ALINTA_WGP_GT | 196 | 196
| Alinta Sales | ALINTA_WGP_U2 | 196 | 196
| Alinta Sales | ALINTA_WWF | 17.185 | 89.1
| Alinta Sales | BADGINGARRA_WF1 | 26.621 | 130
| Alinta Sales | YANDIN_WF1A | 36.196 | 211.68
| BEI WWF Pty Ltd as Trustee for WWF Trust | WARRADARGE_WF1A | 30.223 | 180
| Blair Fox | BLAIRFOX_BEROSRD_WF1B | 0 | 9.252
| Blair Fox | BLAIRFOX_KARAKIN_WF1 | 0.486 | 5
| Blair Fox | BLAIRFOX_WESTHILLS_WF3B | 0 | 5
| Bluewaters Power 1 | BW1_BLUEWATERS_G2 | 217 | 217
| Bluewaters Power 2 | BW2_BLUEWATERS_G1 | 217 | 217
| CleanTech Energy | BIOGAS01 | 1.18 | 2
| Collgar Wind Farm | INVESTEC_COLLGAR_WF1 | 15.823 | 206
| Denmark Community Windfarm | DCWL_DENMARK_WF1 | 0.364 | 1.44
| EDWF Manager | EDWFMAN_WF1 | 16.209 | 80
| Goldfields Power | PRK_AG | 59.748 | 68
| Kwinana WTE Project Co | PHOENIX_KWINANA_WTE_G1A | 33 | 36
| Landfill Gas and Power | KALAMUNDA_SG | 1.3 | 1.3
| Landfill Gas and Power | RED_HILL | 2.842 | 3.64
| Landfill Gas and Power | TAMALA_PARK | 4.351 | 4.8
| Merredin Energy | NAMKKN_MERR_SG1 | 82 | 92.6
| Merredin Solar Farm Nominee | MERSOLAR_PV1 | 16.32 | 100
| Metro Power Company | AMBRISOLAR_PV1 | 0.198 | 0.96
| Mt.Barker Power Company | SKYFRM_MTBARKER_WF1 | 0.521 | 2.43
| Mumbida Wind Farm | MWF_MUMBIDA_WF1 | 7.029 | 55
| NewGen Neerabup Partnership | NEWGEN_NEERABUP_GT1 | 330.6 | 342
| NewGen Power Kwinana | NEWGEN_KWINANA_CCG1 | 327.8 | 335
| Northam Solar Project Partnership | NORTHAM_SF_PV1 | 1.798 | 9.8
| Perth Energy | ATLASB | 0 | 0
| Perth Energy | GOSNELLSB | 0 | 0
| Perth Energy | ROCKINGHAM | 2.323 | 4
| Perth Energy | SOUTH_CARDUP | 2.966 | 4.158
| Southern Cross Energy | STHRNCRS_EG | 20 | 23
| SRV AGWF Pty Ltd as trustee for AGWF Trust | ALBANY_WF1 | 5.294 | 21.6
| SRV AGWF Pty Ltd as trustee for AGWF Trust | GRASMERE_WF1 | 3.712 | 13.8
| SRV GRSF Pty Ltd as Trustee for GRSF Trust | GREENOUGH_RIVER_PV1 | 7.377 | 40
| Synergy | BREMER_BAY_WF1 | 0.166 | 0.6
| Synergy | COCKBURN_CCG1 | 240 | 249.7
| Synergy | COLLIE_G1 | 317.2 | 318.3
| Synergy | KALBARRI_WF1 | 0.259 | 1.6
| Synergy | KEMERTON_GT11 | 155 | 154.7
| Synergy | KEMERTON_GT12 | 155 | 154.7
| Synergy | KWINANA_GT2 | 98.5 | 103.2
| Synergy | KWINANA_GT3 | 99.2 | 103.2
| Synergy | MUJA_G5 | 195 | 195.8
| Synergy | MUJA_G6 | 193 | 193.6
| Synergy | MUJA_G7 | 211 | 212.6
| Synergy | MUJA_G8 | 211 | 212.6
| Synergy | MUNGARRA_GT1B | 0 | 39.5
| Synergy | MUNGARRA_GT3B | 0 | 38
| Synergy | PINJAR_GT1 | 30.7 | 38.5
| Synergy | PINJAR_GT10 | 111 | 118.2
| Synergy | PINJAR_GT11 | 124 | 130
| Synergy | PINJAR_GT2 | 30.3 | 38.5
| Synergy | PINJAR_GT3 | 37 | 39.3
| Synergy | PINJAR_GT4 | 37 | 39.3
| Synergy | PINJAR_GT5 | 37 | 39.3
| Synergy | PINJAR_GT7 | 37 | 39.3
| Synergy | PINJAR_GT9 | 111 | 118.2
| Synergy | PPP_KCP_EG1 | 80.4 | 85.7
| Synergy | WEST_KALGOORLIE_GT2B | 0 | 41.2
| Synergy | WEST_KALGOORLIE_GT3B | 0 | 23.3
| Tesla Corporation Management | TESLA_PICTON_G1 | 9.9 | 9.9
| Tesla Geraldton | TESLA_GERALDTON_G1 | 9.9 | 9.9
| Tesla Kemerton | TESLA_KEMERTON_G1 | 9.9 | 9.9
| Tesla Northam | TESLA_NORTHAM_G1 | 9.9 | 9.9
| Tronox Management | TIWEST_COG1B | 0 | 42.1
| Waste Gas Resources | HENDERSON_RENEWABLE_IG1 | 1.632 | 3
| Western Australia Biomass | BRIDGETOWN_BIOMASS_PLANTB | 0 | 40
| Western Energy | PERTHENERGY_KWINANA_GT1 | 109 | 116
A. Candidates for Registration that hold Capacity Credits for the 2021-22 Capacity Year.
B. Registered Facilities that did not participate in the RCM for the 2021-22 Capacity Year.

## Table 46
Table 46 - Registered DSM Facilities – capability and availability (MW)
| Market Participant | Facility | Capacity Credits (2021-22)
| Bluewaters Power 1 | GRIFFINP_DSP_01 | 20
| Synergy | SYNERGY_DSP_04 | 42
| Wesfarmers Kleenheat Gas | PREPWR_DSP_02 | 22.5

## Table 47
Table 47 - Amending WEM Rules made by the WA Minister for Energy over the past 12 months
| Gazette | Gazettal Date | Name | Commencement Date
| 2020/24 | 2020-02-21 | Wholesale Electricity Market Amendment (Reserve Capacity Pricing Reforms) Rules 2019 | 22/02/2020 (8:00 am)
| 2020-02-21 | 2019-10-22 | Wholesale Electricity Market Amendment (AEMO to provide information to the Minister) Rule 2019 | 01/11/2019 (8:00 am)
Source: Rule Change Panel.

## Table 48
Table 48 - WEM Rules commenced over the past 12 months
| ID | Title | Submitted by | Date commenced
| RC_2020_01 | Market Participant Fee calculation manifest error | Rule Change Panel | 2020-03-30
| RC_2013_15 | Outage Planning Phase 2 – Outage Process Refinements | Independent Market OperatorA | 2020-02-01
| RC_2015_03 | Formalisation of the Process for Maintenance Applications | Independent Market OperatorA | 2019-10-01
| RC_2018_06 | Full Runway Allocation of Spinning Reserve Costs | Public Utilities OfficeB | 2019-09-01
| RC_2015_01 | Removal of Market Operation Market Procedures | Independent Market OperatorA | 2019-08-01
| RC_2014_06 | Removal of Resource Plans and Dispatchable Loads | Independent Market OperatorA | 2019-07-01
Source: Rule Change Panel.
A. The Independent Market Operator has been abolished and its functions transferred to AEMO, the ERA, or the Rule Change Panel.
B. Renamed EPWA.