## Important note
IMPORTANT NOTE
This document contains the table information contained in the Power System Design Data Sheets and Power System Setting Data Sheets.
Purpose
This document has been prepared by AEMO as required by clause S5.5.7(a) of the National Electricity Rules (NER), and has effect only for the purposes set out in the NER. The NER and the National ElectricityLaw (Law) prevail over this document to the extent of any inconsistency.
Disclaimer
This document might also contain information which is provided for explanatory purposes. That information does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the Law, the NER, or any other applicable laws, procedures or policies. AEMO has made every reasonable effort to ensure the quality of the information but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
• make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the explanatory information in this document; and
• are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.
Copyright
© 2018 Australian Energy Market Operator Limited. The material in this publication may be used in accordance with the copyright permissions on AEMO’s website.

## Readme
Power System Design Data Sheets
and
Power System Setting Data Sheets
For these draft data sheets, colours have the following meaning:
Prepared by: AEMO Operational Analysis and Engineering
| Version 0.2 |  | = Information has been added or altered compared to the previous Generating System Data Sheets
| 2018-05-14 |  | = This tab is slated for deletion as its contents have been captured elsewhere
Usage Note:
1 | This spreadsheet is provided to assist applicants in preparing their generator connection documents. It is not optional. Revelant tabs must be submitted as part of a connection application.
2 | The "Main" sheet contains a list of all the data sheets. Some typical data sheet "packages" for generating systems have been provided for reference. The applicant should only select the relevant ones based on the actual arrangement of the generating plant.
3 | Each data sheet listed in the "Main" sheet contains a hyperlink which points to the corresponding tab.
4 | All cells in this document are write-protected except those which are allowed to change, e.g. values and remarks. Users can unprotect these sheets but are not encouraged to do so.
5 | The "value" cells are only for information in the specified units. Other information should be entered into the remark field. One typical use is the name of additional reference material.
6 | Additional sheets may be inserted but the plant item(s) should be listed under the "Proposed Plant" column in the "Main" sheet.
7 | This spreadsheet is subject to minor changes without further notice.
8 | Users are strongly encouraged to provide feedback on improvement of this spreadsheet.
9 | Data Sheets must be self-contained. External documents / attachments must not be used. Embed these documents instead.
START - GO TO MAIN sheet

## Main
Section | Data Sheet | Proposed Plant Examples
(Hybrid generating systems to include the relevant datasheets for each sub-component)
|  | Thermal | Hydro | Gas Turbine | Wind power plant (DFIG) | Wind power plant (Converter interface on stator) | Solar power plant (Converter interface) | Battery Energy Storage System (Converter interface) | Hybrid Battery - Solar Power Plant | HVDC (Converter interface) | Pumped Hydro (DFIG)
6 | Generating system (Power Station) | a | a | a | a | a | a | a | a | a | a
7 | Individual Generating Unit Data | a | a | a | a | a | a | a | aa | a | a
8 | Grid Interfaces
8.1 | Transformer (generating unit and generating system) | aa | aa | aa | aa | a | a | a | aa | a | aa
8.2 | AC-DC-AC or DC-AC Converter |  |  |  | a | a | a | a | aa | a | a
9 | Electrical Generator
9.1 | Synchronous Machine (including synchronous condensor) | a | a | a
9.2 | Asynchronous Machine (cage rotor)
9.3 | Asynchronous Machine (variable rotor resistance)
9.4 | Asynchronous Machine (doubly fed) |  |  |  | a | [5 empty] | a
9.5 | Asynchronous Machine (back-to-back converter) |  |  |  |  | a
9.6 | Photovoltaic Generator | [5 empty] | a |  | a
9.7 | Fuel Cell
9.8 | Battery Energy Storage System | [6 empty] | a | a
9.9 | Supercapacitor Energy Storage System |  | (a) |  | (a) | (a) | (a) | (a) |  |  | (a)
10 | Primary Electrical Control systems
10.1 | Synchronous Machine Excitation System | a | a | a |  | (a)
10.2 | Coordinated control of generating units, generating systems and plant | (a) | (a) | (a) | a | a | a | a | aa | a | a
11 | Secondary Electrical Control systems
11.1 | Fault Ride-Through Control systems |  |  |  | a | a | a | a | aa | a | a
11.2 | Other Generating unit control systems | aa | aa | aa | aa | aa | aa | aa | aa | aa | aa
12 | Prime Mover and Primary Mechanical Control systems
12.1 | Steam turbine and turbine governor | a
12.2 | Hydro turbine and turbine governor |  | a | [7 empty] | a
12.3 | Gas turbine and turbine governor |  |  | a
12.4 | Wind turbine aerodynamic model and blade pitch controller model |  |  |  | a | a
12.5 | Diesel and Gas Reciprocating Engine
13 | Secondary Mechanical Control systems
13 | Secondary Mechanical Control systems | aa | aa | aa | aa | aa |  |  |  |  | aa
14 | Prime Mover Mechanical Coupling / Subsynchronous Resonance
14.1 | Shaft Model / Subsynchronous Resonance Frequencies | a | a | a | a | (a) |  |  |  |  | (a)
15 | Auxiliary Equipment
15.1 | Mechanically or electronically switched capacitor , reactor or resistor | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a)
15.2 | Static VAR Compensator, Thyristor Controlled (SVC) | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a)
15.3 | Voltage Source Converter or Current Source Converter, self commutated, or similar (VSC, CSC, DVAR, Statcon or Statcom) | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a)
15.4 | Flywheel | (a) | (a) | (a) | (a) | (a) | (a) | (a) | (a) |  | (a)
15.5 | Asynchronous Motor (generator auxilaries > 1 MW) | a | a | a
16 | Protection systems
16.1 | Synchronous machine protection systems (backups for excitation limiters) | aa | aa | aa |  | (aa)
16.2 | Asynchronous machine protection systems (for generating unit instability) |  |  |  | aa | aa | aa | aa |  | aa | aa
16.4 | Plant level protection systems |  |  |  | aa | aa | aa | aa | aa
16.5 | Other protection systems | aa | aa | aa | aa | aa | aa | aa |  | aa | aa
|  | Legend | a |  |  | = typically required
|  |  | (a) |  |  | = if applicable
|  |  | aa | or | (aa) | = multiple Data Sheets may be required
|  |  | (blank) |  |  | = unlikely but include if required

## S-6
Return to Main
| 6.1.1 | Design Data Sheet
Note: Much of this information needs to be sourced from NSP-provided data.
| Symbol | Data Description | Units | Data Category | Value |  |  |  | Remarks
|  | Connection point to network | Text | S, D
| VCON | Nominal voltage at connection to network | kV | S
| NMC | Total station net maximum capacity (NMC) | MW (sent out) | S, D, R1
|  | System Strength of the supplying network prior to connection of the Generating System, X/R ratio | Value | S, D, R1
|  | Single line diagram of the power station showing primary plant configuration, switching arrangements, earthing arrangements for plant. On the single line diagram or separate diagram, show branch and earthing impedances. | Diagram | D, R1
|  | Diagram showing the various control systems for the generating unit and generating system together with their inputs and outputs and how they link with each other | Diagram | D
|  | Three phase short circuit infeed at the connection point, for the following faults: |  | D, R1
|  | · Balanced (3 phase) |  |  | max |  | min
|  | · Unbalanced (each phase) |  |  |  | Ia | Ib | Ic
line-line, max
line-line, min
line-line-ground, max
line-line-ground, min
line-ground, max
line-ground, min
| UH | · Highest Voltage of a system (as per AS 1824.1) | kV | D,R1
| ZS1 | · Supplying Network Positive-sequence short-circuit impedance as viewed from the connection point | (a + jb) % on 100 MVA base and VCON | D,R1
| ZS2 | · Supplying Network Negative-sequence short-circuit impedance as viewed from the connection point | (a + jb) % on 100 MVA base and VCON | D,R1
| ZS0 | · Supplying Network Zero-sequence short-circuit impedance as viewed from the connection point | (a + jb) % on 100 MVA base and VCON | D,R1
| IKDDO | · initial symmetrical short-circuit current with generating system disconnected | kA (RMS) | D, R1
(peak RMS short circuit current, assuming non-meshed calculation approach for a radial connection)
| IKDD | · initial symmetrical short-circuit current | kA (RMS) | D, R1
(peak RMS short circuit current, assuming non-meshed calculation approach for a radial connection)
| IP | · peak short-circuit current | kA (peak) | D, R1
(maximum possible instantaneous value of the prospective (available) short-circuit current)
| TMIN | · minimum time delay | s | D, R1
(the minimum time from fault inception to the instant of contact separation of the first pole to open of a switching device at or near the connection point – the time as agreed with the network service provider or 60 milliseconds)
| IB | · symmetrical short-circuit breaking current | kA (RMS) | D, R1
(RMS value of an integral cycle of the symmetrical AC component of the prospective short circuit current at TMIN.)
| IK | · steady-state short-circuit current | kA (RMS) | D, R1
(RMS value of the short-circuit current which remains after the decay of the transient phenomena)
| IDC | · decaying DC component of short-circuit current | kA | D, R1
(mean value between the top and bottom envelope of a short-circuit current decaying from an initial value to zero)
| TDC | · decay time for DC component of short-circuit current | s | D, R1
(the time taken for DC current component to fall to 1/2.718 of IDC)
| ZGS1MIN | Minimum positive sequence impedance of Generating System | % on 100 MVA base and VCON | D, R1
| ZGS2MIN | Minimum negative sequence impedance of Generating System | % on 100 MVA base and VCON | D, R1
| ZGS0MIN | Minimum zero sequence impedance of Generating System | % on 100 MVA base and VCON | D, R1
|  | Description of the assumptions used in the derivation of the above quantities. | Text | D, R1
|  | Single phase to ground fault at the connection point | 3 phase current waveform vs time | D,R1
|  | Two Phase to ground fault at the connection point | 3 phase current waveform vs time | D,R1
|  | Three phase fault at the connection point | 3 phase current waveform vs time | D,R1
|  | Description of the assumptions used in the derivation of the above quantities. | Text | D, R1
|  | Plant Harmonic Profile at connection point (at least 2nd to 40th) | Table | R1
| 6.1.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value |  |  |  | Remarks
|  | Operational arrangements for the generating system or within the generating system where this may affect switching configuration or plant operational limits. | Text | D
|  | Connection point over-voltage and under-voltage trip settings and times (if applicable) | kV and seconds | D
|  | Model documentation (in accordance with Rule s5.2.4 (b)), as specified in the Generating System Model Guidelines. |  | D, R1, R2

## S-7
Return to Main
| 7 | Individual Generating Unit Data
| Symbol | Data Description | Units | Data Category | Value | Remarks
| NGU | Number of identical generating units and identification names or numbers | Text | S, D, R1, R2
|  | Type of generating unit (technology), manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
|  | List or table of plant, control systems and protection systems, applicable to this generating unit, for which data has been provided in the Data Sheets. | Text | S, D
| 7.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| MBASE | Rated MVA | MVA | S, D, R1
| IBASE | Base Current | Amps | S, D, R1
| PSO | Rated MW (Sent Out) | MW (sent out) | S, D, R1
| PMAX | Nameplate Rating (Generated) | MW (Gen) | D, R1
| PDMAX | Maximum capacity MW (Generated)
(e.g. short term rating or maximum dispatchable MW)
|  | · generated MW value(s) | MW | S, D, R1
|  | · time(s) that the generated MW applies; and | minutes | S, D, R1
|  | · conditions for which the generated MW applies. | Text (or chart and text)
|  | Maximum ambient operating temperature (if applicable) | degrees C | S, D
| VT | Nominal terminal voltage | kV | D, R1
| PAUX | Auxiliary load at PMAX | MW | S, D, R2
| Qmax | Rated reactive power output at PMAX | MVAr (sent out) | S, D, R1
| PMIN | Minimum Load (ML) | MW (sent out) | S, D, R2
| GCD | Capability chart | Graphical data | D, R1, R2
| ZGU1MIN | Minimum positive sequence impedance | % on 100 MVA base and VT | D, R1
| ZGU2MIN | Minimum negative sequence impedance | % on 100 MVA base and VT | D, R1
| ZGU0MIN | Minimum zero sequence impedance | % on 100 MVA base and VT | D, R1
| SCR | Minimum short circuit ratio(s) at plant LV terminals where the plant remains in stable operation. |  | D, R1
| X/R | For the minimum SCR above, the range of impedance (X/R) ratio where the plant remains in stable operation |  | D, R1
|  | Unit Harmonic Profile at LV terminals (at least 2nd to 40th) | Table | R1
| 7.1.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Operational arrangements for the generating system or within the generating system where this may affect switching configuration or plant operational limits. | Text | D
Note on G12: The corresponding temperature can be provided in the Remark field.
Note on G13: The corresponding temperature can be provided in the Remark field.
Note on G14: The corresponding temperature can be provided in the Remark field.
Note on G18: e.g. the temperature range.
Note on G23: The corresponding temperature can be provided in the Remark field.
Note on G24: Actual operational capability.

## S-8.1
Return to Main
| 8.1 | Transformer (generating unit and generating system)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Transformer identification number | Text
|  | If this is a generating unit transformer, the list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 8.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| GTW | Number of windings |  | S, D
| GTVG | Vector group | Text | S, D
|  | Core configuration | Text | D |  | e.g. Core-type (3 limb), shell-type (5 limb), three-single phase core-type, etc.
| GTRn | Rated MVA of each winding | MVA | S, D, R1
| GTTRn | Principal tap rated voltages | kV/kV | S, D, R1
| GTZ1n | Positive sequence impedance of each winding | (a + jb) % on 100 MVA base and VCON | S, D, R1
(negative sequence impedance [GTZ2n] is expected to be identical to GTZ1n)
| GTZOn |  | (a + jb) % on 100 MVA base and VCON | S, D, R1
Zero sequence impedance of each winding
|  | Earthing arrangement | Text, diagram | S, D
|  | Saturation curve | Diagram | R1 |  | Not optional - must be provided.
|  | Tap changer type, on/off load | On/Off | D
|  | Tapped winding | Text, diagram | S, D, R1
|  | Controlled bus |  | D, R2 |  | HV, MV, LV bus
| GTAPR | Tap change range | kV – kV | S, D
|  | Number of taps | Text | D
| GTAPS | Tap change step size | % | D
|  | Inverse Time characteristic curve for OLTC voltage regulation system (Tap Change Time vs Voltage Deviation) | Diagram | D
|  | OLTC details of control loop described in block diagram form, in accordance with Rule s5.2.4 (b), showing transfer functions of individual elements, measurement units and measurement location. | Diagram | D, R2
| 8.1.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| VREFMAX | Upper voltage reference | V | D, R2
| VREFMIN | Lower voltage reference | V | D, R2
| VREF | Nominal votlage reference | V | D, R2
| GTAPV | Tap change voltage setting range and setpoint (if any) | kV – kV | D, R2
| GTAPD | Tap change voltage deadband | kV | D, R2
| GTAPVL | Tap change high and low voltage interlocks (monitoring non-tapped side voltage or other control signal (specify)) | kV, kV | D, R2
| GTAPT | Minimum tap change cycle time(s) | s, text | D, R2
| RL and XL | Line Drop Compensation or reactive power droop settings | pu , pu | D, R1 | RL:
|  |  | (per unit base on GTRn and nominal voltage of winding where the measurement is taken.) |  | XL:
Note on G15: Additional information such as the tap position for the given impedance can be provided in the remark field.

## S-8.2
Return to Main
| 8.2 | AC-DC-AC or DC-AC Converter
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 8.2.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Converter type and description including manufacturer’s type or product designation | Text | R1, R2
|  | Capability chart | Graphical data | D, R1, R2
|  | Base Converter Current | kA | D, R1
|  | Converter Current Limit | kA | D, R1
| UDC | Nominal DC voltage | V | D, R1
| UDCMAX | Maximum and minimum DC voltage | V | D
UDCMIN
| IDC | Rated DC current | A | D, R1
|  | Voltage angle reference (voltage signal used for reference angle) | Text / Diagram | D
|  | Voltage threshold below which the reference angle tracking stops and internal reference operates (if applicable).This also refers to Phase Locked Loop - freeze threshold e.g. 10%. | kV | D
|  | Functional block diagram of non-grid-side and grid-side converters, including | Diagram | D, R1
· any active power and reactive power control system;
· any AC voltage control scheme;
· any DC voltage and current control systems;
· any limiters (e.g. over-voltage or under-voltage limiters);
· any stabilisation functions.
Non-grid-side Converter (where applicable, e.g. rotor side converter of AC-DC-AC converter):
|  | Converter type | Text | S, D
| UAC | AC voltage as a function of UDC | Text | D, R1
| IAC | Rated AC current | A | D, R1
|  | Switching Frequency | kHz | D, R1
Dynamic braking, crowbar control or protection data (if applicable):
|  | Details of the protection system showing principles of operation, trigger levels, switching times, etc., and conditions for discharging active power to the power system. | Text / Diagram | S, D, R1
|  | Details of how this protection system interfaces to the primary plant or control systems and effects its protection action (e.g. applies resistor or short circuits induction generator rotor inputs or converter capacitor, etc.). | Text / Diagram | D
|  | Crowbar description: | Text / Diagram | D
· its primary function (protecting against what?)
· location (on what plant items and parts of those items does it operate);
· description of conditions (including threshold values) under which it will operate;
· description of conditions (including threshold values and generating unit trip settings) under which it will cease to operate.
| RC | Crowbar protection resistance | % on MBASE and VT | D, R1
| XC | Crowbar protection reactance | % on MBASE and VT | D, R1
Grid-Side Converter:
|  | Converter type | Text | S, D
| UAC | Rated AC voltage | V | D, R1
| IAC | Rated AC current | A | D, R1
|  | Switching Frequency | kHz | D, R1
General:
|  | Details of the voltage and reactive power control system described in functional block diagram form showing: | Functional block diagram | D, R1, R2
· voltage control systems, including deadbands and communication delays;
· converter-level over-voltage limits;
· converter-level under-voltage limits;
· converter-level current limiter (if fitted);
· any other limiters that may restrict voltage control operation.
|  | Details of the frequency control system described in functional block diagram form showing: | Functional block diagram | D, R1, R2
· fast frequency response / synthetic inertia control system and principles
· frequency control systems, including deadbands and communication delays;
· frequency droop mechanisms;
· rate of change of frequency limits;
· over-frequency limits;
· under-frequency limits;
· manual restrictive limiter (if fitted); and
· any other limiters that may restrict frequency control operation.
|  | Details of the active power control system described in functional block diagram form showing: | Functional block diagram | D, R1, R2
· active power control systems, including filtering and communication delays;
· any stabilisation functions, e.g. power system stabiliser (PSS);
· rate of change and limits;
· manual and remote controllers; and
· any other limiters that may restrict active power control operation.
Details of operation and performance during faults, including:
|  | · active current change versus decrease in voltage (LVRT); | Chart | D, R1 |  | V-I curve
|  | · capacitive reactive current change versus decrease in voltage (LVRT); | Chart | D, R1 |  | V-I curve
|  | · active current change versus increase in voltage (HVRT); | Chart | D, R1 |  | V-I curve
|  | · inductive reactive current change versus increase in voltage (HVRT); | Chart | D, R1 |  | V-I curve
|  | · fault ridethrough detection methods and thresholds (e.g. per-phase, positive sequence, any negative sequence dependencies) | Text | D, R1
|  | · positive sequence fault ride through logic | Text | D,R1
|  | · negative sequence fault ride through logic | Text | D,R1
· during the fault, maximum reactive current limit
|  | · after the fault, minimum reactive current limit applied and the duration of the limit/clamp | pu | D,R1
|  | · minimum active power recovery rate on clearance of the fault | pu, sec | D,R1
| 8.2.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.) in accordance with Rule s5.2.4 (b). |  | D, R1, R2
|  | Protection trigger levels and timings. |  | D
|  | Resistance of applied crowbar (if on an asynchronous machine, referred to the stator, if possible) | % of MBASE and VTGEN | D
|  | Voltage thresholds for HVRT and LVRT activation, including hysteresis | pu | D, R1
|  | Maximum Voltage Droop | % | D, R1, R2
(% change in voltage / per-unit change in point of connection voltage)
|  | Normal Voltage Droop | % | D, R1, R2
(% change in voltage / per-unit change in point of connection voltage)
|  | Minimum Voltage Droop | % | D, R1, R2
(% change in voltage / per-unit change in point of connection voltage)
|  | Maximum Voltage Deadband | pu | D, R1
|  | Normal Voltage Deadband | pu | D, R1, R2
|  | Minimum Voltage Deadband | pu | D, R1
|  | Voltage Deadband | pu | D, R1, R2
| RMAX | Maximum Frequency Droop | % | D, R1, R2
(% change in frequency / per-unit change in generating unit output)
| RNORM | Normal Frequency Droop | % | D, R1, R2
(% change in frequency / per-unit change in generating unit output)
| RMIN | Minimum Droop | % | D, R1, R2
(% change in frequency / per-unit change in generating unit output)
|  | Sustained response to frequency change | MW/Hz | D, R1, R2
|  | Non-sustained response to frequency change | MW/Hz | D, R1, R2
| FDBMAX | Maximum Frequency Dead band | Hz | D, R1
| FDBN | Normal Frequency Deadband | Hz | D, R1, R2
| FDBMIN | Minimum Frequency Deadband | Hz | D, R1
| PDB | MW Frequency Deadband | MW | D, R1, R2
|  | · raise MW output | MW/s | D, R1, R2
|  | · lower MW output | MW/s | D, R1, R2
|  | Active Power setpoint rate of change maximum | MW/s | D, R1
|  | Active Power setpoint rate of change minimum | MW/s | D, R1
|  | Active Power setpoint rate of change (raise) | MW/s | D, R1, R2
|  | Active Power setpoint rate of change (lower) | MW/s | D, R1, R2
|  | Details of settings relating to operation and performance during faults, including: | Text | D, R1
|  | · active current decrease versus decrease in voltage (LVRT); | % | D, R1
|  | · capacitive reactive current increase versus decrease in voltage (LVRT); | % | D, R1
|  | · active current decrease versus increase in voltage (HVRT); | % | D, R1
|  | · inductive reactive current increase versus increase in voltage (HVRT); | % | D, R1
|  | Hardware / firmware sampling time for fault detection | µs / ms | D, R1
|  | Settings for multiple-fault protection limitations, including: |  | D, R1
|  | · heat dissipation across the dynamic braking resistors (if applicable); | Text | D, R1
|  | · capability of auxiliary supplies, e.g. uninterrupted power supply; | Text | D, R1
|  | · torsional stress protection on shaft drive train and prime mover (if applicable); | Text | D, R1
|  | · protection associated with thermal design limits of the integral assembly of the plant; and | Text | D, R1
|  | · any other relevant electrical, mechanical or thermal protection. | Text | D, R1

## S-9.1
Return to Main
| 9.1 | Synchronous Machine (including synchronous condensor)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| VTGEN | Nominal terminal voltage | kV | D, R1
| MBASEGEN | Synchronous machine nameplate rating (MVA) | MVA | S, D, R1
| GCD | Capability chart | Graphical data | D, R1
| Q+PMAX | Maximum lagging Reactive power at PMAX | MVAr export | S, D, R2
| Q+PMIN | Maximum lagging Reactive power at PMIN | MVAr export | S, D, R2
| Q-PMAX | Maximum leading Reactive power at PMAX | MVAr import | S, D, R2
| Q-PMIN | Maximum leading Reactive power at PMIN | MVAr import | S, D, R2
| Q+OEX | Maximum lagging short term Reactive power capability at PMAX, VTGEN and rated speed (before over-excitation limiter action) | MVAr export | D, R1
| Hgen | Synchronous machine inertia constant (excluding prime mover inertia) | MWs/MBASE | D, R1, R2
| NP | Number of poles | Text | S, D
| GSCR | Short circuit ratio |  | D, R1
| ISTATOR | Rated stator current | A | D, R1
| IROTOR | Rated rotor current at rated MVA and power factor, rated terminal voltage and rated speed | A | D, R1, R2
| VROTOR | Rotor voltage at which IROTOR is achieved | V | D, R1, R2
| VF | DC field voltage at VTGEN and rated speed with unit unsynchronised | V | D, R1, R2
| IF | DC field current at VTGEN and rated speed with unit unsynchronised | A | D, R1, R2
| RA | Stator resistance | % on MBASE and VTGEN | S, D, R1, R2
|  | (at normal or typical operating temperature – specify temperature) | (temperature in °C)
| RF | Rotor resistance | % on MBASE and VTGEN | S, D, R1, R2
|  | (at normal or typical operating temperature – specify temperature) | (temperature in °C)
| XL | Stator leakage reactance | % on MBASE and VTGEN | D, R1, R2
| X2 | Negative sequence reactance | % on MBASE and VTGEN | D, R1
| Z0 | Zero sequence impedance | (a+jb) % on MBASE and VTGEN | D, R1
(including any neutral earthing impedance)
| XD | Direct axis unsaturated synchronous reactance | % on MBASE and VTGEN | S, D, R1, R2
| XDD | Direct axis unsaturated transient reactance | % on MBASE and VTGEN | S, D, R1, R2
| XDDD | Direct axis unsaturated sub-transient reactance | % on MBASE and VTGEN | S, D, R1, R2
| XQ | Quadrature axis unsaturated synchronous reactance | % on MBASE and VTGEN | D, R1, R2
| XQQ | Quadrature axis unsaturated transient reactance | % on MBASE and VTGEN | D, R1, R2
| XQQQ | Quadrature axis unsaturated sub-transient reactance | % on MBASE and VTGEN | D, R1, R2
| TD0 | Direct axis open circuit transient time constant | s | S, D, R1, R2
| TDD0 | Direct axis open circuit sub-transient time constant | s | S, D, R1, R2
| TKD | Direct axis damper leakage time constant | s | S, D, R1, R2
| TQ0 | Quadrature axis open circuit transient time constant | s | D, R1, R2
| TQQ0 | Quadrature axis open circuit sub-transient time constant | s | D, R1, R2
| GOCC | Open circuit saturation characteristic | Graphical data | R1
| S10 | Saturation Parameter at 1.0pu terminal voltage on GOCC (the ratio between measured voltage and the air-gap line). |  | R1
| S12 | Saturation Parameter 1.2pu terminal voltage on GOCC(the ratio between measured voltage and the air-gap line). |  | R1
| Xp | Potier Reactance | % on MBASE and VTGEN | R1
| Agf | Air Gap Factor | % on MBASE and VTGEN | R1
| GSCC | Short circuit saturation characteristic | Graphical data | R1
| GZPC | Zero power factor curve | Graphical data | R1
Note on G18: Additional information such as the rotor type (salient/round) can be provided in the remark field.
Note on G25: resistance value
Note on G26: temperature
Note on G27: resistance
Note on G28: temperature

## S-9.2
Return to Main
| 9.2 | Asynchronous Machine (cage rotor)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.2.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| VTGEN | Nominal terminal voltage | kV | D, R1
| MBASEGEN | Asynchronous machine nameplate rating (MVA) | MVA | S, D, R1
| QN | Reactive power consumption over range of asynchronous machine output (0 to PMAX) at VTGEN | Chart | D, R1, R2
(MVAr vs. MW)
| Hgen | Asynchronous machine and gearbox inertia constant (excluding prime mover inertia) | MWs/MBASE | D, R1, R2
| NP | Number of poles |  | S, D
| SLIP | Rated slip |  | S, D, R1
| RS | Stator resistance | % on MBASE and VTGEN | S, D, R1, R2
|  | (at normal or typical operating temperature – specify temperature) | (temperature in °C)
| XS | Stator leakage reactance | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| RM | Iron loss resistance, referred to the stator | % on MBASE and VTGEN | S, D, R1, R2
| XM | Magnetizing reactance, referred to the stator | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| RR | Rotor resistance at rated slip, referred to the stator | % on MBASE and VTGEN | D, R1, R2
| XR | Rotor leakage reactance, referred to the stator | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| R0 | Zero sequence resistance | % on MBASE and VTGEN | D, R1, R2
| X0 | Zero sequence reactance | % on MBASE and VTGEN | D, R1, R2
| R2 | Negative sequence resistance | % on MBASE and VTGEN | D, R1
| X2 | Negative sequence reactance | % on MBASE and VTGEN | D, R1
|  | Magnetising curve (voltage versus current) | Chart | D, R1
|  | Speed (slip) vs torque (power) curve(s) | Chart | D, R1
|  | Equivalent circuit noting location of equivalent impedances | Chart | D, R1
Note on F13: For R2 test purposes, the value of Hgen may be verified in combination with any relevant prime-mover inertia.
Note on G16: resistance
Note on G17: temperature

## S-9.3
Return to Main
| 9.3 | Asynchronous Machine (variable rotor resistance)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.3.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| VTGEN | Nominal terminal voltage | kV | D, R1
| MBASEGEN | Asynchronous machine nameplate rating (MVA) | MVA | S, D, R1
| QN | Reactive power consumption over range of asynchronous machine output (0 to PMAX) at VTGEN | Chart | D, R1, R2
(MVAr vs. MW)
| Hgen | Asynchronous machine and gearbox inertia constant (excluding prime mover inertia) | MWs/MBASE | D, R1, R2
| NP | Number of poles | Text | S, D
| SLIP | Rated slip |  | S, D, R1
| RS | Stator resistance | % on MBASE and VTGEN | S, D, R1, R2
|  | (at normal or typical operating temperature – specify temperature) | (temperature in °C)
| XS | Stator leakage reactance | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| RM | Iron loss resistance, referred to the stator | % on MBASE and VTGEN | S, D, R1, R2
| XM | Magnetizing reactance, referred to the stator | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| RR | Rotor resistance at rated slip, referred to the stator | % on MBASE and VTGEN | D, R1, R2
| XR | Rotor leakage reactance, referred to the stator | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| RRR | Rotor resistance range, referred to the stator | % on MBASE and VTGEN | D, R1
| R0 | Zero sequence resistance | % on MBASE and VTGEN | D, R1
| X0 | Zero sequence reactance | % on MBASE and VTGEN | D, R1
| R2 | Negative sequence resistance | % on MBASE and VTGEN | D, R1
| X2 | Negative sequence reactance | % on MBASE and VTGEN | D, R1
| Vlr | Locked rotor voltage with open rotor terminals | V | D, R1
|  | Magnetising curve (voltage versus current) | Chart | D, R1
|  | Speed (slip) vs torque (power) curve(s) | Chart | D, R1
These curves to show effect of variable rotor resistance
|  | Equivalent circuit noting location of equivalent impedances | Chart | D, R1
Note on F13: For R2 test purposes, the value of Hgen may be verified in combination with any relevant prime-mover inertia.

## S-9.4
Return to Main
| 9.4 | Asynchronous Machine (doubly fed)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.4.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| VTGEN | Nominal terminal voltage | kV | D, R1
| MBASE | Asynchronous machine nameplate rating (MVA) | MVA | S, D, R1
| GCD | Capability chart | Graphical data | D, R1, R2
|  | Output power characteristics or capability diagram as a function of wind speed, ambient temperature and any other relevant parameters; | Text, Charts | D, R1
| Q+PMAX | Maximum lagging Reactive power at PMAX | MVAr export | S, D, R2
| Q+PMIN | Maximum lagging Reactive power at PMIN | MVAr export | S, D, R2
| Q-PMAX | Maximum leading Reactive power at PMAX | MVAr import | S, D, R2
| Q-PMIN | Maximum leading Reactive power at PMIN | MVAr import | S, D, R2
| Hgen | Asynchronous machine and gearbox inertia constant (excluding prime mover inertia) | MWs/MBASE | D, R1
| NP | Number of poles | Text | S, D
| SLIP | Slip at PMAX |  | S, D, R1, R2
| RS | Stator resistance | % on MBASE and VTGEN | S, D, R1, R2
| XS | Stator leakage reactance | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| RM | Iron loss resistance, referred to the stator | % on MBASE and VTGEN | S, D, R1, R2
| XM | Magnetizing reactance, referred to the stator | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| RR | Rotor resistance at rated slip, referred to the stator | % on MBASE and VTGEN | D, R1, R2
| XR | Rotor leakage reactance, referred to the stator | % on MBASE and VTGEN
|  | · unsaturated and |  | S, D, R1
|  | · at VTGEN |  | S, D, R1, R2
| R0 | Zero sequence resistance | % on MBASE and VTGEN | D, R1
| X0 | Zero sequence reactance | % on MBASE and VTGEN | D, R1
| R2 | Negative sequence resistance | % on MBASE and VTGEN | D, R1
| X2 | Negative sequence reactance | % on MBASE and VTGEN | D, R1
| Vlr | Locked rotor voltage with open rotor terminals | V | D, R1
|  | Magnetising curve (voltage versus current) | Chart | D, R1
|  | Equivalent circuit noting location of equivalent impedances | Chart | D, R1
| 9.4.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.) in accordance with Rule s5.2.4 (b). | Units to be specified | D, R1, R2

## S-9.5
Return to Main
| 9.5 | Asynchronous Machine (back-to-back converter)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.5.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| VTGEN | Nominal terminal voltage | kV | D, R1
| MBASE | Asynchronous machine nameplate rating (MVA) | MVA | S, D, R1
| GCD | Capability chart | Graphical data | D, R1, R2
| MBASEGEN | Nameplate rating of generating unit | MW | S, D, R1
|  | Description of technical characteristics including (where relevant): | Text, Charts | D
· plant ratings;
|  | · output power characteristics or capability diagram as a function of wind speed, ambient temperature and any other relevant parameters; |  | D, R1
|  | · rate of change limits on power controllers (e.g. active power ramp rate, pitching limitations); |  | D, R1
|  | · performance under fault conditions (e.g. for a fault at the connection point and for more remote faults, including the performance of fault ride-through control systems and multiple fault ride-though limitations). |  | D, R1
|  | Details of plant and control systems in functional block diagram form, in accordance with Rule s5.2.4 (b), including: | Text, Charts
· dc power control systems;
· inner and outer control loops;
· fault ride-through control systems
| 9.5.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.) in accordance with Rule s5.2.4 (b). | Units to be specified | D, R1, R2

## S-9.6
Return to Main
| 9.6 | Photovoltaic Generator
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.6.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| MBASEGEN | Nameplate rating of generating unit | MW | S, D, R1
| GCD | Capability chart | Graphical data | D, R1, R2
| VTGEN | Nominal terminal voltage | kV | D, R1
|  | Description of technical characteristics including (where relevant): | Text, Charts | D
· cell array configuration;
· presence of a DC/DC switching stage
· plant ratings;
· cell or cell array I-V curve and details of power point tracking (if applicable)
|  | · output power characteristics or capability diagram as a function of insolation, cell array terminal voltage, ambient temperature and any other relevant parameters; |  | D, R1
|  | · rate of change limits on power controllers (e.g. active power ramp rate, maximum power point tracker, sun tracking control systems); |  | D, R1
|  | · performance under fault conditions (e.g. for a fault at the connection point and for more remote faults, including the performance of fault ride-through control systems and multiple fault ride-though limitations). |  | D, R1
|  | Details of plant and control systems in functional block diagram form, in accordance with Rule s5.2.4 (b), including: | Text, Charts
· dc power control systems;
· inner and outer control loops;
· fault ride-through control systems
| 9.6.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.) in accordance with Rule s5.2.4 (b). | Units to be specified | D, R1, R2

## S-9.7
Return to Main
| 9.7 | Fuel Cell
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.7.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| MBASEGEN | Fuel cell group (generating unit) nameplate rating | MW | S, D, R1
|  | Description of technical characteristics including (where relevant): | Text, Charts | D
· cell array configuration;
· plant ratings;
· cell or cell array power characteristics and details of power controller;
|  | · output power capability diagram as a function of fuel flow, cell array terminal voltage, ambient temperature and any other relevant parameters; |  | D, R1
|  | · rate of change limits on power controllers; |  | D
· performance under fault conditions (e.g. for a fault at the connection point and for more remote faults, including the performance of an fault ride-through control systems).
|  | Functional block diagram descriptions, in accordance with Rule s5.2.4 (b), of control systems for: | Graphical | D, R1
· dc power control systems;
· if a converter is integral to the array, active power and reactive power control systems and voltage control systems;
· fault ride-through control systems (if applicable)
| 9.7.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.), in accordance with Rule s5.2.4 (b). | Units to be specified | D, R1, R2

## S-9.8
Return to Main
| 9.8 | Battery Energy Storage System
Note: Potential SRAS services are required to provide frequency controller data for both grid following and grid forming modes of operation
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of units to which this information applies. | Text | S, D,R1,R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.8.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| BASE | Nameplate rating | MVA | S, D, R1
| VNOM | Rated voltage | kV | S, D
| EMAX | Nominal capacity | MWh | D, R1, R2
| SCD | Capability diagram | Chart | S, D, R1
(e.g. active power versus voltage)
|  | Number of individual inverters and battery controllers |  | D, R1
|  | Number of individual batteries |  | D, R1
|  | Individual battery capacity | kWh | D, R1
|  | Individual battery nominal voltage | kV | D, R1
|  | Individual battery rated voltage | kV | D, R1
|  | Individual battery rated current | A | D, R1
|  | Presence of a DC/DC switching stage |  | D, R1
|  | Output power capability diagram as a function of battery terminal voltage, ambient temperature and any other relevant parameters; | Text / Diagram | D, R1
|  | Description of the control system showing principles of operation, trigger levels, switching times, etc., and conditions for discharging active power to the power system. | Text / Diagram | S, D, R1
|  | Details of the control system in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Details of how this controller interfaces with the primary electrical or mechanical control systems (if applicable), or how this controller effects its control action. | Text / Diagram | D
| 9.8.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). | Functional block diagram | D, R1, R2

## S-9.9
Return to Main
| 9.9 | Supercapacitor Energy Storage System
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of units to which this information applies. | Text | S, D,R1,R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 9.9.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| BASE | Nameplate rating | MVA | S, D, R1
| VNOM | Rated voltage | kV | S, D
| EMAX | Nominal capacity | MWh | D, R1, R2
| SCD | Capability diagram | Chart | S, D, R1
(e.g. active power versus voltage)
|  | Number of individual capacitors |  | D, R1
|  | Total capacitance | F | D, R1
|  | Capacitors rated voltage | kV | D, R1
|  | Capacitors rated current | kA | D, R1
|  | Output power capability diagram as a function of capacitor voltage, ambient temperature and any other relevant parameters; | Text / Diagram | D, R1
|  | Description of the control system showing principles of operation, trigger levels, switching times, etc., and conditions for discharging active power to the power system. | Text / Diagram | S, D, R1
|  | Details of the control system in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Details of how this controller interfaces with the primary electrical or mechanical control systems (if applicable), or how this controller effects its control action. | Text / Diagram | D
| 9.9.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). | Functional block diagram | D, R1, R2

## S-10.1
Return to Main
| 10.1 | Synchronous Machine Excitation System
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 10.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| VCEIL | Rotor voltage capable of being supplied for 5s at rated voltage (VTGEN) and rated speed | V | D, R1
| VFMIN | Minimum field voltage | V | D, R1
|  | Maximum rate of change of field voltage | Rising V/s | D, R1
|  | Maximum rate of change of field voltage | Falling V/s | D, R1
|  | Exciter description including type, ratings, connection schematic, source of any external supplies, etc. | Text | D, R1
|  | If applicable, exciter saturation curve over 50%-120% of rated voltage. | Diagram | D, R1
|  | Details of the excitation control system described in functional block diagram form showing: | Functional block diagram | S, D, R1
· voltage control systems (AVR);
· power system stabiliser (PSS);
· exciter;
· reactive current or reactive power compensation (if fitted)
(e.g. Load drop compensation/VAr sharing, also referred to as line drop compensation or reactive power droop);
· over-excitation limiter;
· under-excitation limiter;
· stator current limiter (if fitted);
· flux (V/f) limiter (if fitted);
· manual restrictive limiter (if fitted); and
· any other limiters that may restrict excitation system operation.
|  | Details of excitation control system components failover (e.g. for multiple AVR channels, or AVR to manual control) or generator trip, describing conditions that cause the failover or trip. | Text | D, R1
| 10.1.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | DC gain of excitation control loop | V/V | D, R1
|  | Active power operating range of the generating unit when the PSS is in operation. |  | D, R1
All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, etc.) for:
|  | · voltage control systems (AVR); |  | D, R2
|  | · power system stabiliser; |  | D, R2
|  | · exciter; |  | D, R2
|  | · reactive current or reactive power compensation; |  | D, R2
|  | · over-excitation limiter; |  | D, R2
|  | · under-excitation limiter; |  | D, R2
|  | · stator current limiter; |  | D, R2
|  | · flux (V/f) limiter; and |  | D, R2
|  | · any other limiters that may restrict excitation control system operation. |  | D, R2

## S-10.2
Return to Main
| 10.2 | Coordinated control of generating systems and plant (i.e. Power Plant Controller & other coordinated control systems)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 10.2.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the control system showing principles of operation, trigger levels, etc. | Text / Diagram | S, D, R1
|  | Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Details of how this controller interfaces with other control systems or directly to generating system plant (if applicable), or how this controller effects its control action. | Text / Diagram | D
|  | Details of the voltage and reactive power control system described in functional block diagram form showing: | Functional block diagram | D, R1, R2
· voltage control systems, including deadbands and communication delays;
· maximum and minimum dispatchable voltage limitations;
· reactive current or reactive power compensation (if fitted)
(e.g. Load drop compensation/VAr sharing, also referred to as line drop compensation or reactive power droop);
· voltage droop mechanism;
· over-voltage limits;
· under-voltage limits;
· central controller command halt trigger (e.g. LVRT voltage);
· current limiter (if fitted);
· manual restrictive limiter (if fitted); and
· any other limiters that may restrict voltage control operation.
|  | Details of the frequency control system described in functional block diagram form showing: | Functional block diagram | D, R1, R2
· frequency control systems, including deadbands and communication delays;
· frequency droop mechanisms;
· rate of change of frequency limits;
· over-frequency limits;
· under-frequency limits;
· manual restrictive limiter (if fitted); and
· any other limiters that may restrict frequency control operation.
|  | Details of the active power control system described in functional block diagram form showing: | Functional block diagram | D, R1, R2
· active power control systems, including filtering and communication delays;
· rate of change and limits;
· manual and remote controllers; and
· any other limiters that may restrict active power control operation.
| 10.2.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| GCD | Capability chart (as applied by P-Q or P-V control system) | Graphical data | D, R2
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2
|  | Maximum Voltage Droop | % | D, R1, R2
(% change in voltage / per-unit change in point of connection voltage)
|  | Normal Voltage Droop | % | D, R1, R2
(% change in voltage / per-unit change in point of connection voltage)
|  | Minimum Voltage Droop | % | D, R1, R2
(% change in voltage / per-unit change in point of connection voltage)
|  | Maximum Voltage Deadband | pu | D, R1
|  | Normal Voltage Deadband | pu | D, R1, R2
|  | Minimum Voltage Deadband | pu | D, R1
|  | Voltage Deadband | pu | D, R1, R2
| RMAX | Maximum Frequency Droop | % | D, R1, R2
(% change in frequency / per-unit change in generating unit output)
| RNORM | Normal Frequency Droop | % | D, R1, R2
(% change in frequency / per-unit change in generating unit output)
| RMIN | Minimum Droop | % | D, R1, R2
(% change in frequency / per-unit change in generating unit output)
|  | Sustained response to frequency change | MW/Hz | D, R1, R2
|  | Non-sustained response to frequency change | MW/Hz | D, R1, R2
| FDBMAX | Maximum Frequency Dead band | Hz | D, R1
| FDBN | Normal Frequency Deadband | Hz | D, R1, R2
| FDBMIN | Minimum Frequency Deadband | Hz | D, R1
| PDB | MW Frequency Deadband | MW | D, R1, R2
|  | · raise MW output | MW/s | D, R1, R2
|  | · lower MW output | MW/s | D, R1, R2
|  | Active Power setpoint rate of change maximum | MW/s | D, R1
|  | Active Power setpoint rate of change minimum | MW/s | D, R1
|  | Active Power setpoint rate of change (raise) | MW/s | D, R1, R2
|  | Active Power setpoint rate of change (lower) | MW/s | D, R1, R2

## S-10.3
Return to Main
| 10.3 | DC Current Regulator
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 10.3.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of control system including functional block diagram, in accordance with Rule s5.2.4 (b). | Functional Block Diagram/Text | D, R1, R2
| 10.3.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2

## S-11.1
Return to Main
| 11.1 | Fault Ride-Through Control systems
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 11.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the fault ride through control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Equipment limitations for multiple fault ride-through (time, number, etc.) | Text | D, R1
Low Voltage Ride Through
|  | Details of the fault ride through control system showing principles of operation, trigger levels, etc. | Text / Diagram | S, D, R1
|  | Details of the fault ride through control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
High Voltage Ride Through
|  | Details of the fault ride through control system showing principles of operation, trigger levels, etc. | Text / Diagram | S, D, R1
|  | Details of the fault ride through control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
| 11.1.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Setting for maximum permitted number of consecutive voltage disturbances to ride through. | Text | S, D, R1
|  | Time Setting for maximum permitted number of consecutive voltage disturbances to ride through. | Text | S, D, R1
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2
Note on F22: Notes: The ‘R2’ data provision is not necessary, provided that ‘R1’ data is available that is derived from an off-site test that is the application of a fault, where the: • fault applied is a 2 phase-ground or 3-phase fault equivalent to what might be experienced by the generating unit installed on-site; • post-fault fault level is reasonably representative of, or lower than, the post-fault fault level that the generating unit would experience on-site (assuming all generating units of the generating system operated the same way); • generating unit tested is identical to the ones being installed on-site; • generating unit tested has identical control system settings to the ones being installed on-site, or the difference in settings can be translated into appropriate model parameter values applicable to the generating unit being installed on site; and • test and associated documentation clearly demonstrate the features and settings of the fault-ride through control system.

## S-11.2
Return to Main
| 11.2 | Other Generating unit control systems
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 11.2.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the control system showing principles of operation, trigger levels, etc. | Text / Diagram | S, D, R1
|  | Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Details of how this controller interfaces with other control systems or directly to generating system plant (if applicable), or how this controller effects its control action. | Text / Diagram | D
| 11.2.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2

## S-11.3
Return to Main
| 11.3 | Generating System Control systems (coordinated control of generating system plant)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 11.3.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the control system showing principles of operation, trigger levels, etc. | Text / Diagram | S, D, R1
|  | Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Details of how this controller interfaces with other control systems or directly to generating system plant (if applicable), or how this controller effects its control action. | Text / Diagram | D
| 11.3.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2

## S-12.1
Return to Main
| 12.1 | Steam turbine and turbine governor
Note: Potential SRAS services are required to provide the following data for both droop and isochronous modes of operation
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
|  | If this is the steam cycle part of a combined cycle gas turbine, list the generating unit(s) that forms the gas cycle part of the generating system and describe the power output relationship between the cycles. | Text / Chart | D
| 12.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Description of steam turbine configuration (e.g. cross compound, single reheat) | Text | D
|  | Functional block diagram for turbine governor and turbine model, in accordance with Rule s5.2.4 (b). | Diagram | D
Power fractions and rated power(s) (whichever apply):
| Symbol | Data Description | Units | Data Category | Value | Remarks
| FVHP | Very high pressure turbine power fraction | Per-unit of PMAX | D, R2
| FHP | High pressure turbine power fraction | Per-unit of PMAX | D, R2
| FIP | Intermediate pressure turbine power fraction | Per-unit of PMAX | D, R2
| FLP1 | Low pressure turbine 1 power fraction | Per-unit of PMAX | D, R2
| FLP2 | Low pressure turbine 2 power fraction | Per-unit of PMAX | D, R2
| PM1 | Rated mechanical power, shaft 1 | MW | D
| PM2 | Rated mechanical power, shaft 2 | MW | D
(if applicable)
| HT1, HT2 | Summated turbine inertias (excluding electrical generator), as seen on each generator shaft. | MWs/MBASE | D, R1, R2
Turbine time constants (whichever apply) :
| Symbol | Data Description | Units | Data Category | Value | Remarks
| TCH | Steam chest time constant (control valves to HP or VHP) Exhaust | s | D
| TVHP | Very high pressure turbine time constant | s | D
(possible alternative to TCH)
| THP | High pressure turbine | s | D
(possible alternative to TCH)
| TRH1 | Boiler reheat #1 time constant | s | D
| TRH2 | Boiler reheat #2 time constant | s | D
| TCO | Crossover time constant (IP exhaust to LP exhaust) | s | D
| TLP1 | Low pressure turbine 1 time constant | s | D
(possible alternative to TCO)
| TLP2 | Low pressure turbine 2 time constant | s | D
(possible alternative to TCO)
| 12.1.2 | Setting Data Sheet
Turbine governor
| Symbol | Data Description | Units | Data Category | Value | Remarks
| RMAX | Maximum Droop | % | S, D, R1
(% change in frequency / per-unit change in generating unit output)
| RNORM | Normal Droop | % | D, R1
(% change in frequency / per-unit change in generating unit output)
| RMIN | Minimum Droop | % | D, R1
(% change in frequency / per-unit change in generating unit output)
|  | Sustained response to frequency change | MW/Hz | D, R2
|  | Non-sustained response to frequency change | MW/Hz | D, R2
| PLR | Load Rejection Capability | MW | S, D, R2
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2
| FDBMAX | Maximum Frequency Dead band | Hz | D, R1
| FDBN | Normal Frequency Deadband | Hz | D, R1
| FDBMIN | Minimum Frequency Deadband | Hz | D, R1
| PDB | MW Deadband | MW | D, R1
Governor/servomotor rate limits
|  | · raise MW output | MW/s | D
|  | · lower MW output | MW/s | D
Note on F23: For R2 test purposes, the inertia value may be verified in combination with any relevant generator inertia.

## S-12.2
Return to Main
| 12.2 | Hydro turbine and turbine governor
Note: Potential SRAS services are required to provide the following data for both droop and isochronous modes of operation
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
|  | Description of hydro-turbine type (e.g. Francis turbine, Pelton wheel, etc.) | Text | D
|  | Functional block diagram, in accordance with Rule s5.2.4 (b), for turbine governor and turbine model showing: | Diagram | D
· functional structure;
· mathematical model details within each block (gains, time constants and non-linear elements);
· input and output quantities for each function block; and
· units for functional block diagram input and output quantities (if per-unit, specify base).
| 12.2.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| PM1 | Rated mechanical power | MW | D, R2
| PTMAX | Power limits imposed by valve or gate travel | MW | D, R2
PTMIN
| TW | Water starting time | s | D, R2
| TG | Gate servomotor time constant | s | D, R2
| TP | Pilot valve time constant | s | D, R2
| TR | Dashpot time constant | s | D, R2
Governor/gate rate limits
|  | · raise MW output | MW/s | D
|  | · lower MW output | MW/s | D
| HT | Turbine inertia (excluding electrical generator) | MWs/MBASE | D, R1, R2
| 12.2.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| RMAX | Maximum Droop | % | S, D, R1
(% change in frequency / per-unit change in generating unit output)
| RNORM | Normal Droop | % | D, R1
(% change in frequency / per-unit change in generating unit output)
| RMIN | Minimum Droop | % | D, R1
(% change in frequency / per-unit change in generating unit output)
|  | Sustained response to frequency change | MW/Hz | D, R2
|  | Non-sustained response to frequency change | MW/Hz | D, R2
|  | Governor control system time constant(s) | s | S, D, R2
(specify)
| PLR | Load Rejection Capability | MW | S, D, R2
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2
| FDBMAX | Maximum Frequency Dead band | Hz | D, R1
| FDBN | Normal Frequency Deadband | Hz | D, R1
| FDBMIN | Minimum Frequency Deadband | Hz | D, R1
| PDB | MW Deadband | MW | D, R1
Note on F26: For R2 test purposes, the inertia value may be verified in combination with any relevant generator inertia.
Note on G38: When there is more than 1 time constant, please differentiate each with a specific name.

## S-12.3
Return to Main
| 12.3 | Gas turbine and turbine governor
Note: Potential SRAS services are required to provide the following data for both droop and isochronous modes of operation
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
|  | Description of gas turbine type (e.g. combined cycle, open cycle, etc.) | Text | D
|  | Fuel capability (gas, distillate, other) | Text | D
|  | Functional block diagram for turbine governor and turbine model, in accordance with Rule s5.2.4 (b), showing: | Diagram | D
· functional structure;
· mathematical model details within each block (gains, time constants and non-linear elements);
· input and output quantities for each function block; and
· units for functional block diagram input and output quantities (if per-unit, specify base).
|  | Details of the temperature control system and its impact on sustainable generating unit output (e.g. characteristic of output power versus frequency). | Diagram | D
| 12.3.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| PM1 | Rated mechanical power | MW | D, R2
| KFC | Fuel control system gain | pu/pu | D, R2
(per unit valve position / per unit governor output)
(specify per unit bases)
| TFC | Fuel control system time delay | s | D, R2
| TVP | Valve positioner time constant | s | D, R2
| TFS | Fuel system time constant | s | D, R2
| KVP | Valve positioner forward gain | pu/pu | D, R2
(per unit fuel flow / per unit valve position)
(specify per unit bases)
| KVPF | Valve positioner feedback gain | pu/pu | D, R2
(per unit valve position / per unit fuel flow)
(specify per unit bases)
| VPMAX | Valve positioner range limits | pu | D, R2 | max:
| VPMIN | (maximum and minimum) |  |  | min:
|  | (specify per unit bases) |  |  | p.u. base:
| VPMAXR | Valve positioner rate or change limits | pu/s | D, R2 | max raise rate:
| VPMAXL | (maximum raise and lower rates) |  |  | max lower rate:
|  | (specify per unit bases) |  |  | p.u. base:
| TC | Combustor time delay | s | D, R2
| TCD | Gas turbine output time constant | s | D, R2
(compressor discharge time constant)
|  | Output power characteristic / torque function | Graph | D, R2
(per unit output power versus per unit fuel flow and speed, excluding limiting effects of temperature controller)
(specify per unit bases)
| HT | Turbine and compressor inertia (excluding electrical generator), as measured on generator shaft. | MWs/MBASE | D, R1, R2
| 12.3.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| RMAX | Maximum Droop | % | S, D, R1
(% change in frequency / per-unit change in generating unit output)
| RNORM | Normal Droop | % | D, R1
(% change in frequency / per-unit change in generating unit output)
| RMIN | Minimum Droop | % | D, R1
(% change in frequency / per-unit change in generating unit output)
|  | Sustained response to frequency change | MW/Hz | D, R2
|  | Non-sustained response to frequency change | MW/Hz | D, R2
|  | Governor control system time constant(s) | s | S, D, R2
(specify)
|  | Load Rejection Capability | MW | S, D, R2
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2
| FDBMAX | Maximum Frequency Dead band | Hz | D, R1
| FDBN | Normal Frequency Deadband | Hz | D, R1
| FDBMIN | Minimum Frequency Deadband | Hz | D, R1
| PDB | MW Deadband | MW | D, R1
Note on G8: Type of fuels the gas turbine can use.
Note on F43: For R2 test purposes, the inertia value may be verified in combination with any relevant generator inertia.
Note on D53: i.e. steady state response. Also, the effect of temperature controller is excluded here. Please include temperature controller effect in Data Sheet S-13.
Note on D54: i.e. transient response
Note on G55: When there is more than 1 time constant, please differentiate each with a specific name.
Note on D57: Refer to NER S5.2.5.7

## S-12.4
Return to Main
| 12.4 | Wind turbine aerodynamic model and blade pitch controller model
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
|  | Description of wind turbine type (e.g. active stall, passive stall, pitch controlled, etc.) | Text | D. R1
|  | Functional block diagram for pitch controller and turbine model, in accordance with Rule s5.2.4 (b), showing: | Diagram | D, R1
· functional structure;
· mathematical model details within each block (gains, time constants and non-linear elements);
· input and output quantities for each function block; and
· units for functional block diagram input and output quantities (if per-unit, specify base).
| 12.4.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| UCI | Cut-in wind speed | m/s | D, R1, R2
| UFP | Wind speed at which full power is attained | m/s | D, R1, R2
| UCO | Cut-out wind speed | m/s | D, R1
|  | Efficiency (Cp) curves | Data / Equations | D, R1
(efficiency versus tip speed ratio and blade pitch angle)
Pitch control:
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Power curve | Diagram | D, R1, R2
(turbine output power versus wind speed characteristic)
| BETA_MAX | Blade pitch limits | Degrees | D, R1
BETA_MIN
| BETA_REST | Blade resting pitch angle | Degrees | D, R1
(pitch angle below rated power, if not BETA_MIN)
|  | Pitch controller setpoint characteristic | Diagram | D, R1
(e.g. generator speed setpoint versus generator output power)
Blade pitch rate limits:
| RMAX | · increase angle | Degrees / s | D, R1
| RMIN | · decrease angle | Degrees / s | D, R1
| TP | Blade pitch controller servomotor/actuator time constant | s | D, R1
| HT | Turbine and blade inertia (excluding electrical generator), as measured on generator shaft. | MWs/MBASE | D, R1, R2
| 12.4.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1
Note on F34: For R2 test purposes, the inertia value may be verified in combination with any relevant generator inertia.

## S-12.5
Return to Main
| 12.5 | Diesel and Gas Reciprocating Engine
Note: Potential SRAS services are required to provide the following data for both droop and isochronous modes of operation
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 12.5.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Description engine type | Text | D
| PM1 | Rated mechanical power | MW | D, R2
|  | Actuator functional block diagram |  | D, R2
(including gains, time constants and locations of range and rate limits)
| ACMAX | Actuator range limits | pu | D, R2 | max:
| ACMIN | (maximum and minimum) |  |  | min:
|  | (specify per unit bases) |  |  | p.u. base:
| ACMAXR | Actuator rate of change limit (raise) | pu/s (raise) | D, R2 | raise:
|  | (specify per unit base) |  |  | p.u. base:
| ACMAXL | Actuator rate of change limit (lower) | pu/s (lower) | D, R2 | lower:
|  | (specify per unit base) |  |  | p.u. base:
| TD | Engine combustion time delay (dead time) | s | D, R2
|  | Output power characteristic | Graph | D, R2
(per unit output power versus per unit actuator position and speed)
(specify per unit bases)
| HT | Engine rotating inertia (excluding electrical generator), as measured on generator shaft. | MWs/MBASE | D, R1, R2
|  | Functional block diagram for governor controller and engine model, in accordance with Rule s5.2.4 (b). | Diagram | D
| 12.5.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2
Note on F25: For R2 test purposes, the inertia value may be verified in combination with any relevant generator inertia.

## S-13
Return to Main
| 13 | Secondary Mechanical Control systems
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
|  | Description of controller type (e.g. over-speed controller, etc.) and a description of its purpose. | Text | D
| 13.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the control system showing principles of operation, trigger levels, etc. | Text / Diagram | S, D, R1
|  | Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Details of how this controller interfaces with the primary mechanical control systems (if applicable), or how this controller effects its control action. | Text / Diagram | D
| 13.1.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2

## S-14.1
Return to Main
| 14.1 | Shaft Model / Subsynchronous Resonance Frequencies
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
| 14.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Dynamic model of turbine/ generator shaft system in lumped element form showing: | Diagram | D, R1
· component inertia,
· damping,
· shaft stiffness and
· any gearbox or shaft driven rotating exciter.
Proposed minimum model to be provided for each turbine type (steam, wind turbine generator, hydro or gas)
Natural damping of shaft torsional oscillation modes (for each mode):
|  | - Modal frequency | Hz | D, R1
|  | - Logarithmic decrement | Nepers/s | D, R1
| T | Shaft torque on low speed shaft | Nm | D, R1
| N | Gear ratio | Text | D, R1

## S-15.1
Return to Main
| 15.1 | Mechanically or electronically switched capacitor, reactor or resistor
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 15.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| VNOM | Nominal voltage | kV | D
| NSTEPS | Number of capacitor steps |  | D, R1
| XC | Capacitive reactance per step | MVAr at VNOM | D, R1
| NL | Number of reactor steps |  | D, R1
| XL | Inductive reactance per step | MVAr at VNOM | D, R1
| NR | Number of resistor steps |  | D, R1
| RR | Resistance per step | Ohm | D, R1
|  | Details of the control system showing principles of operation, trigger levels, switching times, discharge times, etc. | Text / Diagram | S, D, R1
|  | 3 phase electrical connection diagram, including earthing arrangements | Diagram | S, D
|  | Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Details of how this controller interfaces with the primary electrical or mechanical control systems (if applicable), or how this controller effects its control action. | Text / Diagram | D
| 15.1.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Number of steps normally on at PMAX and PMIN | Text | D, R1, R2
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). |  | D, R1, R2

## S-15.2
Return to Main
| 15.2 | Static VAR Compensator, Thyristor Controlled (SVC)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 15.2.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| BASE | Nameplate rating | MVA | S, D, R1
| VNOM | Rated voltage | kV | S, D
| SCD | Capability diagram (reactive power versus voltage) | Chart | S, D, R1
| XC | Capacitor reactance (thyristor switched capacitor) | % on BASE and VNOM | D,R1
| XL | SVC inductor reactance (thyristor controlled reactor) | % on BASE and VNOM | D,R1
(If a different configuration is used, please describe)
|  | Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional Block Diagram/Text | D,R1
| SCR | Minimum short circuit ratio(s) at plant LV terminals where the plant remains in stable operation. |  | D, R1
| X/R | For the minimum SCR above, the range of impedance (X/R) ratio where the plant remains in stable operation |  | D, R1
|  | Unit Harmonic Profile at LV terminals (at least 2nd to 40th) | Table | R1
Transformer data:
| Symbol | Data Description | Units | Data Category | Value | Remarks
| GTW | Number of windings |  | S, D
| GTVG | Vector group | Text | S, D
| GTRn | Rated MVA of each winding | MVA | S, D, R1
| GTTRn | Principal tap rated voltages | kV/kV | S, D, R1
| GTZ1n | Positive sequence impedance of each winding | (a + jb) % on 100 MVA base | S, D, R1
| GTZ2n | Negative sequence impedance of each winding | (a + jb) % on 100 MVA base | S, D, R1
| GTZOn | Zero sequence impedance of each winding | (a + jb) % on 100 MVA base | S, D, R1
|  | Earthing arrangement | Text, diagram | S, D
|  | Saturation curve | Diagram | R1
|  | Tap changer type, on/off load | On/Off | D
|  | Tapped winding | Text, Diagram | S, D, R1
| GTAPR | Tap change range | kV – kV | S, D
| GTAPS | Tap change step size | % | D
| 15.2.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). | Functional block diagram | D, R1, R2
Transformer data:
|  | OLTC details of control loop described in block diagram form, in accordance with Rule s5.2.4 (b), showing transfer functions of individual elements and measurement units. | Diagram | D, R2
| VREFMAX | Upper voltage reference | V | D, R2
| VREFMIN | Lower voltage reference | V | D, R2
| GTAPV | Tap change voltage setting range and setpoint (if any) | kV – kV | D, R2
| GTAPD | Tap change voltage deadband | kV | D, R2
| GTAPVL | Tap change high and low voltage interlocks (monitoring non-tapped side voltage or other control signal (specify)) | kV, kV | D, R2
| GTAPT | Tap change cycle time(s) | s, Text | D, R2

## S-15.3
Return to Main
| 15.3 | Voltage Source Converter or Current Source Converter, self commutated, or similar (VSC, CSC, STATCOM)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 15.3.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| BASE | Nameplate rating | MVA | S, D, R1
| VNOM | Rated voltage | kV | S, D
| SCD | Capability diagram (reactive power versus voltage) | Chart | S, D, R1
| ICMAX | Maximum capacitive current | % on BASE and VNOM | S, D, R1
|  | (If the device has an overload rating, include the overload rating and any time characteristics.) | (Diagram for any overload rating with time characteristics)
| ILMAX | Maximum inductive current | % on BASE and VNOM | S, D, R1
|  | Details of the control system described in block diagram form, in accordance with Rule s5.2.4 (b), showing transfer functions of individual elements and measurement units. | Functional block diagram / Text | D, R1, R2
(If the device has an overload rating, include the control system characteristics to control this functionality)
| SCR | Minimum short circuit ratio(s) at plant LV terminals where the plant remains in stable operation. |  | D, R1
| X/R | For the minimum SCR above, the range of impedance (X/R) ratio where the plant remains in stable operation |  | D, R1
|  | Unit Harmonic Profile at LV terminals (at least 2nd to 40th) | Table | R1
Transformer data:
| Symbol | Data Description | Units | Data Category | Value | Remarks
| GTW | Number of windings |  | S, D
| GTVG | Vector group | Text | S, D
| GTRn | Rated MVA of each winding | MVA | S, D, R1
| GTTRn | Principal tap rated voltages | kV/kV | S, D, R1
| GTZ1n | Positive sequence impedance of each winding | (a + jb) % on 100 MVA base and VNOM | S, D, R1
| GTZ2n | Negative sequence impedance of each winding | (a + jb) % on 100 MVA base and VNOM | S, D, R1
| GTZOn | Zero sequence impedance of each winding | (a + jb) % on 100 MVA base and VNOM | S, D, R1
|  | Earthing arrangement | Text, diagram | S, D
|  | Saturation curve | Diagram | R1
|  | Tap changer type, on/off load | On/Off | D
|  | Tapped winding | Text, diagram | S, D, R1
| GTAPR | Tap change range | kV – kV | S, D
| GTAPS | Tap change step size | % | D
| 15.3.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). | Functional block diagram | D, R1, R2
Transformer data:
|  | OLTC details of control loop described in block diagram form, in accordance with Rule s5.2.4 (b), showing transfer functions of individual elements and measurement units. | Diagram | D, R2
| VREFMAX | Upper voltage reference | kV | D, R2
| VREFMIN | Lower voltage reference | kV | D, R2
| GTAPV | Tap change voltage setting range and setpoint (if any) | kV – kV | D, R2
| GTAPD | Tap change voltage deadband | kV | D, R2
| GTAPVL | Tap change high and low voltage interlocks (monitoring non-tapped side voltage or other control signal (specify)) | kV, kV | D, R2
| GTAPT | Tap change cycle time(s) | s, Text | D, R2
Note on D2: e.g. driven by IGBT (Insulated Gate Bipolar Transistor)

## S-15.4
Return to Main
| 15.4 | Flywheel
The relevant tab in section 9 must also be completed for the relevant grid interface technology (synchronous machine, doubly-fed asynchronous machine etc.)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 15.4.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
| BASE | Nameplate rating | MVA | S, D, R1
| VNOM | Rated voltage | kV | S, D
| H | Stored energy in flywheel inertia | MWs/BASE | D
(normal or rated value)
| SCD | Capability diagram | Chart | S, D, R1
(active power versus voltage and speed)
|  | Description of the control system showing principles of operation, trigger levels, switching times, etc., and conditions for discharging active power to the power system. | Text / Diagram | S, D, R1
|  | Details of the control system in functional block diagram form, in accordance with Rule s5.2.4 (b). | Functional block diagram | S, D, R1
|  | Details of how this controller interfaces with the primary electrical or mechanical control systems (if applicable), or how this controller effects its control action. | Text / Diagram | D
| 15.4.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.). | Functional block diagram | D, R1, R2

## S-15.5
Return to Main
| 9.2 | Asynchronous Motor (generator auxilaries > 1 MW)
| Symbol | Data Description | Units | Data Categories | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1
|  | Manufacturer and manufacturer’s type designation or product name. | Text | S, D, R1
| 9.2.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Categories | Value | Remarks
| VTGEN | Nominal terminal voltage | kV | S, D, R1
| MBASE | Asynchronous machine nameplate rating (MVA) | MVA | S, D, R1
| QN | Reactive power consumption over range of asynchronous machine output (0 to PMAX) at VTGEN | Chart | S, D, R1
(MVAr vs. MW)
| H | Asynchronous machine and gearbox inertia constant (excluding prime mover inertia) | MWs/MBASE | S, D, R1
| NP | Number of poles |  | S, D, R1
| SLIP | Rated slip |  | S, D, R1
|  | Stator/rotor turn ratio |  | S, D, R1
| RS | Stator resistance | % on MBASE and VTGEN | S, D, R1
|  | (at normal or typical operating temperature – specify temperature) | (temperature in °C)
| XS | Stator leakage reactance | % on MBASE and VTGEN | S, D, R1
· unsaturated and
· at VTGEN
| RM | Iron loss resistance, referred to the stator | % on MBASE and VTGEN | S, D, R1
| XM | Magnetizing reactance, referred to the stator | % on MBASE and VTGEN | S, D, R1
· unsaturated and
· at VTGEN
| RR | Rotor resistance at rated slip, referred to the stator | % on MBASE and VTGEN | S, D, R1
| XR | Rotor leakage reactance, referred to the stator | % on MBASE and VTGEN | S, D, R1
· unsaturated and
· at VTGEN
| R0 | Zero sequence resistance | % on MBASE and VTGEN | S, D, R1
| X0 | Zero sequence reactance | % on MBASE and VTGEN | S, D, R1
| R2 | Negative sequence resistance | % on MBASE and VTGEN | S, D, R1
| X2 | Negative sequence reactance | % on MBASE and VTGEN | S, D, R1
|  | Magnetising curve (voltage versus current) | Chart | S, D, R1
|  | Speed (slip) vs torque (power) curve(s) | Chart | S, D, R1
|  | Equivalent circuit noting location of equivalent impedances | Chart | S, D, R1
Note on G17: resistance
Note on G18: temperature

## S-16.1
Return to Main
| 16.1 | Synchronous machine protection systems (backups for excitation limiters)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | D, R1
|  | Manufacturer and manufacturer’s type designation or product name. | Text | D, R1 |  | Key relays to include: - High and low voltage protection; - Over- and under-frequency protection; - Rate of change of frequency protection; - Loss of excitation protection; - Over-flux (V/Hz) protection; - Out-of-step protection; - Negative phase sequence (current unbalance) protection; - Reverse active power protection; - Torsional stress protection; - Unit transformer and generator differential protection.
| 16.1.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the protection system showing principles of operation, trigger levels, switching times, etc. for the following protective functions: | Text / Diagram | D, R1
|  | Details of how this protection system effects its protection action (e.g. trips the generating unit at the generating unit circuit breaker, turbine trip, etc.) for the following protective functions: | Text / Diagram | D
|  | · over and under voltage protection; |  | D, R1
· over and under frequency protection;
· over and under rate-of-change-of-frequency protection;
· over-excitation protection;
· under-excitation protection;
· stator current protection (if fitted);
· flux (V/f) protection ;
· negative phase sequence protection;
· reverse active power protection;
· torsional stress protection;
· unit transformer differential protection;
· generator differential protection;
· loss of field protection; and
· pole-slip (out-of-step) protection.
|  | Winding ratios, voltages and connection locations of Current Transformers and Voltage Transformers feeding protection relays |  | D
| 16.1.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Protection trigger levels and timings for the following protective functions: |  | D, R1
|  | · over and under voltage protection; |  | D, R1
· over and under frequency protection;
· over and under rate-of-change-of-frequency protection;
· over-excitation protection;
· under-excitation protection;
· stator current protection (if fitted);
· flux (V/f) protection ;
· negative phase sequence protection;
· reverse active power protection;
· torsional stress protection;
· unit transformer differential protection;
· generator differential protection;
· loss of field protection; and
· pole-slip (out-of-step) protection.

## S-16.2
Return to Main
| 16.2 | Asynchronous plant protection systems (for geneating unit and plant instability)
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1 |  | Key relays to include: - High and low voltage protection; - Over- and under-frequency protection; - Rate of change of frequency protection; - Multiple fault ride-through protection; - Instability protection; - Negative phase sequence protection; - (SRAS Providers only): Generator and unit transformer differential protection; - (SRAS Providers only): Any other protection relays that may be relevant
| 16.2.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the protection system showing principles of operation, trigger levels, switching times, etc. | Text / Diagram | S, D, R1
|  | Details of how this protection system effects its protection action (e.g. trips the generating unit at the generating unit circuit breaker, etc.). | Text / Diagram | D
|  | Winding ratios, voltages and connection locations of Current Transformers and Voltage Transformers feeding protection relays |  | D
| 16.2.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Protection trigger levels and timings. |  | D, R1

## S-16.3
Return to Main
| 16.3 | Dynamic braking / Crowbar protection systems
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1, R2
|  | Manufacturer and manufacturer’s type designation or product name. | Text | R1, R2
| 16.3.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the protection system showing principles of operation, trigger levels, switching times, etc., and conditions for discharging active power to the power system. | Text / Diagram | S, D, R1
|  | Details of how this protection system interfaces to the primary plant or control systems and effects its protection action (e.g. applies resistor or short circuits induction generator rotor inputs or converter capacitor, etc.). | Text / Diagram | D
| 16.3.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Protection trigger levels and timings. |  | D
|  | Resistance of applied crowbar (if on an asynchronous machine, referred to the stator, if possible) | % of MBASE and VTGEN | D

## S-16.4
Return to Main
| 16.4 | Generating system-level protection systems
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1
|  | Manufacturer and manufacturer’s type designation or product name. | Text | D, R1 |  | Key relays to include: - Any protection system that is more restrictive on the generating system performance than individual unit protection; - High and low voltage protection; - Over- and under-frequency protection; - Rate of change of frequency protection; - Multiple fault ride-through protection; - Negative phase sequence protection; - Reverse active power protection; - Plant transformer protection;
| 16.4.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the protection system showing principles of operation, trigger levels, switching times, etc., and conditions for discharging active power to the power system. | Text / Diagram | S, D, R1
|  | Details of how this protection system effects its protection action (e.g. trips the generating unit at the generating unit circuit breaker, turbine trip, etc.). | Text / Diagram | D
|  | Winding ratios, voltages and connection locations of Current Transformers and Voltage Transformers feeding protection relays |  | D
| 16.4.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Protection trigger levels and timings. |  | D, R1 |  | Must be consistent with the plant's performance standards

## S-16.5
Return to Main
| 16.5 | Other protection systems
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | The list of generating units to which this information applies. | Text | S, D, R1 |  | Include runback schemes, special protection schemes, and system strength tripping schemes in this section.
|  | Manufacturer and manufacturer’s type designation or product name. | Text | D, R1
| 16.5.1 | Design Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Details of the protection system showing principles of operation, trigger levels, switching times, etc., and conditions for discharging active power to the power system for the following protective functions: | Text / Diagram | D, R1
|  | Details of how this protection system effects its protection action (e.g. trips the generating unit at the generating unit circuit breaker, turbine trip, etc.) for the following protective functions: | Text / Diagram | D
|  | · over-speed, high or low frequencies; |  | D, R1
· high frequency rates of change;
· high or low voltages;
· excessive negative phase sequence current;
· sustained voltage fluctuations or harmonic distortion;
· differential;
· anti-islanding; and
· synchrocheck (if fitted);
|  | Winding ratios, voltages and connection locations of Current Transformers and Voltage Transformers feeding protection relays |  | D
| 16.5.2 | Setting Data Sheet
| Symbol | Data Description | Units | Data Category | Value | Remarks
|  | Protection trigger levels and timings for the following protective functions: |  | D, R1 |  | Must be consistent with the plant's performance standards
|  | · over-speed, high or low frequencies; |  | D, R1
· high frequency rates of change;
· high or low voltages;
· excessive negative phase sequence current;
· sustained voltage fluctuations or harmonic distortion;
· differential;
· anti-islanding; and
· synchrocheck (if fitted);