## Index
The National Electricity Market Constraint Report 2020
Electronic Material
This spreadsheet provides (for each calendar year):
* Constraint equation changes year on year comparison
* Binding constraint equations (energy and FCAS separately)
* Binding Impact of constraint equations
* Summary of binding/binding impact constraint equations by region
* Summary of binding/binding impact constraint equations for System Normal vs Outages
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
* Network and generation augmentations
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page
Binding constraints:
A constraint equation is a linear equation, with a left hand side (LHS) and a right hand side (RHS). A constraint is binding when LHS=RHS, which means it has reached its upper limit.
In some cases, the binding results for several constraint equation IDs have been combined. This is due to some limits being represented by several constraint equations, to either:
• Move each generator from a maximum calculation onto the LHS of separate constraint equations (such as the New South Wales to Queensland voltage stability limit).
• Manage the same limit under different network configurations (such as Yallourn W1 switched into 500 kV or 220 kV mode).
• Combine different values of network support for the same generator(s).
Binding Impact:
Binding Impact is used to distinguish between the severities of different binding constraint equations. It represents the financial pain associated with that binding constraint equation and can be a good way of picking up congestion issues. It is a relative term, not an absolute term.

## Constraint Changes
Constraint changes by region and year
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Ad-Hoc | 0 | 0 | 1 | 1 | 0 | 0
Constraint Automation - Real Time | 11484 | 22603 | 29805 | 37744 | 32817 | 53504
Constraint Automation | 98 | 64 | 20 | 48 | 49 | 39
DATASNAP | 105 | 115 | 44 | 92 | 90 | 62
FCAS | 543 | 257 | 267 | 486 | 1192 | 730
NSW | 6332 | 1973 | 2455 | 8206 | 5092 | 7926
Negative Residue | 0 | 0 | 0 | 0 | 0 | 12
Non-Conformance | 5 | 5 | 52 | 35 | 29 | 31
Other | 2 | 0 | 0 | 3 | 1 | 0
Outage Ramping | 21056 | 20484 | 16928 | 19368 | 25718 | 23622
PASA | 12 | 0 | 0 | 0 | 0 | 0
Qld | 118 | 206 | 246 | 1716 | 582 | 937
Quick | 101 | 359 | 386 | 1032 | 865 | 1072
SA | 1001 | 3197 | 1775 | 3239 | 7132 | 2309
Tas | 121 | 1050 | 134 | 193 | 629 | 25
Vic | 3541 | 3251 | 1376 | 6280 | 5656 | 1418
Total constraint eqns | 11231 | 11660 | 11578 | 11467 | 12348 | 13127
Total changes without outage ramping and CA-RT | 11979 | 10477 | 6756 | 21331 | 21317 | 14561
Total number of constraints
| 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Constraint Equations | 7746 | 7697 | 8275 | 8902 | 9523 | 9745 | 9935 | 10303 | 11231 | 11660 | 11578 | 11467 | 12348 | 13127
Constraint Sets | 3366 | 3369 | 3431 | 3559 | 3657 | 3597 | 3410 | 3424 | 3630 | 3778 | 3917 | 4036 | 4390 | 4603
Constraint Functions |  |  | 347 | 382 | 390 | 401 | 366 | 359 | 364 | 373 | 387 | 505 | 585 | 588
Increase in Constraint Equations |  |  | 578 | 627 | 621 | 222 | 190 | 368 | 928 | 429 | -82 | -111 | 881 | 779

## Binding
Constraint Equation ID | 2020 Hours | 2019 Hours | Description | Type | Region
#PPCCGT_D_E | 2074.0833 | 26 | SPPT.ENERGY * 1 = 168 (Wt = 755) | Other | Direction
#MARYRSF1_E | 1946.8333 | 0 | QMRY2M.ENERGY * 1 <= 27.3 (Wt = 360) | Other | Quick
Q_NIL_STRGTH_MEWF | 1572.1667 | 32.1667 | Out = Nil, limit Mt Emerald WF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
#YARANSF1_E | 1403.5833 | 0 | QMRY1Y.ENERGY * 1 <= 82 (Wt = 360) | Other | Quick
T_MRWF_FOS | 1187.8333 | 0 | Limit Musselroe wind farm due to upper limit on Tasmanian generator events. Limit is 153 MW (effective 144 MW at the connection point at Derby) | NIL | Tas
#TORRB2_D_E | 1078 | 12.25 | STSB2.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
Q_NIL_STRGTH_HAUSF | 995.0833 | 1.3333 | Out = Nil, limit Haughton SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
V_MURRAWRWF_MAX | 971.75 | 172.1667 | Limit MW output of Murra Warra wind farm to hold point levels during day/night | Outage | Vic
SVML_ZERO | 947 | 624.4167 | SA to Vic on ML upper transfer limit of 0 MW | Outage | SA
S_WIND_1200_AUTO & S_NIL_STRENGTH_1 | 942.3333 | 624.25 | Upper limit (1300 to 1750 MW) for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements. Automatically swamps out when required HIGH combination is online. | NIL | SA
#VIC1_E_20200811 | 884.1667 | 0 | Multiple VIC1 LHS <= 295 (Wt = 360) | Other | Quick
#TORRB3_D_E | 819.5 | 0 | STSB3.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
N_X_MBTE2_A & N_X_MBTE2_B | 801.6667 | 216.75 | Out= two Directlink cables, NSW to Qld limit | Outage | NSW
N_X_MBTE_3A & N_X_MBTE_3B | 797.5 | 174 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | NSW
V_YENDWF_MAX | 796.4167 | 31.6667 | Limit MW output of Yendon wind farm to hold point levels during day/night | Outage | Vic
#CTHLWF1_E | 648.1667 | 0 | TWC11C.ENERGY * 1 <= 95 (Wt = 360) | Other | Quick
N^N-LS_SVC | 638.75 | 22.3333 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage | NSW
V^^N_NIL_1 | 585.1667 | 166.4167 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Vic
N>N-NIL_CLDP_1 | 583.75 | 448.3333 | Out= Nil, avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | NIL | NSW
N^^V_NIL_1 | 535.5 | 2060.5833 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | NSW
Q_NIL_STRGTH_SMSF | 504.75 | 0.16667 | Out = Nil, limit Sun Metal SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
#TORRB4_D_E | 465.25 | 26.6667 | STSB4.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
#TORRB1_D_E | 463.9167 | 0 | STSB1.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
#BNGSF2_E | 424.5 | 537.8333 | SBEM2B.ENERGY * 1 <= 74 (Wt = 360) | Other | Quick
Q^^NIL_QNI_SRAR | 397.1667 | 773.8333 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Qld
#MORTLK12_D_E | 374.1667 | 0 | VM0P2O.ENERGY * 1 = 20 (Wt = 755) | Other | Direction
#MORTLK11_D_E | 372.5833 | 0 | VM0P1O.ENERGY * 1 = 265 (Wt = 755) | Other | Direction
#WARWSF1_E | 371.4167 | 0 | QMRY3W.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
#ELAINWF1_E | 366.5833 | 0 | VELT3E.ENERGY * 1 <= 65 (Wt = 360) | Other | Quick
S:V_PA_SVC_420 | 363.75 | 5.6667 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | SA
V_T_NIL_FCSPS | 347.9167 | 974.5833 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Vic
#COOPGWF1_E | 339.8333 | 72.5833 | QCPG1C.ENERGY * 1 <= 357 (Wt = 360) | Other | Quick
T::T_NIL_1 | 315.75 | 0 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Swamp if less than 3 synchronous West Coast units generating or Farrell 220kV bus coupler open or Hampshire 110kV line is closed. | NIL | Tas
Q>NIL_COLNVSF1 | 305.5 | 87 | Out = Nil, Limit Collinsville Solar Farm to thermal rating of Powerlink's RMU | NIL | Qld
#BULGANA1_E | 302.9167 | 0 | VBGT1B.ENERGY * 1 <= 100 (Wt = 360) | Other | Quick
S>V_NIL_NIL_RBNW | 285.8333 | 406.5833 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL | SA
V_BANSF_BBD_60 | 277 | 79.9167 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Vic
#V-SA_I_E | 250.25 | 0 | V-SA. * -1 = 30 (Wt = 360) | Other | Quick
#YENDWF1_E | 239.9167 | 1080.3333 | VBAW1Y.ENERGY * 1 <= 103 (Wt = 360) | Other | Quick
V>V_NIL_17 | 235.5833 | 0.25 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback | NIL | Vic
Q_STR_3113103_MEWF | 229.6667 | 0 | Limit Mt Emerald WF to 25% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
#COHUNSF1_E | 228.9167 | 0 | VKGS2C.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
V_YW_134_580 | 226.8333 | 0 | Upper limits of 580 MW on Yallourn units 1, 3 and 4 | Outage | Vic
#DEVILS_G_E | 226.0833 | 177.75 | TDG11.ENERGY * 1 <= 64 (Wt = 360) | Other | Quick
#TORRA1_D_E | 223.5 | 0 | STSA1.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
#LIMOSF11_E | 214.9167 | 0 | NBSF1L.ENERGY * 1 <= 145 (Wt = 360) | Other | Quick
Q_MEWF1_ZERO | 211 | 0 | Mt Emerald Wind Farm upper limit of 0 MW | Outage | Qld
Q_STR_333104_HASF25 | 196.25 | 0 | Limit Haughton SF to 25 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | Qld
Q_STR_333104_MEWF25 | 196.25 | 0 | Limit Mt Emerald WF to 25 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | Qld
Q_STR_333104_SMSF25 | 196.25 | 0 | Limit Sun Metals SF to 25 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | Qld
#YATSF1_E | 166.5 | 0 | VRCS2Y.ENERGY * 1 <= 50 (Wt = 360) | Other | Quick
N^^N_NIL_2 | 165.25 | 0 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | NSW
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 155.25 | 234.5833 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Qld
V^^N_HWSM_1 | 155.1667 | 0 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Vic
Q_STR_311310_HASF | 151.8333 | 0 | Limit Haughton SF to 25% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
Q>SSRV_M020/3 | 151.6667 | 0 | Out= Nil, Limit Susan River to the continuous ratings of Feeder M020/3 Susan River to T section 66kV line, Feedback | Outage | Qld
#MOORAWF1_E | 148.5833 | 0 | VELT2M.ENERGY * 1 <= 30 (Wt = 360) | Other | Quick
V>>V_NIL_9 | 147.9167 | 1.1667 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Vic
V_MLMO_VS_LB_CAN_50 | 147.5 | 18.0833 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS/DUNDWF generating. | Outage | SA
#GULLRWF2_E | 146.75 | 0 | NGUR3G.ENERGY * 1 <= 36 (Wt = 360) | Other | Quick
Q_SMCSF1_ZERO | 146.5 | 0 | Sun Metals solar farm upper limit of 0 MW | Outage | Qld
S>NIL_MHNW1_MHNW2 | 144 | 0 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL | SA
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 139.75 | 100.9167 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | NSW
Q_STR_311310_SMSF | 134 | 0 | Limit Sun Metals SF to 25% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
V_MURRAWRWF_FLT_90 | 130.5833 | 2.1667 | Limit Murra Warra Wind Farm upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | Vic
N>>N-NIL_94T_947 | 129.6667 | 0 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | NIL | NSW
N^^V_NIL_YW134_N-2 | 127.8333 | 0 | Out = Nil, avoid voltage collapse at Southern NSW for loss of Yallourn units 1, 3 and 4 when declared credible and are the largest contingency | NIL | NSW
#OAKEY2SF_E | 125.0833 | 1015.5 | QTKS2O.ENERGY * 1 <= 55 (Wt = 360) | Other | Quick
V::N_HWSM_xxx | 125 | 113.8333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
SV_420_DYN | 120.6667 | 0 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | SA
N_MBTE1_B | 119.6667 | 466.6667 | Out= one Directlink cable, Qld to NSW limit | Outage | NSW
Q_HAUGHTSF1_ZERO | 106.5833 | 0 | Haughton Solar Farm upper limit of 0MW | Outage | Qld
N^^N_NIL_3 | 104.4167 | 0 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse for contingency trip of Bendigo-Kerang 220kV line in NW Victoria | NIL | NSW
N>N-NIL_LSDU | 101.25 | 27.8333 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
SA_HYSE2 | 94.75 | 1.8333 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage | SA
N_DARLSF1_ZERO | 91.9167 | 0 | Darlington Point solar farm upper limit of 0 MW and all inverters disconnected. | Outage | NSW
NSA_Q_GSTONE34_xxx | 91.5833 | 13.5 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Qld
#TORRA4_D_E | 86 | 17 | STSA4.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
V_KIATA_ISL_0 | 83.0833 | 127.1667 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
S^SETX_GEN_CAP | 79.4167 | 27.5 | Out= One South East 275/132kV transformer O/S, avoid local voltage collapse on trip of remaining South East transformer, | Outage | SA
V_MACARTHUR_ZERO | 79 | 310.9167 | Macarthur upper limit of 0 MW | Outage | Vic
Q_STR_211383_10KIDSF | 78.8333 | 0 | Limit Kidston SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
Q_STR_211383_10RGBSF | 78.8333 | 0 | Limit Rugby Run SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
VSML_ROC_80 | 77.4167 | 31.75 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
V^^N_UTYS_1 | 76.75 | 0 | Out = Upper Tumut to Yass (2) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Vic
Q_STR_211383_10DAYSF | 75.8333 | 0 | Limit Daydream SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
SA_HYSE1 | 74.75 | 3 | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage | SA
Q_STR_211383_10HAMSF | 74.5 | 0 | Limit Hamilton SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
#TORRA2_D_E | 74.4167 | 0 | STSA2.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
Q_STR_211383_10RRSF | 74.0833 | 0 | Limit Ross River SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
N^^V_DDSM1 | 74 | 32.8333 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | NSW
SVML_ROC_80 | 72.8333 | 27.25 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
Q_STR_211383_10HAYSF | 72.5833 | 0 | Limit Hayman SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
Q_STR_211383_10COLSF | 71.8333 | 0 | Limit Collinsville SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
Q_STR_211383_10WHTSF | 68.75 | 0 | Limit Whitsunday SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
V_MURRAWRWF_FLT_0 | 68.5833 | 27.9167 | Limit Murra Warra Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
T_MRWF_QLIM_xx | 66.6667 | 51.5 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Tas
V>V_NIL_8 | 66.4167 | 4.3333 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Vic
N_STWF1_ZERO | 65.5 | 118.8333 | Silverton wind farm upper limit of 0 MW and all wind turbines disconnected. | Outage | NSW
V_BANNERTSF_FLT_25 | 63.9167 | 0 | Limit Bannerton Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | Vic
Q>NIL_YLMR | 63.6667 | 0 | Out= Nil, avoid overload on 110kV feeders between Yarranlea and Middle Ridge(733/1 and 734/1), Feedback | NIL | Qld
V_KARADSF_FLT_25 | 63.5833 | 9.3333 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | Vic
#WARWSF2_E | 63.1667 | 0 | QMRY4W.ENERGY * 1 <= 16 (Wt = 360) | Other | Quick
VT_ZERO | 60.5833 | 27.9167 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Vic
#DARLSF1_E | 59.8333 | 0 | NDNS1D.ENERGY * 1 <= 172 (Wt = 360) | Other | Quick
N_BKHSF_40INV | 59.4167 | 11.0833 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 40. Constraint swamp out otherwise. DS only | NIL | NSW
#CROWLWF1_E | 57.75 | 301.0833 | VCWL1C.ENERGY * 1 <= 72 (Wt = 360) | Other | Quick
Q>N-MUTE_757 | 56.5 | 0 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
VSML_220 | 55.8333 | 3.5833 | Vic to SA on ML upper transfer limit of 220 MW | NIL | Vic
#MUWAWF1_E | 55.6667 | 601.75 | VMRT1M.ENERGY * 1 <= 148 (Wt = 360) | Other | Quick
#CHYTWF1_E | 53.75 | 0 | VSM71C.ENERGY * 1 <= 28 (Wt = 360) | Other | Quick
#OSB-AG_O_L6 | 53.6667 | 0 | SNBN1.LOWER6SEC * 1 = 14 (Wt = 60) | Other | Quick
#OSB-AG_O_L60 | 53.6667 | 0 | SNBN1.LOWER60SEC * 1 = 14 (Wt = 60) | Other | Quick
#OSB-AG_P_L6 | 53.6667 | 0 | SNBN1.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | Quick
#OSB-AG_P_L60 | 53.6667 | 0 | SNBN1.LOWER60SEC * 1 <= 0 (Wt = 12) | Other | Quick
V_WEMENSF_FLT_25 | 53.5 | 0 | Limit Wemen Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | Vic
V_BULGANAWF_FLT_0 | 52.9167 | 0 | Limit Bulgana Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
N_LIMOSF2_FLT_25 | 52.8333 | 0 | Limit Limondale 2 solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | NSW
S:V_550_HY_TEST_DYN | 52.5 | 0.75 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
V_NUMURKAH_ZERO | 52.0833 | 0 | Numurkah Solar Farm upper limit of 0 MW | NIL | Vic
SVML^NIL_160 | 52 | 0 | Out=NIL, SA to Vic on ML upper transfer limit of 160 MW to manage voltage collapse at Monash | NIL | SA
Q:NIL_OAKEY2SF | 51.3333 | 46.3333 | Limit Oakey 2 solar farm to 0MW when Oakey GT is online to prevent transient instability for 3 phase fault at Tangkam | NIL | Qld
V^^SML_NSWRB_2 | 50.8333 | 59.1667 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Vic
Q_NIL_STRGTH_KIDSF | 50.6667 | 0 | Out = Nil, limit Kidston SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
Q_STR_333104_MEWF70 | 49.5 | 0 | Limit Mt Emerald WF to 70 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | Qld
Q_NIL_STRGTH_RGBSF | 49.4167 | 0 | Out = Nil, limit Rugby Run SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
#LOYYB1_E | 47.9167 | 0 | VLYP5.ENERGY * 1 <= 530 (Wt = 360) | Other | Quick
#OSB-AG_D_E | 47.8333 | 4.75 | SNBN1.ENERGY * 1 = 155 (Wt = 755) | Other | Direction
Q_STR_211383_10CLRSF | 47.8333 | 0 | Limit Clare SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | Qld
V_GANWRSF_FLT_25 | 47.6667 | 230.8333 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | NIL | Vic
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 47.1667 | 49 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Vic
#OSB-AG_O_R6 | 46.5833 | 0 | SNBN1.RAISE6SEC * 1 = 14 (Wt = 60) | Other | Quick
#OSB-AG_P_R6 | 46.5833 | 0 | SNBN1.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | Quick
N_FINLYSF_FLT_45 | 46.4167 | 0 | Limit Finley solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | NSW
N_BROKENHSF_FLT_25 | 46.25 | 0 | Limit Broken Hill Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | NSW
N::N_CRGR_2 | 45.8333 | 0 | Out = Crookwell to Gullen Range(3H), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | NSW
V_KIATAWF_FLT_0 | 45.1667 | 269.4167 | Limit Kiata Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
NC_N_WRSF1 | 45.0833 | 1 | Non Conformance Constraint for WHITE ROCK SOLAR | Other | Non-Conformance
N>N-NIL_9R4_99A | 44.0833 | 0 | Out= Nil, avoid O/L Finley to Mulwala 132kV line (9R4) on trip of Finley to Uranquinty (99A) line, Feedback | NIL | NSW
Q_LILYSF1_ZERO | 43.9167 | 147.75 | Lilyvale Solar Farm upper limit of 0 MW | Outage | Qld
S>NIL_HUWT_STBG2 | 42.25 | 14.8333 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL | SA
SA_ISLE_STRENGTH_LB | 42.1667 | 4.8333 | Maximum limit (0 MW) for Lake Bonney and Canunda Wind Farm for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
Q_STR_311393_HASF | 41.5833 | 0 | Limit Haughton SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | Qld
VSML_ZERO | 41.4167 | 33.4167 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Vic
V_BANNERTSF_FLT_45 | 40.0833 | 2.4167 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
Q>CPWO2_CPWU_CPWO1 | 40 | 0 | Out= Calliope River to Woolooga (814) line, avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (813) line, Feedback | Outage | Qld
N_BROKENH1_ZERO | 39.8333 | 85.0833 | Broken Hill Solar Farm upper limit of 0 MW and all inverters disconnected. | Outage | NSW
N^^V_NIL_ARWBBA | 39.6667 | 0 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL | NSW
V_BANSF_BBD_80 | 38.8333 | 0.5 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Vic
SVML_095 | 38.5833 | 0 | SA to Vic on ML upper transfer limit of 95 MW | Outage | SA
#LGAPWF1_E | 38.4167 | 676.4167 | SLGW1L.ENERGY * 1 <= 126 (Wt = 360) | Other | Quick
V::N_NIL_xxx | 37.9167 | 17.0833 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL | Vic
NQTE_ROC | 37.6667 | 12.4167 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | NSW
T>T_GTSH_IMP_4K | 37.6667 | 4.1667 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
V_CWWF_ISL_0 | 37.3333 | 7.1667 | Crowlands Wind Farm total upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
#NEVERSF1_E | 37.0833 | 37 | NWLS3N.ENERGY * 1 <= 79 (Wt = 360) | Other | Quick
Q_STR_21138_RGBSF50 | 36.8333 | 0 | Limit Rugby Run SF to 50% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
T^V_NIL_9 | 36.3333 | 19.5833 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
Q>NIL_EMBW_EMLV_DS | 36.1667 | 0 | Out= Nil, limit Emerald SF to 40MW to avoid overload on Emerald - Lilyvale 66kV line on trip of Emerald - Comet - Blackwater 66kV line (6056 or 6011), swamp if Emerald CBs S612,S610 and Blackwater CB S605 are closed (DS only) | NIL | Qld
N_BKHSF_40INV | 36 | 11.0833 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 40. Constraint swamp out otherwise. DS only | Outage | NSW
V>>V_NIL_18 | 35.6667 | 0 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Vic
Q_NIL_STRGTH_CLRSF | 34.75 | 0 | Out = Nil, limit Clare SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
V_DUNDWF1_ZERO | 34.3333 | 0 | Dundonnell wind farm 1 upper limit of 0 MW | Outage | Vic
Q_9C3_10C21_MEWF | 34 | 0 | Limit Mt_Emerald 70% capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | Qld
V_DUNDWF3_ZERO | 34 | 0 | Dundonnell wind farm 3 upper limit of 0 MW | Outage | Vic
S:V_550_HY_TEST | 33.5 | 0.58333 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
#LIMOSF21_E | 32.9167 | 0 | NBL21L.ENERGY * 1 <= 14 (Wt = 360) | Other | Quick
N_BROKENHSF_FLT_0 | 32.8333 | 33.8333 | Limit Broken Hill Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | NSW
N_DARLSF_FLT_SC_25 | 32.6667 | 0 | Limit Darlington Pt solar farm upper limit to 25 MW to manage post contingent voltage oscillation. If either/both Buronga Syncon 2 or/and 3 out of service, limit Darlington Pt solar farm to 0 MW | Outage | NSW
T>T_NIL_110_1 | 32.6667 | 251.5833 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Tas
V^^N_X_MNYS_CNUT_1 | 32.25 | 0 | Out = Canberra to Upper Tumut (01) and Marulan to Yass (4 or 5) 330kV lines, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Vic
#GOONSF1_E | 32.0833 | 0 | NPG12G.ENERGY * 1 <= 70 (Wt = 360) | Other | Quick
V_BANNERTSF_FLT_0 | 32.0833 | 69.5833 | Limit Bannerton Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V_DUNDWF2_ZERO | 31.9167 | 0 | Dundonnell wind farm 2 upper limit of 0 MW | Outage | Vic
S>RBTX1_RBTX2_WEMWP4 | 31.8333 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-MWP4 132kV line on trip of Robertstown 275/132kV TX2, | Outage | SA
S:VS_PA_SVC_570 | 31.25 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage | SA
N_FINLYSF_FLT_SC_25 | 30.5833 | 0 | Limit Finley solar farm upper limit to 25 MW to manage post contingent voltage oscillation. If Buronga Syncon 1 is out of service, limit Finley solar farm to 0 MW | Outage | NSW
Q_STR_21138_EMSF50 | 30.5 | 0 | Limit Emerald SF to 50% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
V_ARARATWF_ISL_0 | 30.25 | 7.3333 | Limit Ararat Wind Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Vic
QNTE_ROC | 30 | 18.25 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
#NSW1-QLD1_RAMP_I_F | 29.6667 | 2.1667 | NSW1-QLD1 >= MIN(-246, InitialFlow + 200) (Wt=35) | Other | Quick
N_MBTE1_A | 29.5833 | 3.0833 | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
Q_9C3_10C21_HASF | 29.4167 | 0 | Limit Haughton70% Max capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | Qld
Q_NIL_STRGTH_COLSF | 28.9167 | 0 | Out = Nil, limit Collinsville SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
V_WEMENSF_FLT_45 | 28.5 | 1.25 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
I_CTRL_ISSUE_ML | 28.25 | 9.0833 | DC Link Control Issue Constraint for Murraylink | Outage | Other
#TORRA3_D_E | 28 | 0 | STSA3.ENERGY * 1 = 40 (Wt = 755) | Other | Direction
N_BROKENHSF_FLT_26 | 28 | 126.1667 | Limit Broken Hill Solar Farm upper limit to 26 MW to manage post contingent voltage oscillation | Outage | NSW
S>NIL_SGBN_SGSE-T2 | 28 | 22.25 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
N_DARLSF_FLT_80 | 27.9167 | 0 | Limit Darlington Pt Solar Farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | NSW
S:V_XPAVC_310 | 27.9167 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage | SA
V::N_BYPASS_HW_SY_xxx | 27.9167 | 2.6667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
N>>N_DPYC_99D_C_1 | 27.6667 | 0 | Out= Darlington Point to Yanco (99D) 132kV line.X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521, avoid O/L Darlington Point to Griffith (99K) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, Feedback | Outage | NSW
V^SML_BUDP_3 | 27.0833 | 42.5833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
V_GANWR_BAT_L_ISL_0 | 26.9167 | 0.083333 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
Q>CMTX | 26.75 | 0 | Out = Clermont T1 or T2 132/66 kV transformer, limit to Clermont Solar Farm to 30MW to prevent overload on remaining transformer | Outage | Qld
Q_STR_211383_KIDSF80 | 26.5833 | 0 | Limit Kidston SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | Qld
Q_STR_211383_RGBSF80 | 26.4167 | 0 | Limit Rugby Run SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | Qld
N_BROKENHSF_FLT_26 | 25.1667 | 126.1667 | Limit Broken Hill Solar Farm upper limit to 26 MW to manage post contingent voltage oscillation | NIL | NSW
V_WEMENSF_FLT_0 | 24.4167 | 100.75 | Limit Wemen Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
Q_STR_211383_RRSF80 | 24.3333 | 0 | Limit Ross River SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | Qld
Q_STR_211383_HAMSF80 | 24.25 | 0 | Limit Hamilton SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | Qld
#MIDDLSF1_E | 23.6667 | 0 | QLIS2M.ENERGY * 1 <= 13 (Wt = 360) | Other | Quick
Q>>NIL_CLWU_RGLC | 23.6667 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL | Qld
Q_STR_211383_WHTSF80 | 23.5833 | 0 | Limit Whitsunday SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | Qld
Q>>NIL_BCCP_RGLC | 23.5 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Qld
V:S_600_HY_TEST_DYN | 23.5 | 21 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
Q_STR_211383_DAYSF80 | 23.4167 | 0 | Limit Daydream SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | Qld
Q_STR_211383_COLSF80 | 23.3333 | 0 | Limit Collinsville SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | Qld
S>DVTX_NIL_DVTX | 23.25 | 0 | Out= One Davenport 275/132kV TX O/S, avoid O/L of remaining Davenport 132/275kV TX on NIL trip. | NIL | SA
Q_STR_211383_CLRSF80 | 23.25 | 0 | Limit Clare SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3.Zero otherwise. Strathmore need to be OS. | Outage | Qld
V::N_MLTX_xxx | 22.5833 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
Q_NIL_STRGTH_HAMSF | 22.3333 | 0 | Out = Nil, limit Hamilton SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
S>V_NWRB_RBMWP3 | 22.3333 | 9.3333 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage | SA
V_KARADSF_FLT_45 | 22.3333 | 162.9167 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | Vic
#QPS5_O_L6 | 22.0833 | 0 | SQPS5Q.LOWER6SEC * 1 = 16 (Wt = 60) | Other | Quick
#QPS5_P_L6 | 22.0833 | 0 | SQPS5Q.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | Quick
S>VMLMHNW1 | 22.0833 | 104.4167 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | SA
NRM_NSW1_VIC1 | 22 | 2.75 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue
#PPCCGT_O_R6 | 21.9167 | 0 | SPPT.RAISE6SEC * 1 = 17 (Wt = 60) | Other | Quick
#PPCCGT_P_R6 | 21.9167 | 0 | SPPT.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | Quick
Q_NIL_STRGTH_WHTSF | 21.9167 | 0 | Out = Nil, limit Whitsunday SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
Q_STR_211383_HAYSF80 | 21.9167 | 0 | Limit Hayman SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | Qld
#MORTLK12_E | 21.8333 | 12.4167 | VM0P2O.ENERGY * 1 = 20 (Wt = 35) | Other | Quick
V_MURRAWRWF_FLT_15 | 21.6667 | 37.4167 | Limit Murra Warra Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
#BRAEMAR2_E | 21.4167 | 0 | QBRA2.ENERGY * 1 <= 173 (Wt = 360) | Other | Quick
#MORTLK11_E | 21.4167 | 0 | VM0P1O.ENERGY * 1 = 220 (Wt = 35) | Other | Quick
V::N_EPMB_xxx | 21.1667 | 0.91667 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
SA_ISLE_LBB_HIGH_SOC | 21.0833 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Lake Bonney battery of 2 MW, except when state of charge is above 70% | Outage | SA
N::V_UTYS_2 | 20.75 | 0 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | NSW
V^^N_MNYS_1 | 20.6667 | 0 | Out = Marulan to Yass (4 or 5) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Vic
T::T_NIL_3 | 20.4167 | 15.9167 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Tas
S^DVBG_SA_NTH | 20.1667 | 0 | Out = Davenport-Bungama 275kV line, Manage voltage collapse in northern SA for the trip of Robertstown-Mokota 275kV line. | Outage | SA
N^^V_CNCW_1 | 19.25 | 16.3333 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
#TORRA2_O_R6 | 19 | 0 | STSA2.RAISE6SEC * 1 = 10 (Wt = 60) | Other | Quick
#TORRA2_P_R6 | 19 | 0 | STSA2.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | Quick
V_GANWRSF_FLT_25 | 18.8333 | 230.8333 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | Vic
N_COLEASF1_FLT_30 | 18.6667 | 0 | Limit Coleambally solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | NSW
I_QNI_ONE_PHASE_N-2 | 18.5 | 34.3333 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage | Other
T^^V_GTSH_1 | 18.5 | 2.75 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
V>>N-NIL_HA | 18.1667 | 75.5 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Vic
N_LIMOSF1_FLT_50 | 18.0833 | 0 | Limit Limondale 1 solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | NSW
V::N_ESTN_MLMOHG_V | 17.9167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage | Vic
V>>V_NIL_7 | 17.9167 | 0 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Vic
SA_ISLE_STRENGTH_BU | 17.5833 | 0.5 | Maximum limit (130 MW) for Bungala Solar Farm for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
V:S_600_HY_TEST | 17.5833 | 20.0833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
V_CWWF_FLT_0 | 17.5833 | 0 | Limit Crowlands Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | Vic
Q_NIL_STRGTH_RRSF | 17.4167 | 0 | Out = Nil, limit Ross River SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
N^^Q_ARTW_B1 | 17.3333 | 0 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | NSW
Q>NIL_SRMB_M020/1 | 17.3333 | 1.75 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Qld
Q_STR_311310_WHTSF | 17.25 | 0 | No limit to Whitsundays SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
V^V_NIL_ARWBBA | 17.25 | 0 | Out = Nil, limit NW Vic generation to 600 MW to avoid voltage collapse on trip of Ararat to Waubra to Ballarat 220 kV line | NIL | Vic
Q_STR_311310_CLRSF | 17.1667 | 0 | No limit to Clare SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
Q_STR_311393_SMSF | 17.1667 | 0 | Limit Sun Metals SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | Qld
Q_STR_311310_COLSF | 17.0833 | 0 | No limit to Collinsville SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
Q_STR_311310_HAMSF | 17.0833 | 0 | No limit to Hamilton SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
Q_STR_311310_HAYSF | 17.0833 | 0 | No limit to Hayman SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
Q_STR_311310_KIDSF | 17.0833 | 0 | No limit to Kidston SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
Q_STR_311310_RRSF | 17.0833 | 0 | No limit to Ross River SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
#TORRA4_O_R6 | 17 | 0 | STSA4.RAISE6SEC * 1 = 10 (Wt = 60) | Other | Quick
#TORRA4_P_R6 | 17 | 0 | STSA4.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | Quick
Q_STR_311310_DAYSF | 17 | 0 | No limit to Daydream SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
Q>EMBW_NIL_EMLV_DS | 16.9167 | 12.5 | Out= 6056 or 6011 Emerald - Comet - Blackwater 66kV line ,limit Emerald SF to 40MW avoid overloading on Emerald - Lilyvale 66kV line, swap if Emerald CBs S612 or S610 or Blackwater CB S605 is closed (DS only) | NIL | Qld
Q_STR_311310_RGBSF | 16.8333 | 0 | No limit to Rugby Run SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | Qld
Q_STR_311393_MEWF | 16.75 | 0 | Limit Mt Emerald SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | Qld
#TORRB3_O_R6 | 16.5 | 0 | STSB3.RAISE6SEC * 1 = 15 (Wt = 60) | Other | Quick
#TORRB3_P_R6 | 16.5 | 0 | STSB3.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | Quick
N_WRWSF_055 | 16.4167 | 12.0833 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | NSW
TVBL_ROC | 16.1667 | 9.6667 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Tas
T_SHWI | 16.1667 | 0 | Out-Sheffield-Wilmot 220KV line | Outage | Tas
Q:NIL_CS | 16 | 57.75 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW) | NIL | Qld
Q_STR_333104_HASF70 | 15.9167 | 0 | Limit Haughton SF to 70 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | Qld
CA_BRIS_4D2AAD32_1 | 15.8333 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG MVPB on trip of DDTS-SMTS1 &DDTS-SMTS2 330KV LINES. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage | Constraint Automation
V_ARARATWF_FLT_0 | 15.75 | 28.5833 | Limit Ararat Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | Vic
N^N_CHLS_1 | 15.6667 | 30.25 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage | NSW
N::N_BYCR_UTYS_2 | 15.5 | 0 | Out = Upper Tumut -Yass(2) and Bannaby to Crookwell(61) , stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | NSW
N^^V_BUDP_1 | 15.5 | 35.1667 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
Q>CPWO_BI_INTACT | 15 | 0 | Out= 813 or 814,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, Feedback | Outage | Qld
N>LSDU9U6_LSDU9U7 | 14.8333 | 29.5833 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
N_FINLYSF_FLT_30 | 14.5 | 0 | Limit Finley solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | NSW
NSA_Q_BARCALDN | 14.25 | 48.9167 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Qld
V_WEMENSF_FLT_44 | 14.25 | 92.4167 | Limit Wemen Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | NIL | Vic
S_WIMK_270 | 14.1667 | 3.6667 | Out =Willalo-Mokota 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF <= 270 MW | Outage | SA
#CPP_3_E | 13.8333 | 3.75 | QCAC3.ENERGY * 1 <= 420 (Wt = 360) | Other | Quick
Q_STR_32392_HASF | 13.8333 | 0 | Limit Haughton SF to 75% of Max capacity if Stan>=3+CalB+C>=2+Glad>=3+ (Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise | Outage | Qld
S>RB_275KV_N_BUS_1 | 13.8333 | 18.25 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | SA
V_MTMERCER_ZERO | 13.4167 | 88.9167 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
T_T_FASH_1_N-2 | 13.25 | 3.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
VS_250_DYN | 13.0833 | 0 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage | Vic
V_OAKHILL_TFB_42 | 13.0833 | 48.4167 | Out = Nil, Oaklands Hill Windfarm upper limit of 42.7 MW due to Oaklands Hill windfarm TFB mode operation, DS only. Swamp out if TFB mode is OFF | NIL | Vic
#PPCCGT_O_L6 | 13 | 0 | SPPT.LOWER6SEC * 1 = 17 (Wt = 60) | Other | Quick
#PPCCGT_O_L60 | 13 | 0 | SPPT.LOWER60SEC * 1 = 15 (Wt = 60) | Other | Quick
#PPCCGT_P_L6 | 13 | 0 | SPPT.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | Quick
#PPCCGT_P_L60 | 13 | 0 | SPPT.LOWER60SEC * 1 <= 0 (Wt = 12) | Other | Quick
V_T_NIL_BL1 | 13 | 61.75 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL | Vic
Q_STR_333104_SMSF70 | 12.8333 | 0 | Limit Sun Metals SF to 70 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | Qld
T^V_NIL_8 | 12.8333 | 5.8333 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
V_KARSF_12INV | 12.6667 | 17.6667 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out otherwise. This is to manage voltage oscillation. DS only | Outage | Vic
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 12.4167 | 28.9167 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL | Qld
VN_0450 | 12.0833 | 0 | Discretionary Vic to NSW transfer upper limit of 450 MW | Outage | Vic
NSA_V_NPSD_100 | 12 | 4.4167 | Newport unit >= 100 MW for Network Support Agreement | Outage | Vic
N_TARALGAWF_ZERO | 11.9167 | 1.9167 | Taralga WF upper limit of 0 MW | Outage | NSW
V^^N_ESTN_MLMOHG_1 | 11.8333 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, avoid voltage collapse around Murray for loss of Basslink when Basslink exporting > 400MW to TAS, will swamp otherwise. | Outage | Vic
SA_ISLE_LBB_LOW_SOC | 11.5 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Lake Bonney battery of 2 MW, except when state of charge is below 30% | Outage | SA
#LADBROK1_E | 11.4167 | 0 | SPEW1.ENERGY * 1 <= 21 (Wt = 360) | Other | Quick
N>N-FLML_9R4 | 11.3333 | 4 | Out= Finley to Mulwala (9R4) or Mulwala to Corowa(997/2) or Corowa to Albury (997/1), avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | Outage | NSW
V_S_NIL_ROCOF | 11.25 | 0.083333 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | Vic
S>>RBTX2_NIL_RBTX1 | 11.0833 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Robertstown 275/132kV TX1 on Nil trip, Feedback | NIL | SA
#MEWF1_E | 11.0833 | 4.9167 | QWKM1M.ENERGY * 1 <= 20 (Wt = 360) | Other | Quick
V::N_DDSM_xxx | 11.0833 | 7.1667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
N>>N-PKWL_94K_1 | 11 | 0 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Forbes to Cowra (998) line, Feedback | Outage | NSW
S-WIWF_0 | 11 | 1.4167 | Discretionary upper limit for Willogolechi WF generation of 0 MW | Outage | SA
T_GRANVH_ZERO | 10.8333 | 0 | Granville Harbour wind farm upper limit of 0 MW | Outage | Tas
V>>V_KTS_TX_A2_2A_R | 10.8333 | 4.3333 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
T_T_FASH_10_N-2 | 10.75 | 0.58333 | Out = NIL, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain John Butters and Bastyan to 0 MW as per TAS Networks advice | Outage | Tas
#DRYCGT3_D_E | 10.6667 | 0 | SDCA3.ENERGY * 1 = 35 (Wt = 755) | Other | Direction
S>NIL_BWMP_HUWT | 10.6667 | 8.6667 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
V_OWF_TGTSNRBHTN_30 | 10.6667 | 65.0833 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Vic
N^^V_DDWG | 10.5833 | 5.6667 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
#BRAEMAR3_E | 10.5 | 0 | QBRA3.ENERGY * 1 <= 173 (Wt = 360) | Other | Quick
Q_STR_21138_KIDSF80 | 10.5 | 0 | Limit Kidston SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
S_SECB_LG-2 | 10.5 | 13.6667 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 2 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
V>>V_ROTS_TX_2A_R | 10.4167 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
V_YENDONWF_ZERO | 10.4167 | 0 | Yendon Wind Farm upper limit of 0 MW | Outage | Vic
S>NIL_NIL_NWMH2 | 10.3333 | 77.3333 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
VN_0500 | 10.3333 | 0 | Discretionary Vic to NSW transfer upper limit of 500 MW | Outage | Vic
#TORRA2_O_L6 | 10 | 0 | STSA2.LOWER6SEC * 1 = 10 (Wt = 60) | Other | Quick
#TORRA2_O_L60 | 10 | 0 | STSA2.LOWER60SEC * 1 = 25 (Wt = 60) | Other | Quick
#TORRA2_P_L6 | 10 | 0 | STSA2.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | Quick
#TORRA2_P_L60 | 10 | 0 | STSA2.LOWER60SEC * 1 <= 0 (Wt = 12) | Other | Quick
N_SILVRWF_FLT_45_MAX | 9.8333 | 0 | Limit Silverton wind farm upper limit to 45 MW with one of the following solar farms generating: Broken Hill, Limondale 1, Limondale 2, Sunraysia, Darlington Pt, Finley SF. Swamp out if all these solar farms are off. | Outage | NSW
#PPCCGT_O_E | 9.6667 | 830.25 | SPPT.ENERGY * 1 = 202 (Wt = 755) | Other | Direction
S>>CGTB1_TUTB_MOTB | 9.6667 | 0 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage | SA
S>BRDV_BWPA_RHBR | 9.6667 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T_LIPM1_SLOAD_1_N-2 | 9.5 | 10.75 | Out=Liapootah-Waddamana-Palmerston #1 220kV line and associated 220kV CBs at Waddamana I/S, loss of #2 parallel 220 kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Tas
Q::N_AR_CP2_AR_2L-G | 9.4167 | 0 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
Q_CS_1850 | 9.3333 | 214.1667 | Qld Central to Qld South upper transfer limit of 1850MW (discretionary) | Outage | Qld
Q_STR_311393_10HASF | 9.3333 | 0 | Limit Haughton to 20%of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad)>=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG),50%if Stan>=3+CalB+C>=3+Glad>=3+(Stan+Cal+Glad)>=10+Kar>=3+Bar>=1,NQLD>650&670(AVG),Ross_FN>350&370(AVG),0 otherwise. | Outage | Qld
S_SNOWNTH1_ZERO | 9.3333 | 0 | Discretionary upper limit for Snowtown 2 North WF generation of 0 MW | Outage | SA
#BNGSF1_D_E | 9.25 | 0 | SBEM1B.ENERGY * 1 <= 0 (Wt = 755) | Other | Direction
#BNGSF2_D_E | 9.25 | 0 | SBEM2B.ENERGY * 1 <= 0 (Wt = 755) | Other | Direction
#TBSF1_D_E | 9.25 | 0 | STBS1T.ENERGY * 1 <= 0 (Wt = 755) | Other | Direction
#QPS5_D_E | 9.1667 | 0 | SQPS5Q.ENERGY * 1 = 74 (Wt = 755) | Other | Direction
V_KARADSF_FLT_45 | 9.1667 | 162.9167 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | NIL | Vic
V_BULGWF_ISL_0 | 9.0833 | 0 | Bulgana Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
VTBL_ROC | 9.0833 | 9.6667 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Vic
#VIC1_E_20200310 | 9 | 0 | Multiple VIC1 LHS <= 113 (Wt = 360) | Other | Quick
S_SNOWSTH1_ZERO | 9 | 0 | Discretionary upper limit for Snowtown 2 South WF generation of 0 MW | Outage | SA
Q^^N_AR_SVC_1 | 8.9167 | 1.5833 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Qld
N>N-NIL_MBDU | 8.8333 | 61.8333 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
N^^Q_NIL_A | 8.8333 | 24.6667 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | NSW
N_COLEASF1_ZERO | 8.8333 | 55.25 | Coleambally solar farm upper limit of 0 MW and all inverters disconnected. | Outage | NSW
N>>N_DPYC_99D_C_2 | 8.75 | 0 | Out= Darlington Point to Yanco (99D) 132kV line.X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521, avoid O/L Griffith to Yanco (99J) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, Feedback | Outage | NSW
N_SILVERTWF_FLT_100 | 8.75 | 0 | Limit Silverton Wind Farm upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | NSW
N_BROKENHSF_FLT_30 | 8.6667 | 43.5833 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | NSW
SA_ISLE_STRENGTH | 8.6667 | 3.75 | Maximum limit (1300 MW) for SA non-synchronous generation for system strength requirements when SA is at risk of separation or when islanded. | Outage | SA
#TORRA1_O_R6 | 8.5 | 0 | STSA1.RAISE6SEC * 1 = 10 (Wt = 60) | Other | Quick
#TORRA1_P_R6 | 8.5 | 0 | STSA1.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | Quick
#TORRA4_O_E | 8.5 | 113.3333 | STSA4.ENERGY * 1 >= 70 (Wt = 755) | Other | Direction
#TORRA4_O_L6 | 8.5 | 0 | STSA4.LOWER6SEC * 1 = 10 (Wt = 60) | Other | Quick
#TORRA4_O_L60 | 8.5 | 0 | STSA4.LOWER60SEC * 1 = 25 (Wt = 60) | Other | Quick
#TORRA4_P_L6 | 8.5 | 0 | STSA4.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | Quick
#TORRA4_P_L60 | 8.5 | 0 | STSA4.LOWER60SEC * 1 <= 0 (Wt = 12) | Other | Quick
#TORRB3_O_R60 | 8.5 | 0 | STSB3.RAISE60SEC * 1 = 30 (Wt = 60) | Other | Quick
#TORRB3_P_R60 | 8.5 | 0 | STSB3.RAISE60SEC * 1 <= 0 (Wt = 12) | Other | Quick
V_NUMURKAH_ZERO | 8.5 | 0 | Numurkah Solar Farm upper limit of 0 MW | Outage | Vic
N::N_UTYS_2 | 8.3333 | 0 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | NSW
QNI_SOUTH_1150_DYN | 8.3333 | 3.75 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL | Qld
Q_NQ_SEMI_ZERO | 8.25 | 0 | Limit all North Qld semi-scheduled generators to zero | Outage | Qld
VN_0900 | 8.1667 | 0 | Discretionary Vic to NSW transfer upper limit of 900 MW | Outage | Vic
S-SNWWF_0 | 8.0833 | 6.25 | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
#TORRB3_O_L6 | 8 | 0 | STSB3.LOWER6SEC * 1 = 15 (Wt = 60) | Other | Quick
#TORRB3_O_L60 | 8 | 0 | STSB3.LOWER60SEC * 1 = 30 (Wt = 60) | Other | Quick
#TORRB3_P_L6 | 8 | 0 | STSB3.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | Quick
#TORRB3_P_L60 | 8 | 0 | STSB3.LOWER60SEC * 1 <= 0 (Wt = 12) | Other | Quick
V_S_HEYWOOD_UFLS | 7.8333 | 0 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC.Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL | Vic
Q_STR_311393_DAYSF | 7.75 | 0 | No upper limit to Daydream SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | Qld
T>T_NIL_BL_3C | 7.75 | 2.1667 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
V_KIATAWF_FLT_15 | 7.6667 | 43.4167 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
#FISHER_D_E | 7.5833 | 0 | TFI11.ENERGY * 1 = 2 (Wt = 755) | Other | Direction
#LEM_WIL_D_E | 7.5833 | 0 | TSH11.ENERGY * 1 = 2 (Wt = 755) | Other | Direction
V_GANWR_BAT_L_FLT_0 | 7.5833 | 0 | Limit Gannawarra Battery (Load Component) upper limit to 0 MW to manage post contingent voltage oscillation | Outage | Vic
V_GANWRSF_FLT_30 | 7.4167 | 0 | Limit Gannawarra solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | Vic
#OSB-AG_E | 7.25 | 0.083333 | SNBN1.ENERGY * 1 <= 147 (Wt = 360) | Other | Quick
S_WATERLWF_RB | 7 | 21.25 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | SA
V^SML_BEKG_4 | 7 | 0 | Out = Bendigo to Kerang 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Vic
Q_STR_211383_RGBSF50 | 6.9167 | 0 | Limit Rugby Run SF to 50% capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8+Kar>=3. Zero otherwise | Outage | Qld
Q:N_TW330_CB5102_OSC | 6.8333 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage | Qld
VN_0500_DYN | 6.8333 | 0 | VIC to NSW interconnector upper transfer limit of 500 MW, dynamic headroom, DS formulation only. | Outage | Vic
Q_STR_311393_RRSF | 6.6667 | 0 | No upper limit to Ross River SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | Qld
T_T_FASH_7_N-2 | 6.6667 | 7.8333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation <= 110% of West Coast load | Outage | Tas
SA-GEN_RAMP_ZERO | 6.5833 | 0 | Ramp a number of SA scheduled/semi-scheduled generation to 0 MW and hold at zero when SA operational demand <=700 MW; Refer to TOA 397 | Outage | SA
N_GUNNING1_ZERO | 6.5 | 12.8333 | Gunning unit upper limit of 0 MW | Outage | NSW
Q_STR_311393_KIDSF | 6.5 | 0 | No upper limit to Kidston SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | Qld
V^SML_ARWB_3 | 6.5 | 10.5 | Out = Ararat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
Q_STR_311393_COLSF | 6.4167 | 0 | No upper limit to Collinsville SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | Qld
S_SECB_LG-1 | 6.4167 | 1.5 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
Q_STR_NQ275_MEWF_25 | 6.3333 | 0 | Out = One of the 275 kV feeders North of Calvale and Calliope, limit Mt Emerald WF to 25 % capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=2 +Bar>=1. Zero otherwise | Outage | Qld
V_WEMENSF_5INV | 6.3333 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 5. Constraint swamp out if number of inverter available not exceed 5. This is to manage voltage oscillation. DS only | Outage | Vic
NQ_VST_ISLE_A | 6.25 | 0 | Separation between Vic and NSW, allow Vic-NSW to supply Wagga or Northern Victoria | Outage | NSW
V_KIAMSF_FLT_40 | 6.25 | 0 | Limit Kiamal solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | Vic
#OSB-AG_O_E | 6.1667 | 65.5833 | SNBN1.ENERGY * 1 = 170 (Wt = 755) | Other | Direction
V_GANWR_SF_BAT_50 | 6.1667 | 16.4167 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Vic
Q>>WOSP_WOPW_WOGP_2 | 6.0833 | 2.75 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Qld
Q_NIL_STRGTH_DAYSF | 6.0833 | 0 | Out = Nil, limit Daydream SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
Q_STR_311393_10MEWF | 6.0833 | 0 | Limit Mt Emerald to 20% if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad)>=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG),65%if Stan>=3+CalB+C>=3+Glad>=3+(Stan+Cal+Glad)>=10+Kar>=3+Bar>=1,NQLD>650&670(AVG),Ross_FN>350&370(AVG),0 otherwise. | Outage | Qld
V_MURRAWRWF_30WT | 6 | 4.1667 | Limit Murra Warra Wind Farm upper limit to 0 MW if number of turbine ON exceed 30. Constraint swamp out if number of turbine ON not exceed 30. This is to manage voltage oscillation. DS only | Outage | Vic
NRM_QLD1_NSW1 | 5.9167 | 9.25 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue
Q_STR_21138_COLSF80 | 5.9167 | 0 | Limit Collinsville SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
T_T_FASH_2_N-2 | 5.9167 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh >= 90% of West Coast load | Outage | Tas
Q_STR_311393_CLRSF | 5.75 | 0 | No upper limit to Clare SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),Zero otherwise. . | Outage | Qld
Q_STR_311393_HAMSF | 5.75 | 0 | No upper limit to Hamilton SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | Qld
Q_STR_311393_RGBSF | 5.75 | 0 | No upper limit to Rugby Run SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | Qld
Q_STR_311393_WHTSF | 5.6667 | 0 | No upper limit to Whitsunday SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | Qld
NSA_V_BDL0xxx | 5.5833 | 7.4167 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Vic
#SA1_E_20200204 | 5.5833 | 0 | Multiple SA1 LHS <= 250 (Wt = 360) | Other | Quick
Q_STR_21138_CLRSF80 | 5.5833 | 0 | Limit Clare SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
Q_STR_311393_HAYSF | 5.5833 | 0 | No upper limit to Hayman SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | Qld
VN_1100 | 5.5833 | 0 | Discretionary Vic to NSW transfer upper limit of 1100 MW | Outage | Vic
N_COLEASF1_FLT_45 | 5.4167 | 0 | Limit Coleambally solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | NSW
SA_ISLE_HPR_LOW_SOC | 5.4167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Hornsdale battery of 2 MW, except when state of charge is below 30% | Outage | SA
S_DVRB2_270 | 5.4167 | 66.8333 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | SA
Q_STR_NQ275_HASF_25 | 5.3333 | 0 | Out = One of the 275 kV feeders North of Calvale and Calliope, limit Haughton SF to 25 % capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=2 +Bar>=1. Zero otherwise | Outage | Qld
S>>NIL_RBTX_RBTX_1 | 5.3333 | 0 | Out= Nil, avoid O/L of one Robertstown 275/132kV TX on trip of other Robertstown 275/132kV TX, Feedback | NIL | SA
V_BANNERTSF_FLT_44 | 5.3333 | 12 | Limit Bannerton Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | NIL | Vic
#TUMUT3_E | 5.0833 | 0 | NLTS8.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
V^^N_X_DTSS_MNYS_1 | 5.0833 | 0 | Out = Dapto to Sydney South (11) and Marulan to Yass (4 or 5) 330kV lines, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Vic
#VIC1_E_20200131 | 5 | 0 | Multiple VIC1 LHS = 460 (Wt = 360) | Other | Quick
NC_Q_SRSF1 | 4.9167 | 1.0833 | Non Conformance Constraint for SUSANRIVERSOLARFARM | Other | Non-Conformance
S>>RBTX2_RBTX1_WEWT | 4.9167 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage | SA
V^SML_BAWB_3 | 4.9167 | 26.75 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
Q_STR_NQ275_SMSF_25 | 4.8333 | 0 | Out = One of the 275 kV feeders North of Calvale and Calliope, limit Sun Metals SF to 25 % capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=2 +Bar>=1. Zero otherwise | Outage | Qld
V_VS_LB_CAN_50 | 4.75 | 44.1667 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage | SA
#DDSF1_E | 4.75 | 12.25 | QBRS1D.ENERGY * 1 = 0 (Wt = 35) | Other | Quick
N>>N-964_DC | 4.75 | 3.9167 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage | NSW
S:VS_700_HY_TEST_DYN | 4.75 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
VN_0800_DYN | 4.75 | 0 | VIC to NSW interconnector upper transfer limit of 800 MW, dynamic headroom, DS formulation only. | Outage | Vic
N>>N-NIL_DPTX_2 | 4.6667 | 0.58333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | NSW
NV_0500 | 4.5833 | 0 | Discretionary NSW to Vic transfer upper limit of 500 MW | Outage | NSW
S>>BGBW_TWPA_TPRS | 4.5833 | 0 | Out= Bungama - Blyth West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West- Para 275kV line, Feedback | Outage | SA
VSML_-150 | 4.5833 | 0 | Vic to SA on ML upper transfer limit of -150 MW | Outage | Vic
Q_STR_311393_10SMSF | 4.5 | 0 | Limit Sun Metals to 20% if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad)>=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG),50%if Stan>=3+CalB+C>=3+Glad>=3+(Stan+Cal+Glad)>=10+Kar>=3+Bar>=1,NQLD>650&670(AVG),Ross_FN>350&370(AVG),0 otherwise. | Outage | Qld
T::T_HA_GT_PM_4 | 4.5 | 5.4167 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Tas
S:VS_XPAVC_460 | 4.4167 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood and Murraylink combined upper transfer limit of 460 MW based on oscillatory stability. | Outage | SA
SVML_FLT_150 | 4.4167 | 8 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | SA
T>T_LIPM_110_2B | 4.4167 | 0.083333 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
V>>N-JNWG_RADIAL_1 | 4.4167 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
T>T_PMSH_IMP_4F | 4.3333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>V_NIL_14 | 4.25 | 0 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Vic
N^^V_SMTXF2_1 | 4.1667 | 11.1667 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
S>>TBTU_TBCG_TBMO | 4.1667 | 0.16667 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage | SA
S>HUWT_BGTX_RHBR-T | 4.1667 | 0 | Out= Hummocks-Waterloo 132kV line, avoid O/L Redhill-Brinkworth T 132kV line on trip of Bungama 132/275kV TX, Feedback | Outage | SA
T_T_TI_GH_RC12_250 | 4.1667 | 0 | Discretionary 250 MW upper limit on Tribute, Granville Harbour, Reece 1 and 2 generation | Outage | Tas
V^SML_KGRC_4 | 4.1667 | 4.9167 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Vic
V_KARADSF_FLT_0 | 4.1667 | 141 | Limit Karadoc solar farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | Vic
V_SV_MLMO_NETT | 4.1667 | 104.25 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW. Swamp out when MOPS/DUNDWF not generating | Outage | Vic
S>BGTX_BGBR_HUWT | 4.0833 | 0 | Out= Bungama 275/132kV TX, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap windfarm), Feedback | Outage | SA
SVML_FLT_125 | 4.0833 | 0 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | SA
V::N_SMF2_xxx | 4.0833 | 3.8333 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V_KIAMSF_0 | 4.0833 | 0 | Out = Kiamal Syncon, limit Kiamal solar farm to 0 MW | Outage | Vic
N>N-NIL_DC | 4 | 73.4167 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL | NSW
#PPCCGT_E | 3.9167 | 0 | SPPT.ENERGY * 1 = 170 (Wt = 755) | Other | Quick
S_SECB_LG3 | 3.9167 | 2.6667 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
T>>T_NIL_BL_EXP_7C | 3.9167 | 11.0833 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
VN_0900_DYN | 3.9167 | 0 | VIC to NSW interconnector upper transfer limit of 900 MW, dynamic headroom, DS formulation only. | Outage | Vic
N_FINLYSF1_ZERO | 3.8333 | 4.6667 | Finley solar farm upper limit of 0 MW and all inverters disconnected. | Outage | NSW
#V-S-MNSP1_I_E | 3.75 | 0 | V-S-MNSP1. * -1 >= 0 (Wt = 360) | Other | Quick
N^^Q_MUTW_1_B1 | 3.75 | 0 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage | NSW
T_T_FASH_8_N-2 | 3.75 | 0.083333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation >= 90% of West Coast load | Outage | Tas
V>>V_ARCW_7 | 3.75 | 0 | Out = Ararat to Crowlands 220kV line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
VSML_080 | 3.6667 | 0 | Vic to SA on ML upper transfer limit of 80 MW | Outage | Vic
N::N-X_MNYS_CNLT_2 | 3.5833 | 0 | Out= Marulan-Yass (4 or 5) and Canberra to Lower Tumut (07) or Upper Tumut (01) 330kV line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | NSW
S>X_DV-BR-PA_08 | 3.5833 | 6.25 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Hummocks-Waterloo 132kV lineon trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
VN_0800 | 3.5833 | 0 | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage | Vic
T_V_NIL_BL1 | 3.5 | 6.0833 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL | Tas
NC_Q_MPP_1 | 3.4167 | 0.41667 | Non Conformance Constraint for Millmerran 1 Power Station | Other | Non-Conformance
Q_STR_21138_CMSF50 | 3.4167 | 0 | Limit Clermont SF to 50% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
SA_ISLE_HPR_HIGH_SOC | 3.4167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Hornsdale battery of 2 MW, except when state of charge is above 70% | Outage | SA
T>T_NIL_BL_5C | 3.4167 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
Q_STR_211383_9_CLRSF | 3.3333 | 0 | Limit Clare SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
Q_STR_211383_9_COLSF | 3.3333 | 0 | Limit Collinsville SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
Q_STR_211383_9_DAYSF | 3.3333 | 0 | Limit Daydream SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
Q_STR_211383_9_HAMSF | 3.3333 | 0 | Limit Hamilton SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
Q_STR_211383_9_HAYSF | 3.3333 | 0 | Limit Hayman SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
Q_STR_211383_9_KIDSF | 3.3333 | 0 | Limit Kidston SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
Q_STR_211383_9_RGBSF | 3.3333 | 0 | Limit Rugby Run SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
Q_STR_211383_9_RRSF | 3.3333 | 0 | Limit Ross River SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
Q_STR_211383_9_WHTSF | 3.3333 | 0 | Limit Whitsunday SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | Qld
T>T_NIL_BL_110_4 | 3.3333 | 39.1667 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Tas
VSML_020 | 3.3333 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage | Vic
V_BANSF_22INV | 3.3333 | 17.5833 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 22. Constraint swamp out if number of inverter available not exceed 22. This is to manage voltage oscillation. DS only | Outage | Vic
V_WEMENSF_21INV | 3.25 | 0.91667 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 21. Constraint swamp out if number of inverter available not exceed 21. This is to manage voltage oscillation. DS only | Outage | Vic
#MINTARO_D_E | 3.25 | 0 | SMPS.ENERGY * 1 = 30 (Wt = 755) | Other | Direction
NC_Q_YARANSF1 | 3.25 | 0 | Non Conformance Constraint for YARRANLEA SOLAR FARM | Other | Non-Conformance
NRM_SA1_VIC1 | 3.25 | 0.16667 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue
S>>V_NIL_NIL_RBMW3 | 3.25 | 0 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL | SA
T>T_CRNN_3 | 3.25 | 0.83333 | Out= Creek Rd to New Norfolk 110 kV line, avoid O/L New Norfolk to Chapel St 110 kV line for loss of Waddamana to Palmerston 110 kV line, Feedback | Outage | Tas
V_ELAINEWF_ZERO | 3.25 | 0 | Elaine Wind Farm upper limit of 0 MW | Outage | Vic
#DRYCGT1_D_E | 3.1667 | 0 | SDCA1.ENERGY * 1 = 35 (Wt = 755) | Other | Direction
#DRYCGT2_D_E | 3.1667 | 0 | SDCA2.ENERGY * 1 = 0 (Wt = 755) | Other | Direction
#GRANWF1_E | 3.1667 | 0 | TGH11G.ENERGY * 1 <= 106 (Wt = 360) | Other | Quick
QNI_SOUTH_1050_DYN | 3.1667 | 0 | QLD to NSW on QNI upper transfer limit of 1050 MW, dynamic headroom, DS formulation only. | Outage | Qld
S>>NIL_BWMP_BRTW | 3.1667 | 0 | Out= Nil, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | SA
#STWF1_E | 3.0833 | 0.25 | NBKW1S.ENERGY * 1 <= 170 (Wt = 35) | Other | Quick
S>>X_RBTU+RB_SBUS_15 | 3.0833 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
T>T_FASH_1_N-2 | 3.0833 | 6.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, limit Bastyan, John Butters & Mackintosh to west coast load plus Hampshire link line rating | Outage | Tas
V::N_X_ARWBBA_xxx | 3.0833 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
VN_1000 | 3.0833 | 0 | Discretionary Vic to NSW transfer upper limit of 1000 MW | Outage | Vic
V_GANNSF_12INV | 3.0833 | 1.4167 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out if number of inverter available not exceed 12. This is to manage voltage oscillation. DS only | Outage | Vic
#SA1_E_20201203 | 3 | 0 | Multiple SA1 LHS <= 150 (Wt = 360) | Other | Quick
S>>DVBG_RBTU_WEWT | 3 | 0 | Out= Davenport-Bungama 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
NC_Q_MPP_2 | 2.9167 | 0.5 | Non Conformance Constraint for Millmerran 2 Power Station | Other | Non-Conformance
S-BUPV1_0 | 2.9167 | 2.25 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | SA
S-BUPV2_0 | 2.9167 | 0 | Discretionary upper limit for Bungala Stage 2 PV generation of 0 MW | Outage | SA
S-LGAPWF1_0 | 2.9167 | 0 | Discretionary upper limit for Lincoln Gap Wind Farm of 0 MW | Outage | SA
S-TBSF1_0 | 2.9167 | 0 | Discretionary upper limit for Tailem Bend (Coorong) Solar PV of 0 MW | Outage | SA
S_HDWF1_0 | 2.9167 | 0.083333 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | SA
V::N_X_HWSM_HWCB_xxx | 2.9167 | 0 | Out=Hazelwood-South Morang & Hazelwood-Cranbourne 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#MTGELWF1_E | 2.8333 | 3.75 | VGTW1M.ENERGY * 1 <= 66 (Wt = 360) | Other | Quick
N>>N-PKWL_94K_3 | 2.8333 | 0 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | Outage | NSW
S>>X_RBTU+RB_SBUS_16 | 2.8333 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage | SA
V_MURRAWR_ZERO | 2.8333 | 0.33333 | Murra Warra wind farm upper limit of 0 MW | Outage | Vic
V_OWF_NRB_0 | 2.8333 | 9.6667 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Vic
NC_Q_CLERMSF1 | 2.75 | 0.25 | Non Conformance Constraint for CLERMONT SOLAR FARM | Other | Non-Conformance
NC_S_BNGSF2 | 2.75 | 0 | Non Conformance Constraint for Bungala #2 Solar Farm | Other | Non-Conformance
SVML_140 | 2.75 | 0 | SA to Vic on ML upper transfer limit of 140 MW | Outage | SA
#HALLWF2_E | 2.6667 | 5.5833 | SMOK1H.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
#CG1_E | 2.5833 | 0 | NCLG1D.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
#CG2_E | 2.5833 | 0 | NCLG2D.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
#CG3_E | 2.5833 | 0 | NCLG3D.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
Q>N-MUTE_758 | 2.5833 | 0.83333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
Q_DAYDSF1_ZERO | 2.5833 | 0 | Daydream solar farm upper limit of 0 MW | Outage | Qld
V_GANNSF_11INV | 2.5833 | 1.5833 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Constraint swamp out otherwise. DS only | Outage | Vic
S-DLBAT-G_0 | 2.5 | 3.75 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW | Outage | SA
S_AG_0 | 2.5 | 0 | Discretionary upper limit for Angaston generation | Outage | SA
N_FINLYSF_FLT_50 | 2.4167 | 0 | Limit Finley solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | NSW
V_GANNSF_10INV | 2.4167 | 0 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 10. Constraint swamp out if number of inverter available not exceed 10. This is to manage voltage oscillation. DS only | Outage | Vic
V_KIATA_ZERO | 2.4167 | 0 | Kiata Wind Farm upper limit of 0 MW | Outage | Vic
Q:N_1078 | 2.3333 | 25.75 | QNI oscillatory stability limit of 1078 MW | Outage | Qld
S^DVBR_SA_NTH | 2.3333 | 0.91667 | Out = Davenport-Brinkworth 275kV line, Manage voltage collapse in northern SA for the trip of Davenport-Belalie 275kV line | Outage | SA
NC_N_VP5 | 2.3333 | 1.8333 | Non Conformance Constraint for Vales Point VP5 Power Station | Other | Non-Conformance
T_V_FCSPS_RAMP | 2.3333 | 0 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
V_MWWF_GFT1_115 | 2.3333 | 0 | Out= Murra Warra WF associated fast tripping scheme 1 (disabled), Limit Murra Warra Windfarm upper limit to 115 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
NC_V_MUWAWF1 | 2.25 | 0.083333 | Non Conformance Constraint for MURRA WARRA WF 1 | Other | Non-Conformance
N^^V_MSDD2 | 2.1667 | 0 | Out = Dederang to Murray 330 kV line, avoid voltage collapse at Darlington Point for loss of the remaining Dederang to Murray 330 kV line | Outage | NSW
N_COLEASF1_FLT_50 | 2.1667 | 0 | Limit Coleambally solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | NSW
S_HPRG1_E | 2.1667 | 7.3333 | Out= Nil, Hornsdale Battery generation energy target <= 30 MW | NIL | SA
S_LONSD_0 | 2.1667 | 0 | Discretionary upper limit for Lonsdale generation | Outage | SA
S_PTSTAN_0 | 2.1667 | 0 | Discretionary upper limit for Port Stanvac generation | Outage | SA
V::N_SMSC_xxx | 2.1667 | 21.3333 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
VN_1000_DYN | 2.1667 | 0 | VIC to NSW interconnector upper transfer limit of 1000 MW, dynamic headroom, DS formulation only. | Outage | Vic
V_ARARAT_ZERO | 2.1667 | 3.1667 | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
V_WEMENSF_ZERO | 2.1667 | 11.3333 | Wemen Solar Farm upper limit of 0 MW | Outage | Vic
#NSW1_E_20200915 | 2.0833 | 0 | Multiple NSW1 LHS <= 135 (Wt = 35) | Other | Quick
#V-SA_RAMP_I_F | 2.0833 | 20 | V-SA >= MIN(-155, InitialFlow + 50) (Wt=35) | Other | Quick
N^N_KKLS_1 | 2.0833 | 0.83333 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | NSW
N_FINLEYSF_49_INV | 2.0833 | 2 | Limit Finley Solar Farm upper limit to 0 MW if number of inverter available exceed 49. Dispatch only. swamped out if Inverters are within the limit. | Outage | NSW
V::S_NIL_MAXG_xxx | 2.0833 | 4.6667 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
VN_1100_DYN | 2.0833 | 0 | VIC to NSW interconnector upper transfer limit of 1100 MW, dynamic headroom, DS formulation only. | Outage | Vic
#QPS5_O_E | 2 | 9.4167 | SQPS5Q.ENERGY * 1 >= 74 (Wt = 755) | Other | Direction
N::N_MNYS_2 | 2 | 0 | Out= Marulan-Yass (4 or 5), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | NSW
NC_N_MP2 | 2 | 0.16667 | Non Conformance Constraint for Mt Piper 2 Power Station | Other | Non-Conformance
N_NYNGANSF_010 | 2 | 0 | Nyngan Solar Farm upper limit of 10 MW | Outage | NSW
S-HDWF2_0 | 2 | 0 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW | Outage | SA
T_FARC2_2 | 2 | 0 | Out=Farrell - Reece 2 220KV line. Discretionary 144 MW limit on Reece 1 + Granville Harbour WF | Outage | Tas
VN_0700 | 2 | 0 | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage | Vic
#KIAMSF1_E | 1.9167 | 0 | VKMT1K.ENERGY * 1 <= 100 (Wt = 360) | Other | Quick
CA_BRIS_4D69957C_1 | 1.9167 | 0 | Constraint Automation, O/L 275KV_8875:8875:I:275@H73_RAGL@QLD for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage | Constraint Automation
N>N-GITN_TE_B1 | 1.9167 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
NC_N_GULLRWF2 | 1.9167 | 0 | Non Conformance Constraint for GULLEN RANGE WF2 | Other | Non-Conformance
NC_N_VP6 | 1.9167 | 0.91667 | Non Conformance Constraint for Vales Point VP6 Power Station | Other | Non-Conformance
N^^Q_LS_VC_B1 | 1.9167 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
Q>ISTX | 1.9167 | 0 | Out = Isis T2 132/66 kV transformer, limit Childers Solar Farm to 46MW to prevent overload on remaining transformer | Outage | Qld
S_HDWF3_0 | 1.9167 | 0 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW | Outage | SA
S_LB2WF_CONF | 1.9167 | 4.3333 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
V>SMLMHNW1 | 1.9167 | 4.5833 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Vic
#CRURWF1_E | 1.8333 | 0 | NCDS1C.ENERGY * 1 <= 49 (Wt = 360) | Other | Quick
CA_BRIS_4DE6DCA9_1 | 1.8333 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage | Constraint Automation
V_BANSF_20INV | 1.8333 | 3.5 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 20. Constraint swamp out otherwise. DS only | Outage | Vic
CA_BRIS_4DE47816_1 | 1.75 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage | Constraint Automation
T::T_NIL_2 | 1.75 | 52.3333 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL | Tas
VSML_100 | 1.75 | 0 | Vic to SA on ML upper transfer limit of 100 MW | Outage | Vic
V_BANSF_5INV | 1.75 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 5. Constraint swamp out if number of inverter available not exceed 5. This is to manage voltage oscillation. DS only | Outage | Vic
V_KARSF_19INV | 1.75 | 2.75 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | Outage | Vic
I_CTRL_ISSUE_TE | 1.6667 | 20.9167 | DC Link Control Issue Constraint for Terranora | Outage | Other
NC_N_GULLRWF1 | 1.6667 | 0 | Non Conformance Constraint for Gullen Range Wind Farm | Other | Non-Conformance
NC_V_YWPS4 | 1.6667 | 0.58333 | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Other | Non-Conformance
N_BOMENSF1_ZERO | 1.6667 | 0 | Bomen SF upper limit of 0 MW and all inverters disconnected. | Outage | NSW
VN_0700_DYN | 1.6667 | 0 | VIC to NSW interconnector upper transfer limit of 700 MW, dynamic headroom, DS formulation only. | Outage | Vic
V_KIAMAL_0INV | 1.6667 | 0 | Constraint to violate if Kiamal Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | Vic
N>>N-NIL_01N | 1.5833 | 0 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | NSW
N>>N-WGYS_OPEN_4 | 1.5833 | 0 | Out = Wagga-Yass 132 kV Parallel lines Opened, avoid O/L Lower Tumut to Canberra (07) on trip of Lower Tumut to Yass (3) line, Feedback | Outage | NSW
N>N-ARCH_87_TE_C1 | 1.5833 | 0 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage | NSW
Q::N_ARSVC_AR_2L-G | 1.5833 | 5.6667 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
S:V_PA_SVC_270 | 1.5833 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage | SA
S>>RB_275KV_S_BUS_10 | 1.5833 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage | SA
S>>V_CGTI_PPPG_TIPA | 1.5833 | 0 | Out= Cherry Gardens - Torrens Island 275kV line, avoid O/L Torrens Island - Para 275kV line on trip of Pelican Point - Parafield Gardens West 275kV line, Feedback | Outage | SA
V::S_KHKN_MAXG | 1.5833 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
V_MWWF_115 | 1.5833 | 0 | Murra Warra Wind Farm upper limit of 115 MW | Outage | Vic
#BNGSF1_E | 1.5 | 0 | SBEM1B.ENERGY * 1 <= 75 (Wt = 360) | Other | Quick
NC_V_LOYYB2 | 1.5 | 0.083333 | Non Conformance Constraint for Loy Yang B2 Power Station | Other | Non-Conformance
N_BODWF1_ZERO | 1.5 | 0.25 | Bodangora wind farm upper limit of 0 MW and all turbines disconnected | Outage | NSW
Q^^NIL_CS | 1.5 | 0 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation | NIL | Qld
S>>CGTB1_TBTU_TBMO | 1.5 | 0 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
SVML_015 | 1.5 | 0 | SA to Vic on ML upper transfer limit of 15 MW | Outage | SA
V>EPTT | 1.5 | 0 | Outage =Eildon to Thomastown 220kV line, avoid overloading a Mt Beauty to Dederang 220kV line for trip of the parallel line | Outage | Vic
VS_250 | 1.5 | 0 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Vic
NC_V_YWPS3 | 1.4167 | 1.9167 | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Other | Non-Conformance
N_CROOKWF2_ZERO | 1.4167 | 0 | Crookwell wind farm upper limit of 0 MW and all turbines disconnected | Outage | NSW
T^V_HA_GT_220_1 | 1.4167 | 0 | Out= one George Town to Hadspen 220kV line, limit post-contingency loading on Palmerston to Sheffield 220kV line (flow to north) to avoid voltage collapse on trip of the remaining Hadspen to George Town 220kV line. | Outage | Tas
#TORRB1_E | 1.3333 | 0 | STSB1.ENERGY * 1 = 40 (Wt = 755) | Other | Quick
NC_N_UPPTUMUT | 1.3333 | 0 | Non Conformance Constraint for Upper Tumut Power Station | Other | Non-Conformance
NC_Q_STAN-4 | 1.3333 | 0.16667 | Non Conformance Constraint for Stanwell STAN-4 Power Station | Other | Non-Conformance
NC_S_BNGSF1 | 1.3333 | 0 | Non Conformance Constraint for Bungala #1 Solar Farm | Other | Non-Conformance
N^^Q_LDMU_1_B1 | 1.3333 | 0 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of Kogan Creek generator | Outage | NSW
Q>YLMR_YLMR_1 | 1.3333 | 0 | Out= one of the 110kV feeder between Yarranlea and Middle Ridge(733/1 or 734/1), avoid O/L on the remaining feeder(733/1 or 734/1), Feedback | Outage | Qld
Q>YLTX_DS | 1.3333 | 0 | Out = Nil, limit to Maryrorough Solar Farm to dynamic runback limit of Yarranlea 110/33kV transformer(s), DS formulation only | NIL | Qld
S>>RBTX1_RBTX2_WEWT | 1.3333 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage | SA
S>X_NWCB6022+6023_T2 | 1.3333 | 0 | Out = North West Bend 132 kV circuit breakers CB6022 and CB6023(Note: this takes out North West Bend-Monash #2 132kV line); limit SA to Victoria flow on Murraylink to avoid North West Bend transformer #2 O/L on trip NWB 132/66kV Transformer #3. | Outage | SA
T>T_GTSH_IMP_4F | 1.3333 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 2 220 kV line (flow North) for trip of Hadspen to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
V::N_X_HWSM_HWRO_xxx | 1.3333 | 0.16667 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>NWCB6024+25_TX1 | 1.3333 | 0 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #1 132/66kV TX on trip of Monash-North West Bend #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | Vic
#MOLNGSF1_E | 1.25 | 0 | NMOS1M.ENERGY * 1 <= 15 (Wt = 360) | Other | Quick
NC_Q_OAKEY1SF | 1.25 | 0.16667 | Non Conformance Constraint for OAKEY 1 SOLAR FARM | Other | Non-Conformance
Q_STR_RSTVS_SMSF_76 | 1.25 | 0 | Limit Sun metal SF to 100% of max capacity (#76 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | Qld
S_DVRB_270 | 1.25 | 51.75 | Out = DV-BL 275kV line Or MK-RB 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF + Hallet Hill WF (i.e. generation + load component) <= 270 MW | Outage | SA
V>V_NIL_7 | 1.25 | 9.9167 | Out = NIL, prevent overload of either MBTS-DDTS 220 kV line (flow north) for trip of the EPS-TTS 220 kV line, feedback. | NIL | Vic
VSML_VFRB_OFF | 1.25 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL | Vic
N>>N_65+66_N-2_5 | 1.1667 | 0.5 | Out= Nil, avoid O/L Wodonga to Jindera (060) on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL | NSW
S:VS_700_HY_TEST | 1.1667 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
S>>NIL_BWMP_TWPA | 1.1667 | 0.83333 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | SA
S>WT-BUS_MNWT_SNBG-T | 1.1667 | 0 | Out= Waterloo 132kV South bus outage (this offloads TX 5), avoid O/L Snowtown-Bungama 132kV line on trip of Mintaro-Waterloo 132kV line (this offloads Hummocks-Waterloo 132kV line), Feedback | Outage | SA
V::V_1900 | 1.1667 | 0 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Vic
#TORRA2_O_E | 1.0833 | 97.5833 | STSA2.ENERGY * 1 >= 60 (Wt = 755) | Other | Direction
#UPPTUMUT_E | 1.0833 | 0 | NUTS8.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
NC_N_LD03 | 1.0833 | 0 | Non Conformance Constraint for Liddell LD03 Power Station | Other | Non-Conformance
NC_T_CTHLWF1 | 1.0833 | 0 | Non Conformance Constraint for CATTLE HILL WF 1 | Other | Non-Conformance
N_SILVERWF_MAX | 1.0833 | 267.25 | Limit MW output of Silverton wind farm to not exceed 131 MW with Broken Hill solar generating | Outage | NSW
Q_HAMISF1_ZERO | 1.0833 | 2.0833 | Hamilton solar farm upper limit of 0 MW | Outage | Qld
Q_HASMME_RAMP_ZERO | 1.0833 | 1.75 | Ramp Haughton, Sun Metals and Mt Emerald generators to zero and hold at zero. | Outage | Qld
T_GO_ZERO | 1.0833 | 0 | Discretionary 0 MW upper limit on total Gordon generation | Outage | Tas
V_BANSF_20INV | 1.0833 | 3.5 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 20. Constraint swamp out otherwise. DS only | NIL | Vic
#TARONG#2_E | 1 | 0 | QTRN2.ENERGY * 1 <= 245 (Wt = 360) | Other | Quick
N-DBWL_94J | 1 | 0 | Out = Dubbo132 to Wellington (94J) 132 kV line, Upper limit of 80 on Nevertire SF, EE advice on 13/02/2020 | Outage | NSW
N>N-NIL_9R4_9R3 | 1 | 0 | Out= Nil, avoid O/L Finley to Mulwala 132kV line (9R4) trip of Finley to Deniliquin (9R3) line, Feedback | NIL | NSW
N>Q-MUTW_2 | 1 | 0 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage | NSW
N_GOONSF_9_INV | 1 | 0 | Limit Goonumbla Solar Farm upper limit to 0 MW if number of inverter available exceed 9. Dispatch only. swamped out if Inverters are within the limit. | Outage | NSW
SVML_020 | 1 | 0 | SA to Vic on ML upper transfer limit of 20 MW | Outage | SA
T>T_NIL_BL_IMP_7CC | 1 | 20.6667 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V>>V_ROTS_TX_3A_R | 1 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
V^SML_HORC_2 | 1 | 9.3333 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage | Vic
V^^N_CNUT_1 | 1 | 0 | Out = Canberra to Upper Tumut (01) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Vic
V_GANWRSF_FLT_0 | 1 | 166.6667 | Limit Gannawarra solar farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | Vic
V_KIAMAL_ISL_0 | 1 | 0 | Kiamal Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
#COLWF01_E | 0.91667 | 0 | NCLW1C.ENERGY * 1 <= 146 (Wt = 360) | Other | Quick
NC_Q_SWAN_E | 0.91667 | 7.9167 | Non Conformance Constraint for Swanbank E Power Station | Other | Non-Conformance
NC_S_PPCCGT | 0.91667 | 3.5 | Non Conformance Constraint for Pelican Point Power Station | Other | Non-Conformance
Q_NIL_STRGTH_HAYSF | 0.91667 | 0 | Out = Nil, limit Hayman SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | Qld
Q_STR_21138_RRSF80 | 0.91667 | 0 | Limit Ross River SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
Q_WHITSF1_ZERO | 0.91667 | 2.0833 | Whitsunday solar farm upper limit of 0 MW | Outage | Qld
S-DLBAT-L_0 | 0.91667 | 0.25 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW | Outage | SA
S>>V_NIL_NIL_RBNW1 | 0.91667 | 0 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL | SA
SVML_120 | 0.91667 | 0.16667 | SA to Vic on ML upper transfer limit of 120 MW | Outage | SA
S_CGTB_TBMO_N-2_1 | 0.91667 | 0 | Out= NIL, avoid O/L Tailumbend-Tungkillo 275kV line on trip of Tailumbend-Cherry Gardens 275kV line and Tailem Bend-Mobilong 132kV lines, (Note: with both Black Range series caps I/S or O/S) | Outage | SA
T>T_PMSH_IMP_4D | 0.91667 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_TU_MB_NN_N-2_1 | 0.91667 | 0 | Out= Nil, Loss of both Tungatinah - Meadowbank - New Norfolk 110kV lines declared credible, avoid O/L Tungatinah to New Norfolk No.3 110kV line on trip of both Tungatinah to Meadowbank to New Norfolk 110kV lines plus Meadowbank generation. | Outage | Tas
V>>V_NIL_3 | 0.91667 | 7.4167 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL | Vic
VSML_010 | 0.91667 | 0 | Vic to SA on ML upper transfer limit of 10 MW | Outage | Vic
#TORRB3_O_E | 0.83333 | 25.5833 | STSB3.ENERGY * 1 = 70 (Wt = 755) | Other | Direction
#WELLSF1_E | 0.83333 | 0 | NWLS4W.ENERGY * 1 <= 58 (Wt = 360) | Other | Quick
NC_V_YWPS2 | 0.83333 | 0.91667 | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Other | Non-Conformance
Q_CHILDSF1_ZERO | 0.83333 | 0 | Childers Solar Farm upper limit of 0MW | Outage | Qld
T_MRWF_ZERO | 0.83333 | 0 | Discretionary 0 MW upper limit on Musselroe Wind Farm | Outage | Tas
V>SML_NWRB_NWMWP1 | 0.83333 | 0 | Out=NWB - Robertstown 132kV #1 line, limit flow on ML to avoid OL North West Bend- MWP1 132 kV line. | Outage | Vic
V^SML_HORC_3 | 0.83333 | 78 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
V_ARWF_FSTTRP_5 | 0.83333 | 0.16667 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
V_KIAMSF_FLT_50 | 0.83333 | 0 | Limit Kiamal solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | Vic
#LBBL1_E | 0.75 | 0.16667 | SLBB2L.ENERGY * 1 <= 2 (Wt = 755) | Other | Quick
#SNOWTWN1_E | 0.75 | 0 | SNWF1T.ENERGY * 1 <= 5 (Wt = 360) | Other | Quick
NC_N_BW04 | 0.75 | 0.33333 | Non Conformance Constraint for Bayswater 4 Power Station | Other | Non-Conformance
NC_N_SITHE01 | 0.75 | 0 | Non Conformance Constraint for Smithfield Energy Facility | Other | Non-Conformance
Q_STR_21138_HAMSF80 | 0.75 | 0 | Limit Hamilton SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
T_T_FASH_HM_OPEN_1 | 0.75 | 0 | Out = one Farrell to Sheffield 220kV line, West Coast 220/110 kV parallel open, Farrell 220 kV bus not split, limit West Coast gen <= 110% of West Coast load | Outage | Tas
V:T_NIL_BL_1 | 0.75 | 6.0833 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL | Vic
DSNAP_V::S_NIL_MAXG1 | 0.66667 | 0 | DATASNAP NEVER TO BIND 10000 swamp; TESTING Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
NC_N_FINLYSF1 | 0.66667 | 0 | Non Conformance Constraint for FINLEY SOLAR FARM | Other | Non-Conformance
NC_N_LD04 | 0.66667 | 0.25 | Non Conformance Constraint for Liddell LD04 Power Station | Other | Non-Conformance
NC_Q_TARONG#1 | 0.66667 | 1.25 | Non Conformance Constraint for Tarong 1 Power Station | Other | Non-Conformance
NQ_VST_ISLE_B | 0.66667 | 0 | Separation between Vic and NSW, allow Vic-NSW to supply Wagga or Northern Victoria | Outage | NSW
N_FINLEYSF_6_INV | 0.66667 | 0 | Limit Finley Solar Farm upper limit to 0 MW if number of inverter available exceed 6. Dispatch only. swamped out if Inverters are within the limit. | Outage | NSW
N_SAPHWF1_ZERO | 0.66667 | 0 | Sapphire wind farm upper limit of 0 MW | Outage | NSW
S>>RB_275KV_N_BUS_3 | 0.66667 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | SA
S>BRTW_BWPA_HUWT | 0.66667 | 2.5 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>NIL_NIL_SGMYSE-T2 | 0.66667 | 0 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on Nil trip (for Line component SECS assumed O/S or I/S), Feedback | NIL | SA
V::S_PAVC1_MAXG | 0.66667 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | SA
V>X_NWCB6022+6023_T1 | 0.66667 | 0 | Out = North West Bend 132 kV circuit breakers CB6022 and CB6023(Note: this takes out North West Bend-Monash #2 132kV line); limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB 132/66kV TX3. | Outage | Vic
V_KARSF_19INV | 0.66667 | 2.75 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | NIL | Vic
V_KARSF_8INV | 0.66667 | 0.58333 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 8. Constraint swamp out if number of inverter available not exceed 8. This is to manage voltage oscillation. DS only | Outage | Vic
V_VS_MLMO_NETT | 0.66667 | 1.9167 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage | Vic
#N-Q-MNSP1_RAMP_E_F | 0.58333 | 0 | N-Q-MNSP1 >= MIN(60, InitialFlow + 80) (Wt=35) | Other | Quick
#V-SA_RAMP_E_F | 0.58333 | 0.83333 | V-SA <= MAX(25, InitialFlow - 30) (Wt=35) | Other | Quick
CA_BRIS_4DE45CFF_1 | 0.58333 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage | Constraint Automation
N::V_DDMS | 0.58333 | 0 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage | NSW
N>Q-TEMU_757_758 | 0.58333 | 0 | Out= 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line, avoid O/L on remaining T174 Terranora to H4 Mudgeeraba line (758 or 757), Feedback | Outage | NSW
NC_Q_CHILDSF1 | 0.58333 | 3 | Non Conformance Constraint for CHILDERS SF 1 | Other | Non-Conformance
NC_S_AGLHAL | 0.58333 | 0.75 | Non Conformance Constraint for AGL Hallet Power Station | Other | Non-Conformance
NC_S_LKBONNY3 | 0.58333 | 2.1667 | Non Conformance Constraint for Lake Bonney 3 Windfarm | Other | Non-Conformance
NC_S_TBSF1 | 0.58333 | 0.41667 | Non Conformance Constraint for Tailembend Solar Farm | Other | Non-Conformance
N_URANQ12_ZERO | 0.58333 | 0 | Uranquinty unit 2 upper limit of 0 MW | Outage | NSW
N_URANQ14_ZERO | 0.58333 | 0 | Uranquinty unit 4 upper limit of 0 MW | Outage | NSW
S>>BGTX_TWPA_TPRS | 0.58333 | 0 | Out= Bungana 275/132kV TX, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
S>>NIL_TWPA_TPRS | 0.58333 | 0 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL | SA
S>NIL_LKDV_CNRB | 0.58333 | 4.0833 | Out= NIL, avoid O/L Canowi-Robertstown 275kV on trip of Mt Lock-Davenport 275kV line, Feedback | NIL | SA
SVML_010 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 10 MW | Outage | SA
SVML_060 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 60 MW | Outage | SA
S_PPT270 | 0.58333 | 0 | SA Pelican Point generation <= 270 MW | Outage | SA
T>T_HAPM_IMP_4L | 0.58333 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
VN_ZERO | 0.58333 | 0 | VIC to NSW upper transfer limit of zero MW | Outage | Vic
V^^S_KHKN_SETB | 0.58333 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
V_WEMENSF_19INV | 0.58333 | 1 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | NIL | Vic
V_WEMENSF_19INV | 0.58333 | 1 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | Outage | Vic
#TORRA4_E | 0.5 | 0 | STSA4.ENERGY * 1 >= 70 (Wt = 35) | Other | Quick
CA_SYDS_4EBD234F_1 | 0.5 | 0 | Constraint Automation, O/L XFMR T_1@R_TOWN@SA for Nil Trip Base Case. Generated by STNET[BNECR2] Host NORREGEEMP3(EMPSYD) | Outage | Constraint Automation
N::N_CNSD_2 | 0.5 | 0 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | NSW
NC_N_ER04 | 0.5 | 0 | Non Conformance Constraint for Eraring ER04 Power Station | Other | Non-Conformance
NC_N_HUMENSW | 0.5 | 0.58333 | Non Conformance Constraint for Hume Hydro Power Station | Other | Non-Conformance
NC_S_LKBONNY2 | 0.5 | 2.1667 | Non Conformance Constraint for Lake Bonney 2 Windfarm | Other | Non-Conformance
NC_V_WEMENSF1 | 0.5 | 0.75 | Non Conformance Constraint for WEMEN SF | Other | Non-Conformance
Q>>CLWU_BCRG_BCCP | 0.5 | 3.4167 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Qld
Q>>NIL_LCCP_BCCP | 0.5 | 0 | Out= Nil, avoid O/L Bouldercombe to Calliope River (812) on trip of Larcom Creek to Calliope River (8859) line, Feedback | NIL | Qld
Q>NIL_BI_xxx | 0.5 | 130.1667 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines | NIL | Qld
QN_1050 | 0.5 | 0 | Qld to NSW on QNI upper transfer limit of 1050 MW | Outage | Qld
Q^^NIL_TR_CLHA | 0.5 | 0 | Out = Nil, Tarong voltage stability limit, Calvale-Halys contingency equation | NIL | Qld
SVML_080 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 80 MW | Outage | SA
SVML_100 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 100 MW | Outage | SA
S^DVMK_SA_NTH | 0.5 | 0 | Out = ONLY one line segment between Davenport-Belalie-Willalo-Mokota 275kV line, manage voltage collapse in northern SA for the trip of Robertstown-Canowie 275kV line. | Outage | SA
T>T_HAPM_IMP_4N | 0.5 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_NIL_BL_IMP_1B | 0.5 | 0 | Out = Nil, avoid O/L either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line with no SPS action, feedback | NIL | Tas
T>T_PMSH_IMP_4E | 0.5 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V:SS_820_HY_TEST | 0.5 | 0.16667 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
VSML_015 | 0.5 | 0 | Vic to SA on ML upper transfer limit of 15 MW | Outage | Vic
V_BGWF_GFT_5 | 0.5 | 0 | Out= Bulgana WF associated fast tripping scheme (disabled), Limit Bulgana Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
V_CWWF_GFT_5 | 0.5 | 18.5833 | Out= Crowlands WF associated fast tripping scheme (disabled), Limit Crowlands Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
V_WEMENSF_8INV | 0.5 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 8. Constraint swamp out otherwise. DS only | NIL | Vic
#NSW1-QLD1_RAMP_E_F | 0.41667 | 0 | NSW1-QLD1 >= MIN(40, InitialFlow + 200) (Wt=35) | Other | Quick
N::N_SDUT_2 | 0.41667 | 0 | Out = Upper Tumut -Stockdill(1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | NSW
NC_N_BW01 | 0.41667 | 0.083333 | Non Conformance Constraint for Bayswater 1 Power Station | Other | Non-Conformance
NC_N_SHGEN | 0.41667 | 0 | Non Conformance Constraint for Shoalhaven Power Station | Other | Non-Conformance
NC_Q_STAN-2 | 0.41667 | 0.25 | Non Conformance Constraint for Stanwell STAN-2 Power Station | Other | Non-Conformance
NC_Q_YABULU | 0.41667 | 0.25 | Non Conformance Constraint for Yabulu Power Station | Other | Non-Conformance
NC_V_CHYTWF1 | 0.41667 | 0 | Non Conformance Constraint for CHERRY TREE WF | Other | Non-Conformance
NC_V_YENDWF1 | 0.41667 | 0 | Non Conformance Constraint for YENDON WIND FARM 1 | Other | Non-Conformance
N_URANQ13_ZERO | 0.41667 | 0 | Uranquinty unit 3 upper limit of 0 MW | Outage | NSW
S>>NIL_CGTB_TUTB_1 | 0.41667 | 0 | Out= Nil, avoid O/L Tungkillo - Tailem Bend 275kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | NIL | SA
T_ROCOF_3 | 0.41667 | 0.58333 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | Tas
V_GANNSF_11INV | 0.41667 | 1.5833 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Constraint swamp out otherwise. DS only | NIL | Vic
V_GANWR_BAT_G_ISL_0 | 0.41667 | 2.25 | Gannawarra Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Vic
N_LIMOSF11_ZERO | 0.33333 | 0 | Limondale 1 solar farm upper limit of 0 MW and all inverters disconnected. | Outage | NSW
#BANN1_E | 0.33333 | 839.25 | VWES1B.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
#CG4_E | 0.33333 | 0 | NCLG4D.ENERGY * 1 <= 0 (Wt = 29) | Other | Quick
#LBBG1_E | 0.33333 | 0.25 | SLBB1L.ENERGY * 1 <= 2 (Wt = 755) | Other | Quick
#TAS1_E_20200302 | 0.33333 | 0 | Multiple TAS1 LHS <= 500 (Wt = 35) | Other | Quick
#TORRB2_E | 0.33333 | 0 | STSB2.ENERGY * 1 >= 60 (Wt = 35) | Other | Quick
N>>N-NIL__3_OPENED & CLOSED | 0.33333 | 1.4167 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
N>>N_65+66_N-2_2 | 0.33333 | 7.5833 | Out= Nil, avoid O/L Dederang to Wodonga on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL | NSW
NC_N_DARLSF1 | 0.33333 | 0 | Non Conformance Constraint for DARLINGTON POINT SF | Other | Non-Conformance
NC_Q_EMERASF1 | 0.33333 | 0 | Non Conformance Constraint for EMERALD SOLAR PARK 1 | Other | Non-Conformance
NC_Q_TARONG#2 | 0.33333 | 0.41667 | Non Conformance Constraint for Tarong 2 Power Station | Other | Non-Conformance
NC_S_SNOWNTH1 | 0.33333 | 0.58333 | Non Conformance Constraint for Snowtown North Wind Farm | Other | Non-Conformance
NC_V_LOYYB1 | 0.33333 | 0 | Non Conformance Constraint for Loy Yang B1 Power Station | Other | Non-Conformance
N_BKHSF_44INV | 0.33333 | 22 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 44. Constraint swamp out if number of inverter available not exceed 44. This is to manage voltage oscillation. DS only | Outage | NSW
N_NIL_TE_B | 0.33333 | 15.0833 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
Q>>RGLC_CLWU_BCCP | 0.33333 | 0 | Out= Raglan to Larcom Creek (8875), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
S>>BRTW_RBTU_WTTP | 0.33333 | 0.083333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
S>>BWMP_TWPA_TPRS | 0.33333 | 0.41667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
S>>X_RBTU+RB_SBUS_14 | 0.33333 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
S>NIL_BWMP_RHBR-T | 0.33333 | 0 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | SA
S^BGBW_SA_NTH | 0.33333 | 0 | Out = Bungama-Blyth West 275kV line, Manage voltage collapse in northern SA for the trip of Para-Templers West 275kV line | Outage | SA
S^NIL_PL_MAX | 0.33333 | 3.5 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
T^V_HAPM_220_1 | 0.33333 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage | Tas
T_T_FASH_HM_OPEN_2 | 0.33333 | 0 | Out = one Farrell to Sheffield 220kV line, West Coast 220/110 kV parallel open, Farrell 220 kV bus not split, limit West Coast gen >= 90% of West Coast load | Outage | Tas
V:T_SHGT_BL_1 | 0.33333 | 1.0833 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
V>>V_BUDP_6 | 0.33333 | 5.9167 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Vic
V>V_NIL_6 | 0.33333 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Vic
V^^S_MLSY_2 | 0.33333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
V^^S_PAVC1_MAXG | 0.33333 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
V_MWWF_5 | 0.33333 | 3.3333 | Murra Warra Wind Farm upper limit of 5 MW | Outage | Vic
#N-Q-MNSP1_I_E | 0.25 | 0 | N-Q-MNSP1.ENERGY * -1 >= 49 (Wt = 35) | Other | Quick
#TORRA2_E | 0.25 | 0 | STSA2.ENERGY * 1 >= 70 (Wt = 35) | Other | Quick
N::Q_BWSW_KC | 0.25 | 0 | Out= Bayswater to Sydney West (32), NSW to Qld Transient Stability Limit for trip of Kogan Creek | Outage | NSW
N::V_MNYS_MSDD | 0.25 | 0 | Out=Marulan-Yass(4 or 5), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | NSW
N>Q_LSLS_9U8 | 0.25 | 8.5833 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 directlink cable O/S. | Outage | NSW
NC_N_MP1 | 0.25 | 0.5 | Non Conformance Constraint for Mt Piper 1 Power Station | Other | Non-Conformance
NC_Q_DDPS1 | 0.25 | 0.66667 | Non Conformance Constraint for Darling Downs Power Station | Other | Non-Conformance
NC_Q_OAKEY2SF | 0.25 | 0.083333 | Non Conformance Constraint for OAKEY 2 SOLAR FARM | Other | Non-Conformance
NC_Q_SMCSF1 | 0.25 | 0.41667 | Non Conformance Constraint for Sun Metals solar farm | Other | Non-Conformance
NC_Q_STAN-3 | 0.25 | 0.16667 | Non Conformance Constraint for Stanwell STAN-3 Power Station | Other | Non-Conformance
NC_Q_TNPS1 | 0.25 | 0.25 | Non Conformance Constraint for Tarong North Power Station | Other | Non-Conformance
NC_S_BARKIPS1 | 0.25 | 1.0833 | Non Conformance Constraint for BARKER INLET PS | Other | Non-Conformance
NC_S_MINTARO | 0.25 | 0 | Non Conformance Constraint for Mintaro Gas Turbine | Other | Non-Conformance
NC_V_MORTLK12 | 0.25 | 0 | Non Conformance Constraint for Mortlake GT unit 2 | Other | Non-Conformance
NV_ZERO | 0.25 | 0 | NSW to VIC upper transfer limit of zero MW | Outage | NSW
N^^N_NIL_1 | 0.25 | 0.16667 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
N^^Q_BCDM_B1 | 0.25 | 0 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
Q:N_NIL_OSC | 0.25 | 0 | Out= Nil, QNI oscillatory stability limit of 1200 MW, limit reduced to 950 MW when any one SEQ SVC POD is out, limit is reduced to 853 MW when all three SEQ SVCs or PODs out. | NIL | Qld
Q>>WOSP_WOPW_WOGP_1 | 0.25 | 0.083333 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Qld
Q_STR_21138_DAYSF80 | 0.25 | 0 | Limit Daydream SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | Qld
S>>BRBG_BGTX_HUWT | 0.25 | 0 | Out= Brinkworth to Redhill to Bungama 132kV lines (this takes out Clements Gap WF), avoid O/L Hummocks to Waterloo 132kV on trip of Bungama 132/275kV TX2, Feedback | Outage | SA
S>>BRTW_BWPA_WTTP | 0.25 | 0.83333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
SA-GEN_030 | 0.25 | 0 | Discretionary 30 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | SA
SA-GEN_090 | 0.25 | 0 | Discretionary 90 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | SA
SA-GEN_120 | 0.25 | 0 | Discretionary 120 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | SA
SA_ISLE_DAL_HIGH_SOC | 0.25 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Dalrymple battery of 2 MW, except when state of charge is above 70% | Outage | SA
T_T_MC_ZERO | 0.25 | 0 | Discretionary 0 MW upper limit on Macintosh generation | Outage | Tas
V::N_LT_UT_MS_xxx | 0.25 | 0 | Out = Lower Tumut - Murray (66) line or Upper Tumut - Murray (65) line, prevent transient instability for fault and trip of Upper Tumut - Murray (65) or Lower Tumut - Murray (66) line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_PATU_MAXG | 0.25 | 1 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
V:SS_820_HY_TEST_DYN | 0.25 | 0.58333 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
V_EP_BUS1 | 0.25 | 0 | Eildon PS Unit 2 upper limit set to zero due to outage of Eildon No 1 220 kV Bus | Outage | Vic
#STAN-2_E | 0.16667 | 0 | QSTN2.ENERGY * 1 <= 365 (Wt = 360) | Other | Quick
CA_BRIS_4D2AA9D0_1 | 0.16667 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG MVPB on trip of DDTS-SMTS1 &DDTS-SMTS2 330KV LINES. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage | Constraint Automation
CA_BRIS_4DE6D9E8_1 | 0.16667 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage | Constraint Automation
N>N-NIL_TE_E1 | 0.16667 | 6.3333 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST | NIL | NSW
NC_N_BW02 | 0.16667 | 0.16667 | Non Conformance Constraint for Bayswater 2 Power Station | Other | Non-Conformance
NC_N_BW03 | 0.16667 | 0.16667 | Non Conformance Constraint for Bayswater 3 Power Station | Other | Non-Conformance
NC_N_TALWA1 | 0.16667 | 0.83333 | Non Conformance Constraint for Tallawarra Power Station | Other | Non-Conformance
NC_N_URANQ14 | 0.16667 | 0 | Non Conformance Constraint for Uranquinty 4 Power Station | Other | Non-Conformance
NC_Q_BRAEMAR1 | 0.16667 | 0.33333 | Non Conformance Constraint for Braemar 1 Power Station | Other | Non-Conformance
NC_Q_CPP_3 | 0.16667 | 0.083333 | Non Conformance Constraint for Callide C CPP_3 | Other | Non-Conformance
NC_Q_GSTONE1 | 0.16667 | 0.25 | Non Conformance Constraint for Gladstone 1 Power Station | Other | Non-Conformance
NC_Q_GSTONE2 | 0.16667 | 0.083333 | Non Conformance Constraint for Gladstone 2 Power Station | Other | Non-Conformance
NC_Q_GSTONE3 | 0.16667 | 0.25 | Non Conformance Constraint for Gladstone 3 Power Station | Other | Non-Conformance
NC_Q_HAYMSF1 | 0.16667 | 5.5833 | Non Conformance Constraint for HAYMAN SOLAR FARM | Other | Non-Conformance
NC_Q_STAN-1 | 0.16667 | 1.5833 | Non Conformance Constraint for Stanwell STAN-1 Power Station | Other | Non-Conformance
NC_Q_TARONG#4 | 0.16667 | 0.083333 | Non Conformance Constraint for Tarong 4 Power Station | Other | Non-Conformance
NC_Q_W/HOE#2 | 0.16667 | 0 | Non Conformance Constraint for Wivenhoe No 2 Power Station | Other | Non-Conformance
NC_S_QPS5 | 0.16667 | 0 | Non Conformance Constraint for Quarantine QPS5 Power Station | Other | Non-Conformance
NC_S_TORRA2 | 0.16667 | 0 | Non Conformance Constraint for Torrens A2 Power Station | Other | Non-Conformance
NC_S_TORRA4 | 0.16667 | 0 | Non Conformance Constraint for Torrens A4 Power Station | Other | Non-Conformance
NC_V_ELAINWF1 | 0.16667 | 0 | Non Conformance Constraint for ELAINE WIND FARM 1 | Other | Non-Conformance
NC_V_MTGELWF1 | 0.16667 | 0 | Non Conformance Constraint for MT GELLIBRAND WF | Other | Non-Conformance
N_COLEASF1_FLT_0 | 0.16667 | 0 | Limit Coleambally solar farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | NSW
Q>X_CPWO1_CPWU_CPWO2 | 0.16667 | 12.5 | Out= Calliope River to Woolooga (813+815) line, avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (814) line, Feedback | Outage | Qld
QNI_ISLE_B | 0.16667 | 0 | Qld / Southern separation, allow QNI to supply Northern NSW Load | Outage | Qld
QNI_SOUTH_1100_DYN | 0.16667 | 0 | QLD to NSW on QNI upper transfer limit of 1100 MW, dynamic headroom, DS formulation only. | Outage | Qld
Q^^CS_-080 | 0.16667 | 0 | Nominated Offset -80MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage | Qld
Q_EMERASF1_ZERO | 0.16667 | 0 | Emerald Solar Farm upper limit of 0 MW | Outage | Qld
Q_STR_SMHAU_HASF_40 | 0.16667 | 0.083333 | Limit Haughton SF to 50% capacity (40 inverters) If Stan >= 3 + Cal >=3 + Glad >= 3 and (Stan+Cal+Glad) >=10, Zero otherwise | Outage | Qld
S>>NIL_RBTU_WEWT | 0.16667 | 2.6667 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | SA
S>>NIL_TBTU_TBMO_1 | 0.16667 | 3.9167 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
S>>V_CGTI_TIPA_PGPA | 0.16667 | 0 | Out= Cherry Gardens - Torrens Island 275kV line, avoid O/L Parafield Gardens West-Para 275kV line on trip of Torrens Island A -Para 275kV line, Feedback | Outage | SA
S>NIL_NIL_SGBN | 0.16667 | 1.5833 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | SA
S>NWCB6021+22_TX2 | 0.16667 | 0 | Out= North West Bend 132kV CBs 6021 and 6022(this offloads NWB TX1), avoid O/L North West Bend #2 132/66kV TX on trip of North West Bend-Robertstown #1 132kV line (this splits NWB 132kV bus), | Outage | SA
S>V_NWRB2_RBNW1 | 0.16667 | 9.9167 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage | SA
SA-GEN_060 | 0.16667 | 0 | Discretionary 60 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | SA
SA-GEN_150 | 0.16667 | 0 | Discretionary 150MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | SA
SA-GEN_180 | 0.16667 | 0 | Discretionary 180MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | SA
SA-GEN_210 | 0.16667 | 0 | Discretionary 210 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | SA
SVML_040 | 0.16667 | 0 | SA to Vic on ML upper transfer limit of 40 MW | Outage | SA
S_BRBG_CMWF_0 | 0.16667 | 0 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | SA
T::T_PMSH_2 | 0.16667 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage | Tas
T>T_GTSH_IMP_4E | 0.16667 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of Hadspen to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_NIL_BL_110_8_1 | 0.16667 | 0.33333 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
T_FAJB | 0.16667 | 0 | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Tas
T_GO_250 | 0.16667 | 0 | Discretionary 250 MW upper limit on total Gordon generation | Outage | Tas
T_GO_260 | 0.16667 | 0 | Discretionary 260 MW upper limit on total Gordon generation | Outage | Tas
V>>N-X_MSUT_LTUT | 0.16667 | 0 | Out = Murray-Upper Tumut and Lower Tumut-Upper Tumut(65+64), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Vic
VN_0650 | 0.16667 | 0 | Discretionary Vic to NSW transfer upper limit of 650 MW | Outage | Vic
V^^S_SEVC1_MAXG | 0.16667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
V_BANNERTON_ZERO | 0.16667 | 5.75 | Bannerton Solar Farm upper limit of 0 MW | Outage | Vic
V_GANWRSF_0INV | 0.16667 | 0 | Constraint to violate if Gannawarra Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | Vic
V_GANWR_BAT_G_FLT_0 | 0.16667 | 3.0833 | Limit Gannawarra Battery (Generation Component) upper limit to 0 MW to manage post contingent voltage oscillation | Outage | Vic
V_WEMENSF_FLT_44 | 0.16667 | 92.4167 | Limit Wemen Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | Outage | Vic
#FISHER_E | 0.083333 | 0 | TFI11.ENERGY * 1 = 2 (Wt = 755) | Other | Quick
#HAYMSF1_E | 0.083333 | 187.6667 | QCCK2H.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
#LILYSF1_E | 0.083333 | 915.8333 | QBDR1L.ENERGY * 1 <= 100 (Wt = 360) | Other | Quick
#LYA2_E | 0.083333 | 78.4167 | VLYP2.ENERGY * 1 <= 535 (Wt = 360) | Other | Quick
#T-V-MNSP1_RAMP_E_F | 0.083333 | 0 | T-V-MNSP1 >= MIN(0, InitialFlow + 200) (Wt=35) | Other | Quick
#TORRB3_E | 0.083333 | 0 | STSB3.ENERGY * 1 = 40 (Wt = 755) | Other | Quick
N::Q_MUTW_1 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | NSW
N>>N-NIL_DPTX | 0.083333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL | NSW
N>>N-NIL__H_15M | 0.083333 | 0.25 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | NSW
N>>Q-LDTW_2 | 0.083333 | 0 | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage | NSW
N>>V-NIL_0X1 | 0.083333 | 0 | Out= NIL, avoid O/L Buronga to Redcliff (OX1) on Nil trip, Feedback | NIL | NSW
N>N-GITN_TE_C1 | 0.083333 | 2.3333 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
NC_N_BROKENH1 | 0.083333 | 0 | Non Conformance Constraint for Broken Hill Solar Farm | Other | Non-Conformance
NC_N_ER01 | 0.083333 | 0.16667 | Non Conformance Constraint for Eraring ER01 Power Station | Other | Non-Conformance
NC_N_ER03 | 0.083333 | 0.083333 | Non Conformance Constraint for Eraring ER03 Power Station | Other | Non-Conformance
NC_N_HVGTS | 0.083333 | 0 | Non Conformance Constraint for Hunter Valley Gas Turbine | Other | Non-Conformance
NC_Q_BRAEMAR3 | 0.083333 | 1.4167 | Non Conformance Constraint for Braemar 3 Power Station | Other | Non-Conformance
NC_Q_CPP_4 | 0.083333 | 0 | Non Conformance Constraint for Callide C CPP_4 | Other | Non-Conformance
NC_Q_W/HOE#1 | 0.083333 | 0 | Non Conformance Constraint for Wivenhoe No 1 Power Station | Other | Non-Conformance
NC_S_DRYCGT3 | 0.083333 | 0 | Non Conformance Constraint for Dry Creek 3 Power Station | Other | Non-Conformance
NC_S_QPS1 | 0.083333 | 0 | Non Conformance Constraint for Quarantine QPS1 Power Station | Other | Non-Conformance
NC_T_JBUTTERS | 0.083333 | 0 | Non Conformance Constraint for John Butters Power Station | Other | Non-Conformance
NC_T_MUSSELR1 | 0.083333 | 0 | Non Conformance Constraint for MUSSELROE WF U 1-56 | Other | Non-Conformance
NC_V_EILDON1 | 0.083333 | 0 | Non Conformance Constraint for Eildon 1 Power Station | Other | Non-Conformance
NC_V_JLA02 | 0.083333 | 0 | Non Conformance Constraint for Jeeralang A - 02 Power Station | Other | Non-Conformance
NC_V_JLA04 | 0.083333 | 0 | Non Conformance Constraint for Jeeralang A - 04 Power Station | Other | Non-Conformance
NC_V_JLB01 | 0.083333 | 0.41667 | Non Conformance Constraint for Jeeralang B - 01 Power Station | Other | Non-Conformance
NC_V_LYA1 | 0.083333 | 0 | Non Conformance Constraint for Loy Yang A1 Power Station | Other | Non-Conformance
NC_V_LYA2 | 0.083333 | 0 | Non Conformance Constraint for Loy Yang A2 Power Station | Other | Non-Conformance
NC_V_YWPS1 | 0.083333 | 0 | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Other | Non-Conformance
NRM_VIC1_NSW1 | 0.083333 | 11.9167 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue
N_WR_30_WT-INV | 0.083333 | 0 | Limit White Rock wind/solar farm upper limit to 0 MW if number of wind turbine + inverter available exceed 30. Dispatch only. swamped out if Inverters are within the limit. | Outage | NSW
Q::N_DM_CB_AR_2L-G | 0.083333 | 1.6667 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
QN_1100 | 0.083333 | 0 | Qld to NSW on QNI upper transfer limit of 1100 MW | Outage | Qld
Q_CS_1700 | 0.083333 | 41 | Qld Central to Qld South upper transfer limit of 1700MW (discretionary) | Outage | Qld
Q_RGBYRSF1_ZERO | 0.083333 | 8 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Qld
Q_RRSF1_ZERO | 0.083333 | 9.25 | Ross River solar farm upper limit of 0 MW | Outage | Qld
Q_YARANSF1_ZERO | 0.083333 | 0 | Yarrenlea Solar Farm upper limit of 0 MW | Outage | Qld
S>NIL_NIL_MYSG-T | 0.083333 | 0 | Out = NIL; Limit LB2 and LB3 generation to avoid OL Mayura - Snuggery T 132kV line. | NIL | SA
SVML_160 | 0.083333 | 0 | SA to Vic on ML upper transfer limit of 160 MW | Outage | SA
S_HPRL1_E | 0.083333 | 1.25 | Out= Nil, Hornsdale Battery load energy target <= 40 MW | NIL | SA
T>T_NIL_110_2 | 0.083333 | 0 | Out = NIL, avoid O/L Scottsdale Tee to Norwood 110 kV line (flow to Norwood) on trip of Scottsdale to Norwood 110 kV line or 110/22 kV txfmr at Scottsdale, feedback. Swamped when Musselroe Runback Control Scheme available | NIL | Tas
T>T_NIL_BL_220_6B | 0.083333 | 0.16667 | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
T^T_NIL_BL_5 | 0.083333 | 0 | Outage = Nil, avoid voltage instability or violations for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line | NIL | Tas
T^V_NIL_11 | 0.083333 | 5.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
T^^V_PMSH_1 | 0.083333 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of either one Sheffield to Georgetown 220kV line or one Hadspen to Georgetown 220kV line. | Outage | Tas
T_FAMA | 0.083333 | 0 | Out=Farrell-Mackintosh 110KV line. Energy <= 0MW | Outage | Tas
T_FARC1 | 0.083333 | 0.91667 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Tas
V>>N-NIL_HG | 0.083333 | 15.75 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
V>>V_EPTT_1 | 0.083333 | 0 | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to South) for loss of the parallel line, feedback | Outage | Vic
V>>V_MLSY_4BR | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
V>>V_NIL_1A | 0.083333 | 0.91667 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
VS_050 | 0.083333 | 0.33333 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Vic
V^S_HYCP | 0.083333 | 0 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL | Vic
V^^S_KHKN_MAXG | 0.083333 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
V_KARADSF_FLT_20 | 0.083333 | 0 | Limit Karadoc solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | Vic
V_WEMENSF_FLT_10 | 0.083333 | 0 | Limit Wemen Solar Farm upper limit to 10 MW to manage post contingent voltage oscillation | Outage | Vic

## Binding FCAS
Constraint Equation ID | 2020 Hours | 2019 Hours | Description | Type
F_I+LREG_0210 | 7771.25 | 2082.9167 | NEM Lower Regulation Requirement greater than 210 MW | NIL
F_I+NIL_MG_R5 | 7270.5833 | 6863.5833 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL
F_I+NIL_APD_TL_L5 | 7261.0833 | 6646.3333 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_APD_TL_L60 | 6571.0833 | 5908.1667 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R6 | 6571.0833 | 6306.5833 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL
F_I+NIL_MG_R60 | 6295.4167 | 6113.9167 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL
F_I+RREG_0220 | 5017 | 1273.0833 | NEM Raise Regulation Requirement greater than 200 MW | NIL
F_T_AUFLS2_R6 | 4276.3333 | 5082.5833 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL
F_I+ML_L6_0400 | 4191.25 | 3789.8333 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL
F_MAIN+NIL_DYN_RREG | 3201.9167 | 3535.25 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL
F_MAIN++APD_TL_L60 | 2754.5 | 2115.25 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_MAIN++NIL_MG_R60 | 2523.25 | 2131.25 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R6 | 2407.1667 | 1768.4167 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_MAIN++APD_TL_L5 | 2276.8333 | 2465.75 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_I+NIL_APD_TL_L6 | 1981.0833 | 0 | Lower 6 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_T_NIL_MINP_R6 | 1528.0833 | 1218 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL
F_MAIN++NIL_MG_R5 | 1207.75 | 1122.6667 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_Q++MUTW_L6 | 1164.6667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
F_T+NIL_MG_R5 | 1149.25 | 821 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_Q++MUTW_L60 | 1115.5833 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
F_T+NIL_WF_TG_R5 | 1076.3333 | 1306.8333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_T++RREG_0050 | 1048.1667 | 549.3333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_MAIN++APD_TL_L6 | 984.9167 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_T+NIL_WF_TG_R6 | 944.0833 | 1272.8333 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 891.5 | 1340.6667 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R60 | 854.5833 | 1705.25 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R60 | 847.5 | 850.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R6 | 787.8333 | 737.1667 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++ML_L6_0400 | 781.25 | 1417.9167 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_T+NIL_MG_RECL_R5 | 743.9167 | 1501.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R6 | 728 | 1656.3333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++LREG_0210 | 648.4167 | 179.25 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
F_ESTN+MG_R5 | 405.8333 | 4.8333 | Raise 5 min Service Requirement for Eastern Generation Event | Outage
F_ESTN+MG_R6 | 391 | 4.8333 | Raise 6 sec Service Requirement for Eastern Generation Event | Outage
F_ESTN+LREG_0210 | 389.6667 | 4.8333 | Eastern Lower Regulation Requirement greater than 210 MW | Outage
F_V_APD01_R5 | 385.3333 | 605.4167 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage
F_V_APD01_R6 | 385.3333 | 605.4167 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage
F_V_APD01_R60 | 385.3333 | 605.4167 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage
F_I+ML_L6_APD_LD | 378.25 | 0.33333 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage
F_ESTN+MG_R60 | 366.75 | 4.8333 | Raise 60 sec Service Requirement for Eastern Generation Event | Outage
F_ESTN+ML_L6_0400 | 361.4167 | 4.8333 | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_ESTN+ML_L5_0400 | 359.8333 | 4.6667 | Lower 5 min requirement for a Eastern Load Event, ML = 400 | Outage
F_ESTN+ML_L60_0400 | 340.4167 | 4.6667 | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_S+TL_L60_OD | 336.3333 | 4.8333 | Lower 60 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_TASCAP_LREG_0210 | 322.9167 | 341.25 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_MAIN+NIL_DYN_LREG | 313.8333 | 328.8333 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL
F_Q++MUTW_L5 | 312.4167 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
F_S+TL_L5_OD | 302.6667 | 4.6667 | Lower 5 min Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_S+TL_L6_OD | 272 | 4.8333 | Lower 6 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_T++LREG_0050 | 261.5 | 174.5 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_TASCAP_RREG_0220 | 250.1667 | 206.25 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_ESTN+RREG_0220 | 242.9167 | 4.5833 | Eastern Raise Regulation Requirement greater than 220 MW | Outage
F_T++NIL_ML_L6 | 221.75 | 246.9167 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_S+TG_R60_150 | 221.3333 | 0 | Raise 60 sec Service Requirement for a 150 MW SA Generation Event | Outage
F_S+TG_R5_150 | 217.5 | 0 | Raise 5 min Service Requirement for a 150 MW SA Generation Event | Outage
F_T+LREG_0050 | 210.1667 | 1184.3333 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_T+RREG_0050 | 209.3333 | 1127.3333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 207.5 | 1185.3333 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+APD_TL_L5 | 204.8333 | 1143.5 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 203.9167 | 1123 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 202.5 | 1185.3333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 201.5 | 1184.75 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_S+TG_R6_150 | 199.8333 | 0 | Raise 6 sec Service Requirement for a 150 MW SA Generation Event | Outage
F_MAIN+LREG_0210 | 195.6667 | 673.75 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL
F_S+MLMO_TL_L60 | 191.8333 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
F_T+NIL_ML_L60 | 184.25 | 1184.4167 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L6 | 184.1667 | 1184.6667 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_BL_L60 | 181.9167 | 85 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_MAIN++ML_L6_APD_LD | 174 | 0.58333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
F_QNV+DYN_RREG | 171.5 | 0 | Qld, NSW and Vic Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | Outage
F_I+GFT_TG_R5 | 165.75 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_QNV++MG_R60 | 164.5 | 3.5833 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_I+GFT_TG_R60 | 162.9167 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_QNV++ML_L6_0400 | 154.1667 | 0.083333 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_T++NIL_ML_L60 | 152 | 275.5833 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_MAIN++RREG_0220 | 151.1667 | 74.5833 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
F_S_LBBG1_RREG | 140.6667 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) RREG Requirement <= 0MW | Outage
F_QNV++MG_R6 | 126.3333 | 0.41667 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_T++NIL_MG_RECL_R5 | 125.1667 | 194.3333 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_S+TL_L5_0150 | 113.6667 | 0 | Lower 5 min Service Requirement for a 150 MW SA Network (Load) Event | Outage
F_MAIN+RREG_0220 | 111.25 | 322.25 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL
F_Q++LDTW_L6 | 108.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
F_Q++LDTW_L60 | 104.6667 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
F_ESTN++MLMO_L60 | 103.5833 | 14.0833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_S+TL_L6_0150 | 103 | 0 | Lower 6 sec Service Requirement for a 150 MW SA Network (Load) Event | Outage
F_MAIN+ML_L6_0400 | 102.3333 | 1000.8333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_T++NIL_MG_R5 | 97.5 | 49.1667 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_QNV++ML_L60_0400 | 97.5 | 0.25 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_MAIN+APD_TL_L6 | 95.0833 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_S_LBBL1_LREG-5MW | 93.75 | 0 | Out= NIL, Lake Bonney Battery (Load Component) LREG Requirement <= 5MW | Outage
F_S+PPT_R5 | 92.9167 | 2.6667 | Raise 5 min Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage
F_S+PPT_R60 | 92.6667 | 2.9167 | Raise 60 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage
F_T+NIL_ML_L5 | 91.8333 | 1145.1667 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_QNV++MG_R5 | 91.4167 | 1.25 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_S_LBBG1_RREG-5MW | 90.3333 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) RREG Requirement <= 5MW | Outage
F_I+ML_L5_APD_LD | 87.9167 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage
F_T++NIL_MG_RECL_R60 | 84.5 | 106.1667 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_S++ML_R6_1 | 79.5 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA, Segment 1 | Outage
F_S++ML_R5 | 76.8333 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA | Outage
F_S+TL_L60_0150 | 74.8333 | 0 | Lower 60 sec Service Requirement for a 150 MW SA Network (Load) Event | Outage
F_Q++ARTW_L60 | 72.25 | 20.0833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_Q++ARTW_L6 | 69 | 20.0833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
F_I+ML_L60_APD_LD | 68.3333 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage
F_Q++MUTW_R60 | 67.75 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
F_T++NIL_MG_RECL_R6 | 66.8333 | 216.5 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_S+SNS_TG_R60 | 66.5 | 0.41667 | Raise 60 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage
F_S+SNS_TG_R5 | 65.6667 | 0.5 | Raise 5 min Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage
F_QNV++ML_L5_0400 | 65 | 0.083333 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_S+SNS_TG_R6_1 | 64 | 2.8333 | Raise 6 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line, Segment1 | Outage
F_T++NIL_WF_TG_R5 | 64 | 95.3333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_S_HPRL_LREG | 60.1667 | 0 | Out= NIL, Hornsdale Battery (Load Component) LREG Requirement <= 0MW | Outage
F_T++NIL_MG_R60 | 59.75 | 20.0833 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_Q++MUTW_R6 | 57.5 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
F_S+PPT_R6_1 | 57.4167 | 2.9167 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 1 | Outage
F_T++COGT_TL_L6 | 50.5 | 2.6667 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_I+ML_L5_0400 | 46.75 | 35.8333 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL
F_S+MLMO_TL_L5 | 45.75 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 5 min requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
F_I+GFT_TG_R6 | 45.1667 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_Q++BCDM_L6 | 44.6667 | 140.1667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
F_T++COGT_TL_L60 | 44.3333 | 1.1667 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_Q++BCDM_L60 | 43.9167 | 133.0833 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage
F_I+ML_L60_0400 | 40.1667 | 14.75 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL
F_T++COGT_TL_L5 | 39.9167 | 0.41667 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_V_YWPS3_R6 | 39.1667 | 0 | Out= NIL, Yallourn W3 R6 Requirement <= 0MW | Outage
F_S_LBBL1_RREG | 35.9167 | 0 | Out= NIL, Lake Bonney Battery (Load Component) RREG Requirement <= 0MW | Outage
F_T_LI_WY_CA_L5 | 35.25 | 0 | Out= NIL, Liapootah + Wayatinah + Catagunya L5 Requirement <= 0MW | Outage
F_T++NIL_MG_R6 | 34.5833 | 21.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_Q++LDTW_L5 | 31.3333 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
F_S++HYSE_L60 | 28.9167 | 443.5 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
F_S_HPRG_RREG | 28.9167 | 0 | Out= NIL, Hornsdale Battery (Generation Component) RREG Requirement <= 0MW | Outage
F_ESTN++MLMO_L6 | 27.5 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
F_QNV+DYN_LREG | 27.0833 | 0 | Qld, NSW and Vic Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | Outage
F_S++ML_R60 | 27.0833 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA | Outage
F_T++NIL_WF_TG_R60 | 26.5 | 63.9167 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_QNV++LREG_0210 | 25.0833 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Outage
F_T++NIL_WF_TG_R6 | 24.4167 | 61.75 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN++GFT_TG_R60 | 22.9167 | 0 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_I+WIP_N-2_ML_L6 | 21.1667 | 13.5833 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 6 sec requirement | Outage
F_T+GTTE_TL_L6 | 21.0833 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_T+GTTE_TL_L60 | 21 | 0 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_QNV++MLMO_L60 | 20.8333 | 0.16667 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++ARTW_L5 | 20.1667 | 16.4167 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
F_QNV++MLMO_L6 | 19.75 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_S+MLMO_TL_L6_2 | 17.8333 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage
F_S++MOPS1_R60 | 17.25 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Mortlake 1 is the largest generation risk in SA (MOPS connects to SA) | Outage
F_S++MOPS1_R5 | 17.0833 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Mortlake 1 is the largest generation risk in SA (MOPS connects to SA) | Outage
F_S++MOPS1_R6_1 | 16.8333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake 1 is the largest generation risk in SA (MOPS connects to SA), Segment 1 | Outage
F_S++ML_L5 | 16.8333 | 0 | Lower 5 min Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
F_Q++NIL_R5 | 16.5 | 7.3333 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
F_S++ML_L6_1 | 16.1667 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 1 | Outage
F_S_HPRL_LREG-5MW | 15.0833 | 0 | Out= NIL, Hornsdale Battery (Load Component) LREG Requirement <= 5MW | Outage
F_T_LI_WY_CA_L60 | 14.75 | 0 | Out= NIL, Liapootah + Wayatinah + Catagunya L60 Requirement <= 0MW | Outage
F_Q++8E_L6 | 14.6667 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
F_ESTN+APD_TL_L5 | 14.5 | 0.16667 | Lower 5 min requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_Q++8E_L60 | 14.5 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage
F_ESTN+APD_TL_L60 | 14.4167 | 0.16667 | Lower 60 sec requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_ESTN++MLMO_L5 | 14.1667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
F_S_LBBL1_LREG | 13.1667 | 0 | Out= NIL, Lake Bonney Battery (Load Component) LREG Requirement <= 0MW | Outage
F_T_FISHER_L6 | 13.1667 | 0 | Out= NIL, Fisher L6 Requirement <= 0MW | Outage
F_Q++8C_L6 | 12.5833 | 3.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
F_T_LI_WY_CA_L6 | 12.1667 | 0 | Out= NIL, Liapootah + Wayatinah + Catagunya L6 Requirement <= 0MW | Outage
F_S_HPRG_RREG-5MW | 12 | 0 | Out= NIL, Hornsdale Battery (Generation Component) RREG Requirement <= 5MW | Outage
F_Q++BCDM_L5 | 11.1667 | 61.5833 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
F_QNV++APD_TL_L60 | 11 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
F_QNV++APD_TL_L5 | 10.5833 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
F_ESTN++MLTR_L60 | 10.1667 | 28.25 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_Q++8C_L60 | 10.1667 | 3.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage
F_T++CSGO_TG_R60 | 9.9167 | 0.33333 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_S+LREG_0035 | 9.9167 | 0.083333 | SA Lower Regulation FCAS Requirement greater than 35 MW | Outage
F_QNV++MLTR_L6 | 9.1667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_MAIN++WIP_N-2_MLL6 | 8.75 | 9.5833 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage
F_V_YWPS4_R6 | 7.8333 | 0 | Out= NIL, Yallourn W4 R6 Requirement <= 0MW | Outage
F_S++MOPS2_R6_1 | 7.75 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake 2 is the largest generation risk in SA (MOPS connects to SA), Segment 1 | Outage
F_Q++LDMU_L60 | 7.6667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
F_MAIN++GFT_TG_R5 | 7.5 | 0 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_ESTN+TL_L60_0600 | 7.3333 | 0 | Lower 60 sec Service Requirement for a Eastern Network Event, TL = 600 | Outage
F_ESTN+TL_L5_0600 | 7.3333 | 0 | Lower 5 min Service Requirement for a Eastern Network Event, TL = 600 | Outage
F_ESTN+TL_L6_0600 | 7.3333 | 0 | Lower 6 sec Service Requirement for a Eastern Network Event, TL = 600 | Outage
F_NQ+ML_L6_0400 | 6.9167 | 0 | Lower 6 sec Service Requirement for a NSW and Qld Load Event, ML = 400 | Outage
F_VST+MG_R6 | 6.9167 | 0 | Raise 6 sec requirement for a Vic, SA and Tas Generation Event | Outage
F_NQ+ML_L60_0400 | 6.9167 | 0 | Lower 60 sec Service Requirement for a NSW and Qld Load Event, ML = 400 | Outage
F_NQ+ML_L5_0400 | 6.9167 | 0 | Lower 5 min Service Requirement for a NSW and Qld Load Event, ML = 400 | Outage
F_NQ+MG_R5 | 6.9167 | 0 | Raise 5 min Service Requirement for separated NSW and Qld Generation Event | Outage
F_VST+MG_R5 | 6.9167 | 0 | Raise 5 min requirement for a Vic, SA and Tas Generation Event | Outage
F_NQ+MG_R6 | 6.9167 | 0 | Raise 6 sec Service Requirement for separated NSW and Qld Generation Event | Outage
F_VST+LREG_0160 | 6.9167 | 0 | Vic, SA and Tas Lower Regulation Requirement greater than 160 MW | Outage
F_NQ+MG_R60 | 6.9167 | 0 | Raise 60 sec Service Requirement for separated NSW and Qld Generation Event | Outage
F_T++CSGO_TG_R6 | 6.8333 | 0.083333 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_VST+MG_R60 | 6.8333 | 0 | Raise 60 sec requirement for a Vic, SA and Tas Generation Event | Outage
F_T++CO_752_TL_L60 | 6.75 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_Q++MUTW_R5 | 6.6667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
F_T++CO_752_TL_L6 | 6.5833 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_Q++LDMU_L6 | 6.5 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
F_MAIN+ML_L6_APD_LD | 6.3333 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage
F_T++FASH_N-2_TG_R60 | 6.3333 | 2.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_I+TG_R6_1000 | 6.0833 | 0 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage
F_I+TG_R5_1000 | 6.0833 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1000 | Outage
F_ESTN++MLTR_L6 | 6.0833 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
F_S_LBBG1_LREG | 6.0833 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) LREG Requirement <= 0MW | Outage
F_I+TG_R60_1000 | 6.0833 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage
F_Q_W/HOE_R5 | 6 | 8.9167 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage
F_T+COGT_TL_L60 | 5.5833 | 0 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_NQ+LREG_0160 | 5.5833 | 0 | Separated NSW and Qld Lower Regulation Requirement greater than 160 MW | Outage
F_T++CO_752_TL_L5 | 5.5833 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T+COGT_TL_L6 | 5.5833 | 0 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_S+MLMO_TL_L6_1 | 5.5833 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage
F_T+COGT_TL_L5 | 5.5833 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_S++TIB4_R6_1 | 5.5 | 0.91667 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA, Segment 1 | Outage
F_T+CSGO_TG_R60 | 5.5 | 6 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_T+CSGO_TG_R5 | 5.4167 | 0.66667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_S++HYSE_L6_1 | 5.4167 | 390.4167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
F_MAIN+GFT_TG_R60 | 5.4167 | 0 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+GFT_TG_R5 | 5.4167 | 0 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_V_APD01_L60 | 5.3333 | 605.4167 | Out= NIL, APD Potline 1 L60 Requirement <= 0MW | Outage
F_V_APD01_L6 | 5.3333 | 605.4167 | Out= NIL, APD Potline 1 L6 Requirement <= 0MW | Outage
F_V_APD01_L5 | 5.3333 | 605.4167 | Out= NIL, APD Potline 1 L5 Requirement <= 0MW | Outage
F_T++FASH_N-2_TG_R5 | 5.25 | 1.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T++NIL_TL_L6_DS | 5.25 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_Q++8C_L5 | 5.1667 | 2.1667 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
F_S++HYSE_L5 | 5.0833 | 101.5 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
F_MAIN++ML_L5_0400 | 5.0833 | 2.5 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_VST+RREG_0170 | 5.0833 | 0 | Vic, SA and Tas Raise Regulation Requirement greater than 170 MW | Outage
F_QNV++MLTR_L60 | 4.9167 | 4.9167 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_MAIN++ML_L60_0400 | 4.8333 | 1.3333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_S++TIB4_R5 | 4.6667 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA | Outage
F_MAIN++NIL_BL_L6 | 4.6667 | 0 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_T++CSGO_TG_R5 | 4.5833 | 0.33333 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_T++FASH_N-2_TG_R6 | 4.5 | 3.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T++NIL_TL_L60_DS | 4.5 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_Q++LDTW_R60 | 4.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
F_T+CSGO_TG_R6_1 | 4.25 | 4.25 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage
F_MAIN++GFT_TG_R6 | 4.1667 | 0 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_T++NIL_TL_L5_DS | 3.8333 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_ESTN++MLTR_L5 | 3.75 | 5 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
F_S++ML_L6_2 | 3.75 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 2 | Outage
F_S++TIB1_R5 | 3.5833 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 1 is the largest generation risk in SA | Outage
F_S+RREG_0035 | 3.5833 | 0.33333 | SA Raise Regulation FCAS Requirement greater than 35 MW | Outage
F_T+CSGO_TG_R6_2 | 3.5 | 0.083333 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment2 | Outage
F_VS++MG_R60 | 3.4167 | 0 | Raise 60 sec requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
F_S++TIB3_R5 | 3.1667 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA | Outage
F_S++MOPS2_R5 | 3.1667 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Mortlake 2 is the largest generation risk in SA (MOPS connects to SA) | Outage
F_QNV+MG_R60 | 3 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_QNV+MG_R6 | 3 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_T+FASH_N-2_RREG | 3 | 16.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_QNV+MG_R5 | 3 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_QNV+ML_L6_0400 | 2.8333 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage
F_V+NIL_APD01_R5 | 2.75 | 5.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_APD01_L60 | 2.75 | 5.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_V+NIL_APD01_R60 | 2.75 | 5.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_V+NIL_APD01_R6 | 2.75 | 5.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_V+NIL_APD01_L5 | 2.75 | 5.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_V+NIL_APD01_L6 | 2.75 | 5.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_V_YWPS3_R60 | 2.6667 | 0 | Out= NIL, Yallourn W3 R60 Requirement <= 0MW | Outage
F_VST+APD_TL_L6 | 2.6667 | 0 | Lower 6 sec requirement for a Vic, SA and Tas Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_VST+APD_TL_L60 | 2.6667 | 0 | Lower 60 sec requirement for a Vic, SA and Tas Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_VS++APD_TL_L5 | 2.6667 | 0 | Lower 5 min requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage
F_QNV+MLMO_L60 | 2.5833 | 10.0833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+ML_L5_0400 | 2.5833 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage
F_S++TIB2_R6_1 | 2.5833 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA, Segment 1 | Outage
F_QNV+ML_L60_0400 | 2.5833 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage
F_QNV+LREG_0210 | 2.5 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | Outage
F_Q++8E_L5 | 2.5 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
F_Q++NIL_R60 | 2.5 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL
F_VST+TL_L5_0600 | 2.3333 | 0 | Lower 5 min Service Requirement for a Vic, SA and Tas Network Event, TL = 600 | Outage
F_S++MOPS2_R60 | 2.3333 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Mortlake 2 is the largest generation risk in SA (MOPS connects to SA) | Outage
F_VST+TL_L60_0600 | 2.3333 | 0 | Lower 60 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 600 | Outage
F_VST+TL_L6_0600 | 2.3333 | 0 | Lower 6 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 600 | Outage
F_VS++TL_L6_0600 | 2.3333 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage
F_Q++LDTW_R6 | 2.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage
F_VS++APD_TL_L60 | 2.25 | 0 | Lower 60 sec requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage
F_VS++TL_L5_0600 | 2.25 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage
F_S++TIB2_R5 | 2.25 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA | Outage
F_VS++APD_TL_L6 | 2.1667 | 0 | Lower 6 sec requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage
F_T++BLSPS_EXP_L6_1 | 2.0833 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
F_S++TIB4_R60 | 2.0833 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA | Outage
F_S++ML_L60 | 2.0833 | 0 | Lower 60 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
F_T++BLSPS_EXP_L60_1 | 2.0833 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
F_S++TIB2_R60 | 2.0833 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA | Outage
F_VST+APD_TL_L5 | 2.0833 | 0 | Lower 5 min requirement for a Vic, SA and Tas Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_T++BLSPS_EXP_L5 | 2 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage
F_VS++TL_L60_0600 | 2 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage
F_QNV+RREG_0220 | 2 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink unable to transfer FCAS | Outage
F_MAIN+ML_L5_APD_LD | 1.9167 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage
F_MAIN++ML_L5_APD_LD | 1.9167 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
F_QNV+MLMO_L6 | 1.8333 | 0.083333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_MAIN++ML_L60_APD_L | 1.8333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
F_VS++MG_R6 | 1.8333 | 0 | Raise 6 sec requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
F_MAIN+ML_L60_APD_LD | 1.75 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage
F_T+FASH_N-2_TG_R60 | 1.5833 | 5.3333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_S+PPT_R6_2 | 1.5 | 0.5 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 2 | Outage
F_VS++MG_R5 | 1.5 | 0 | Raise 5 min requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
F_QNV++HGML_L6 | 1.4167 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_S+RREG_0070 | 1.4167 | 0 | SA Raise Regulation Requirement greater than 70 MW | Other
F_WESTCOAST_LREG_0 | 1.4167 | 1.8333 | LREG FCAS of West Coast Generation limited to 0 MW | Outage
F_VST+TL_L60_0500 | 1.3333 | 0 | Lower 60 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 500 | Outage
F_QNV++RREG_0220 | 1.3333 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink able transfer FCAS | Outage
F_WESTCOAST_RREG_0 | 1.3333 | 2.75 | RREG FCAS of West Coast Generation limited to 0 MW | Outage
F_MAIN++TG_R60_1000 | 1.3333 | 0 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage
F_VST+TL_L5_0500 | 1.3333 | 0 | Lower 5 min Service Requirement for a Vic, SA and Tas Network Event, TL = 500 | Outage
F_VS++TL_L6_0500 | 1.3333 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage
F_Q++LDMU_R6 | 1.3333 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
F_ESTN++HGML_L60 | 1.3333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 60 sec Requirement | Outage
F_VST+TL_L6_0500 | 1.3333 | 0 | Lower 6 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 500 | Outage
F_ESTN++HGTR_L60 | 1.3333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_QNV++HGML_L60 | 1.3333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+FASH_N-2_TG_R5 | 1.25 | 5.4167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_S++TIB1_R6_1 | 1.25 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 1 is the largest generation risk in SA, Segment 1 | Outage
F_S++TIB3_R60 | 1.25 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA | Outage
F_Q++LDMU_L5 | 1.1667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
F_T+FARE_N-2_TG_R60 | 1.1667 | 5.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_V_YWPS3_RREG | 1.1667 | 0 | Out= NIL, Yallourn W3 RREG Requirement <= 0MW | Outage
F_QNV++HGTR_L60 | 1.1667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_S++TIB1_R60 | 1.0833 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 1 is the largest generation risk in SA | Outage
F_T+FARE_N-2_TG_R5 | 1.0833 | 2.8333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_ESTN++HGTR_L5 | 1.0833 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
F_T+FASH_N-2_TG_R6_2 | 1.0833 | 4.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage
F_QNV++HGTR_L6 | 1.0833 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_S++TIB3_R6_1 | 1 | 1.3333 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA, Segment 1 | Outage
F_MAIN+ML_L5_0400 | 0.91667 | 5.6667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_NQ+RREG_0170 | 0.91667 | 0 | Separated NSW and Qld Raise Regulation Requirement greater than 170 MW | Outage
F_MAIN+ML_L60_0400 | 0.91667 | 3.1667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_Q++ARTW_R60 | 0.83333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
F_VS++TL_L5_0500 | 0.83333 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage
F_ESTN++HGML_L5 | 0.83333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 5 min Requirement | Outage
F_MAIN++MG_R6_1000 | 0.66667 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 1000, Basslink able to transfer FCAS | Outage
F_I+MG_R6_1000 | 0.66667 | 0 | Raise 6 sec Service Requirement for a NEM Generation Event, MG = 1000 | Outage
F_QNV++HGML_L5 | 0.66667 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_Q++NIL_R6 | 0.66667 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 6 sec requirement for loss of a NSW 750 MW unit | NIL
F_I+MG_R60_1000 | 0.66667 | 0 | Raise 60 sec Service Requirement for a NEM Generation Event, MG = 1000 | Outage
F_T++FARE_N-2_TG_R6 | 0.66667 | 2.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T+FARE_N-2_TG_R6_2 | 0.66667 | 2 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage
F_S++MOPS1_R6_2 | 0.66667 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake 1 is the largest generation risk in SA (MOPS connects to SA), Segment 2 | Outage
F_I+MG_R5_1000 | 0.66667 | 0 | Raise 5 min Service Requirement for a NEM Generation Event, MG = 1000 | Outage
F_MAIN++MG_R60_1000 | 0.66667 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 1000, Basslink able to transfer FCAS | Outage
F_VST+TL_L5_0550 | 0.58333 | 0 | Lower 5 min Service Requirement for a Vic, SA and Tas Network Event, TL = 550 | Outage
F_VS++TL_L6_0550 | 0.58333 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage
F_VST+TL_L6_0550 | 0.58333 | 0 | Lower 6 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 550 | Outage
F_VST+TL_L60_0550 | 0.58333 | 0 | Lower 60 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 550 | Outage
F_V_YWPS4_RREG | 0.58333 | 0 | Out= NIL, Yallourn W4 RREG Requirement <= 0MW | Outage
F_VS++LREG_0160 | 0.58333 | 0 | Vic and SA Lower Regulation Requirement greater than 160 MW, Basslink able transfer FCAS | Outage
F_VS++TL_L60_0500 | 0.58333 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage
F_I+TG_R5_0850 | 0.5 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 850 | Outage
F_QNV++APD_TL_L6 | 0.5 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
F_MAIN++ML_L6_APD | 0.5 | 35 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_VS++TL_L5_0550 | 0.5 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage
F_I+TG_R60_0850 | 0.5 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 850 | Outage
F_QNV++MLMO_L5 | 0.5 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_VS++TL_L60_0550 | 0.5 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage
F_MAIN+GFT_TG_R6 | 0.41667 | 0 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_S+NIL_HPR_G+L_LREG | 0.41667 | 0.083333 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS LowerReg ramping constraint | NIL
F_S+APD_TL_L60 | 0.41667 | 0 | Lower 60 sec requirement in SA for loss of both APD potlines, Separation between Heywood (HYTS) and Moorabool (MLTS) | Outage
F_T+FARE_N-2_RREG | 0.41667 | 4.8333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_QNV+MLTR_L6 | 0.41667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_QNV++HGTR_L5 | 0.41667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_V++MOPS_R5 | 0.41667 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Mortlake Station is the largest generation risk in SA (MOPS connects to SA) | Outage
F_I+TG_R6_0850 | 0.41667 | 0 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 850 | Outage
F_V++MOPS_R60 | 0.41667 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Mortlake Station is the largest generation risk in SA (MOPS connects to SA) | Outage
F_V++MOPS_R6_1 | 0.41667 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake Station is the largest generation risk in SA (MOPS connects to SA), Segment 1 | Outage
F_I+ML_L6_APD | 0.41667 | 166.25 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage
F_QNV++MLTR_L5 | 0.41667 | 0.33333 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T+FARE_N-2_TG_R6_1 | 0.41667 | 2.8333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage
F_I+MG_R5_0850 | 0.33333 | 0 | Raise 5 min Service Requirement for a NEM Generation Event, MG = 850 | Outage
F_I+MG_R60_0850 | 0.33333 | 0 | Raise 60 sec Service Requirement for a NEM Generation Event, MG = 850 | Outage
F_I+MG_R6_0850 | 0.33333 | 0 | Raise 6 sec Service Requirement for a NEM Generation Event, MG = 850 | Outage
F_MAIN++MG_R5_1000 | 0.33333 | 0 | Raise 5 min Service Requirement for a Mainland Generation Event, MG = 1000, Basslink able to transfer FCAS | Outage
F_S+NIL_HPR_G+L_RREG | 0.33333 | 0 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS RaiseReg ramping constraint | NIL
F_S+APD_TL_L6 | 0.33333 | 0 | Lower 6 sec requirement in SA for loss of both APD potlines, Separation between Heywood (HYTS) and Moorabool (MLTS) | Outage
F_T++GO_A752_TG_R60 | 0.33333 | 0 | Out= Gordon CB A752, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_QNV+APD_TL_L60 | 0.25 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable transfer FCAS | Outage
F_V_YWPS4_R60 | 0.25 | 0 | Out= NIL, Yallourn W4 R60 Requirement <= 0MW | Outage
F_MAIN++YW134_MGR6 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
F_T++GO_A752_TG_R5 | 0.25 | 0 | Out= Gordon CB A752, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T++GO_C752_TG_R6 | 0.25 | 0 | Out= Gordon CB C752, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T++FARE_N-2_TG_R5 | 0.25 | 1.3333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_QNV+APD_TL_L5 | 0.25 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable transfer FCAS | Outage
F_T++GO_A752_TG_R6 | 0.25 | 0 | Out= Gordon CB A752, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_I+YW134_N-2_MG_R5 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Global Raise 5 Min requirement | Outage
F_QNV+MLTR_L60 | 0.25 | 1.5 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_S++MOPS2_R6_2 | 0.25 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake 2 is the largest generation risk in SA (MOPS connects to SA), Segment 2 | Outage
F_I+YW134_N-2_MG_R6 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Global Raise 6 sec requirement | Outage
F_I+YW134_N-2_MG_R60 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Global Raise 60 sec requirement | Outage
F_MAIN++YW134_MGR60 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
F_MAIN++YW134_MGR5 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage
F_T+GTTE_TL_L5 | 0.16667 | 0 | Out = one George Town to Temco 110 kV line, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_Q+MM1_R5 | 0.16667 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage
F_S_DLBAT-L_L60 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Load Component) L60 Requirement <= 0MW | Outage
F_ESTN++HGTR_L6 | 0.16667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
F_NVS++LREG_0210 | 0.16667 | 0 | NSW, Vic and SA Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Outage
F_Q+MG_R6 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event | Outage
F_Q+TNT_R6 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Tarong North) | Outage
F_S_DLBAT-G_R5 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Generation Component) R5 Requirement <= 0MW | Outage
F_NVS++APD_TL_L5 | 0.16667 | 0 | Lower 5 min requirement for a NSW, Vic and SA Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
F_MAIN++MG_R6_0850 | 0.16667 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
F_T_GORDON_R6 | 0.16667 | 0 | Out= NIL, Gordon R6 Requirement <= 0MW | Outage
F_Q+KC_R6 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Kogan Creek) | Outage
F_Q+ML_L60_0400 | 0.16667 | 0 | Lower 60 sec Service Requirement for Qld Load Event, ML = 390 | Outage
F_Q+MM1_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage
F_Q+MM2_R6 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Millmerran unit 2) | Outage
F_S_DLBAT-G_R60 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Generation Component) R60 Requirement <= 0MW | Outage
F_T++NIL_BLSPS_R6_1 | 0.16667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_T_GORDON_R60 | 0.16667 | 0 | Out= NIL, Gordon R60 Requirement <= 0MW | Outage
F_Q+KC_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Kogan Creek) | Outage
F_Q+TNT_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Tarong North) | Outage
F_STHN+LREG_0210 | 0.16667 | 0 | Southern Lower Regulation Requirement greater than 210 MW | Outage
F_STHN+MG_R6 | 0.16667 | 0 | Raise 6 sec Service Requirement for a Southern Generation Event | Outage
F_QNV+MLMO_L5 | 0.16667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+TL_L5_0600 | 0.16667 | 0 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS | Outage
F_Q+CC4_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Callide C unit 4) | Outage
F_Q+MG_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event | Outage
F_Q+ML_L5_0400 | 0.16667 | 0 | Lower 5 min Service Requirement for Qld Load Event, ML = 390 | Outage
F_Q+ML_L6_0400 | 0.16667 | 0 | Lower 6 sec Service Requirement for Qld Load Event, ML = 390 | Outage
F_Q+MM1_R6 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage
F_STHN+APD_TL_L60 | 0.16667 | 0 | Lower 60 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_STHN+RREG_0220 | 0.16667 | 0 | Southern Raise Regulation Requirement greater than 220 MW | Outage
F_S_DLBAT-G_R6 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Generation Component) R6 Requirement <= 0MW | Outage
F_T_FAJB_RREG | 0.16667 | 0 | Out=Farrell-John Butters 220KV line. RREG <= 0MW | Outage
F_QNV+TL_L6_0600 | 0.16667 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS | Outage
F_QNV+MLTR_L5 | 0.16667 | 0.083333 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_NVS++APD_TL_L6 | 0.16667 | 0 | Lower 6 sec requirement for a NSW, Vic and SA Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
F_NVS++APD_TL_L60 | 0.16667 | 0 | Lower 60 sec requirement for a NSW, Vic and SA Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
F_Q+KC_R5 | 0.16667 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Kogan Creek) | Outage
F_Q+LREG_0110 | 0.16667 | 0 | Qld Lower Regulation Requirement greater than 110 MW | Outage
F_STHN+APD_TL_L6 | 0.16667 | 0 | Lower 6 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_STHN+MG_R5 | 0.16667 | 0 | Raise 5 min Service Requirement for a Southern Generation Event | Outage
F_STHN+MG_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for a Southern Generation Event | Outage
F_S_DLBAT-L_L5 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Load Component) L5 Requirement <= 0MW | Outage
F_Q_MACKAYGT_R5 | 0.16667 | 2.6667 | Out= NIL, Mackay GT R5 Requirement <= 0MW | Outage
F_QNV+TL_L60_0600 | 0.16667 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS | Outage
F_T++GO_C752_TG_R60 | 0.16667 | 0 | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_Q+CC4_R6 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Callide C unit 4) | Outage
F_Q+MM2_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Millmerran unit 2) | Outage
F_MAIN++MG_R60_0850 | 0.16667 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
F_Q++8C_R60 | 0.16667 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 60 sec Requirement | Outage
F_Q+CC3_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Callide C unit 3) | Outage
F_S_DLBAT-L_L6 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Load Component) L6 Requirement <= 0MW | Outage
F_T+CO_752_TL_L6 | 0.083333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_STHN++MUTW_R60 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88) line, Southern Raise 60 sec Requirement | Outage
F_S+HL_TG_R6_1 | 0.083333 | 0 | Raise 6 sec Service Requirement for the loss of Canowie to Hallett 275 kV line, Segment1 | Outage
F_T+CO_752_TL_L5 | 0.083333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_Q+CC3_R6 | 0.083333 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Callide C unit 3) | Outage
F_S+APD_TL_L5 | 0.083333 | 0 | Lower 5 min requirement in SA for loss of both APD potlines, Separation between Heywood (HYTS) and Moorabool (MLTS) | Outage
F_QNV++TL_L5_0600 | 0.083333 | 0 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink able to transfer FCAS | Outage
F_I+TG_R60_0700 | 0.083333 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 700 | Outage
F_S+HL_TG_R5 | 0.083333 | 0 | Raise 5 min Service Requirement for the loss of Canowie to Hallett 275 kV line | Outage
F_S+HL_TG_R60 | 0.083333 | 0 | Raise 60 sec Service Requirement for the loss of Canowie to Hallett 275 kV line | Outage
F_T+FASH_N-2_TG_R6_1 | 0.083333 | 5.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage
F_ESTN++HGML_L6 | 0.083333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 6 sec Requirement | Outage
F_QNV++TL_L60_0600 | 0.083333 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink able to transfer FCAS | Outage
F_V++MOPS_R6_2 | 0.083333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake Station is the largest generation risk in SA (MOPS connects to SA), Segment 2 | Outage
F_Q+MM2_R5 | 0.083333 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Millmerran unit 2) | Outage
F_T_FAMA_R5 | 0.083333 | 0 | Out=Farrell-Mackintosh 110KV line. R5 <= 0MW | Outage
F_T+CO_752_TL_L60 | 0.083333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_I+TG_R5_0700 | 0.083333 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 700 | Outage
F_Q+RREG_0110 | 0.083333 | 0 | Qld Raise Regulation Requirement greater than 110 MW | Outage

## Binding Impact
Constraint Equation ID | 2020 Marginal Values | 2019 Marginal Values | 2020 Hours | 2019 Hours | Description | Type | Region | Column1
Q_NIL_STRGTH_MEWF | 17924238.2776 | 405396.1337 | 1507.9167 | 32.1667 | Out = Nil, limit Mt Emerald WF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
S_WIND_1200_AUTO & S_NIL_STRENGTH_1 | 11147928.6698 | 8084357.5743 | 942.1667 | 669 | Upper limit (1300 to 1750 MW) for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements. Automatically swamps out when required HIGH combination is online. | NIL | System Strength | SA
Q_NIL_STRGTH_HAUSF | 10412278.5645 | 12541.1875 | 858.5833 | 1.3333 | Out = Nil, limit Haughton SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
N>N-NIL_CLDP_1 | 7501340.6571 | 5628169.9325 | 583.6667 | 443.5 | Out= Nil, avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | NIL | Thermal | NSW
V_MURRAWRWF_MAX | 6496189.977 | 142820.3209 | 971.75 | 174.5833 | Limit MW output of Murra Warra wind farm to hold point levels during day/night | Outage | Discretionary | Vic
T_MRWF_FOS | 6217993.99 | 0 | 1188 | 0 | Limit Musselroe wind farm due to upper limit on Tasmanian generator events. Limit is 153 MW (effective 144 MW at the connection point at Derby) | NIL | Other | Tas
V_BANSF_BBD_60 | 3040110.1981 | 1023512.6408 | 277 | 79.9167 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Discretionary | Vic
Q_MEWF1_ZERO | 2856655.1272 | 0 | 247.9167 | 0 | Mt Emerald Wind Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q>NIL_COLNVSF1 | 2712977.2788 | 905855.2266 | 307.9167 | 86.4167 | Out = Nil, Limit Collinsville Solar Farm to thermal rating of Powerlink's RMU | NIL | Thermal | Qld
V>V_NIL_17 | 2501675.7954 | 985.596 | 235.5833 | 0.25 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback | NIL | Thermal | Vic
Q_STR_333104_MEWF25 | 2242763.1836 | 0 | 180.9167 | 0 | Limit Mt Emerald WF to 25 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | System Strength | Qld
F_S+TL_L6_OD | 1918939.114 | 296421.5599 | 269.25 | 4.8333 | Lower 6 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS | FCAS
Q>SSRV_M020/3 | 1874974.2698 | 0 | 151.3333 | 0 | Out= Nil, Limit Susan River to the continuous ratings of Feeder M020/3 Susan River to T section 66kV line, Feedback | Outage | Thermal | Qld
V_MURRAWRWF_FLT_90 | 1603340.3389 | 1891.5574 | 130.6667 | 2.1667 | Limit Murra Warra Wind Farm upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
F_T_AUFLS2_R6 | 1588523.7296 | 1581843.1973 | 4276.6667 | 5076.5 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL | FCAS | FCAS
Q_STR_3113103_MEWF | 1468288.2004 | 0 | 125.4167 | 0 | Limit Mt Emerald WF to 25% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
Q_HAUGHTSF1_ZERO | 1431791.1197 | 0 | 114.25 | 0 | Haughton Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
F_S++MOPS2_R6_1 | 1389692.2755 | 0 | 10.5833 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake 2 is the largest generation risk in SA (MOPS connects to SA), Segment 1 | Outage | FCAS | FCAS
F_S+TL_L60_OD | 1343795.4082 | 98196.49 | 342.8333 | 4.8333 | Lower 60 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS | FCAS
V_YENDWF_MAX | 1305470.9239 | 86854.7926 | 796.5833 | 31.6667 | Limit MW output of Yendon wind farm to hold point levels during day/night | Outage | Discretionary | Vic
F_S+TL_L5_OD | 1270260.3037 | 6645.1099 | 303.8333 | 4.6667 | Lower 5 min Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS | FCAS
N_DARLSF1_ZERO | 1143095.0198 | 0 | 92 | 0 | Darlington Point solar farm upper limit of 0 MW and all inverters disconnected. | Outage | Unit Zero | NSW
F_S+TG_R60_150 | 1129792.6195 | 0 | 221.1667 | 0 | Raise 60 sec Service Requirement for a 150 MW SA Generation Event | Outage | FCAS | FCAS
N^^N_NIL_2 | 1123394.3221 | 0 | 165.25 | 0 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
F_MAIN+NIL_DYN_RREG | 1089423.7806 | 2708935.0518 | 3199.5 | 3535.3333 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL | FCAS | FCAS
Q_STR_333104_HASF25 | 975083.0195 | 0 | 77.9167 | 0 | Limit Haughton SF to 25 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | System Strength | Qld
F_S++MOPS1_R6_1 | 973063.0588 | 0 | 9.8333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake 1 is the largest generation risk in SA (MOPS connects to SA), Segment 1 | Outage | FCAS | FCAS
V_MURRAWRWF_FLT_0 | 854071.0466 | 272157.5749 | 68.75 | 28 | Limit Murra Warra Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
N_STWF1_ZERO | 848820.5999 | 1548348.9304 | 65.5833 | 118.5833 | Silverton wind farm upper limit of 0 MW and all wind turbines disconnected. | Outage | Unit Zero | NSW
Q_STR_311310_HASF | 822029.7332 | 0 | 67.4167 | 0 | Limit Haughton SF to 25% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
V_BANNERTSF_FLT_25 | 798611.0205 | 0 | 64.0833 | 0 | Limit Bannerton Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KARADSF_FLT_25 | 786643.5279 | 32289.5678 | 63.4167 | 9.3333 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_MACARTHUR_ZERO | 766127.9249 | 775383.7835 | 78.9167 | 311.6667 | Macarthur upper limit of 0 MW | Outage | Unit Zero | Vic
F_I+LREG_0210 | 744148.211 | 433292.9139 | 7770.25 | 2080.0833 | NEM Lower Regulation Requirement greater than 210 MW | NIL | FCAS | FCAS
SA_HYSE2 | 735795.9217 | 2185.5504 | 93.3333 | 1.9167 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage | Region Separation | SA
N_BROKENH1_ZERO | 727068.9855 | 1120113.3125 | 39.5 | 85.1667 | Broken Hill Solar Farm upper limit of 0 MW and all inverters disconnected. | Outage | Unit Zero | NSW
V_BULGANAWF_FLT_0 | 680909.0585 | 0 | 53.1667 | 0 | Limit Bulgana Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V_WEMENSF_FLT_25 | 662686.3523 | 0 | 53.25 | 0 | Limit Wemen Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_S+TL_L6_0150 | 657957.8151 | 0 | 108.9167 | 0 | Lower 6 sec Service Requirement for a 150 MW SA Network (Load) Event | Outage | FCAS | FCAS
N_LIMOSF2_FLT_25 | 657343.4851 | 0 | 52.5 | 0 | Limit Limondale 2 solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_T+NIL_WF_TG_R6 | 651219.4926 | 680382.4102 | 943.8333 | 1278.5 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_NUMURKAH_ZERO | 649562.4303 | 0 | 52.0833 | 0 | Numurkah Solar Farm upper limit of 0 MW | NIL | Unit Zero | Vic
F_S+TG_R5_150 | 616082.6421 | 0 | 217.3333 | 0 | Raise 5 min Service Requirement for a 150 MW SA Generation Event | Outage | FCAS | FCAS
Q_NIL_STRGTH_KIDSF | 613792.2817 | 0 | 50.6667 | 0 | Out = Nil, limit Kidston SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
F_I+RREG_0220 | 599388.7364 | 402238.1693 | 5015.6667 | 1272.5 | NEM Raise Regulation Requirement greater than 200 MW | NIL | FCAS | FCAS
S>NIL_MHNW1_MHNW2 | 596843.5063 | 0 | 144 | 0 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL | Thermal | SA
V_GANWRSF_FLT_25 | 593673.3138 | 899364.8397 | 47.5833 | 231.6667 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | NIL | System Strength | Vic
Q_STR_211383_10DAYSF | 586588.4445 | 0 | 47 | 0 | Limit Daydream SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
N_FINLYSF_FLT_45 | 579143.5898 | 0 | 46.3333 | 0 | Limit Finley solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_BROKENHSF_FLT_25 | 577026.6811 | 0 | 46.25 | 0 | Limit Broken Hill Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_211383_10KIDSF | 571319.7059 | 0 | 47.5 | 0 | Limit Kidston SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_10RRSF | 556784.0703 | 0 | 44.6667 | 0 | Limit Ross River SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_10HAMSF | 555050.5642 | 0 | 46.0833 | 0 | Limit Hamilton SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 549343.9385 | 17930.3082 | 12.0833 | 28.8333 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL | Thermal | Qld
Q_LILYSF1_ZERO | 537460.9367 | 1689078.4567 | 44 | 147.75 | Lilyvale Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
N>N-NIL_9R4_99A | 527353.3867 | 0 | 44.0833 | 0 | Out= Nil, avoid O/L Finley to Mulwala 132kV line (9R4) on trip of Finley to Uranquinty (99A) line, Feedback | NIL | Thermal | NSW
Q_STR_211383_10HAYSF | 513660.9919 | 0 | 42.75 | 0 | Limit Hayman SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
F_MAIN++NIL_MG_R6 | 494315.1712 | 162896.1524 | 2407.0833 | 1764.8333 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_Q++NIL_R5 | 486052.6977 | 833.2284 | 17.5833 | 7.1667 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL | FCAS | FCAS
Q_STR_333104_MEWF70 | 471928.4343 | 0 | 37.5833 | 0 | Limit Mt Emerald WF to 70 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | System Strength | Qld
V_CWWF_ISL_0 | 458514.3055 | 91926.1148 | 37.4167 | 7.1667 | Crowlands Wind Farm total upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
F_S+TL_L5_0150 | 456248.7746 | 0 | 113.4167 | 0 | Lower 5 min Service Requirement for a 150 MW SA Network (Load) Event | Outage | FCAS | FCAS
V_BANNERTSF_FLT_45 | 456214.3986 | 33091.7552 | 40.0833 | 2.4167 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_COLEASF1_ZERO | 455677.8449 | 804083.8048 | 8.8333 | 55.25 | Coleambally solar farm upper limit of 0 MW and all inverters disconnected. | Outage | Unit Zero | NSW
Q_STR_211383_10WHTSF | 454692.3154 | 0 | 39.8333 | 0 | Limit Whitsunday SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
F_S_LBBL1_LREG-5MW | 451352.2728 | 0 | 93.5833 | 0 | Out= NIL, Lake Bonney Battery (Load Component) LREG Requirement <= 5MW | Outage | FCAS | FCAS
F_I+NIL_MG_R6 | 444501.4491 | 311558.3065 | 6571.75 | 6288.5833 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL | FCAS | FCAS
Q>NIL_EMBW_EMLV_DS | 443958.4026 | 0 | 36.0833 | 0 | Out= Nil, limit Emerald SF to 40MW to avoid overload on Emerald - Lilyvale 66kV line on trip of Emerald - Comet - Blackwater 66kV line (6056 or 6011), swamp if Emerald CBs S612,S610 and Blackwater CB S605 are closed (DS only) | NIL | Thermal | Qld
F_S_HPRL_LREG | 442865.0825 | 0 | 60.1667 | 0 | Out= NIL, Hornsdale Battery (Load Component) LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S-DLBAT-G_0 | 441000 | 652500 | 2.5 | 3.75 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW | Outage | Unit Zero | SA
Q_STR_311393_HASF | 432687.7303 | 0 | 33.8333 | 0 | Limit Haughton SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
F_S_LBBG1_RREG-5MW | 432363.1854 | 0 | 90.3333 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) RREG Requirement <= 5MW | Outage | FCAS | FCAS
Q_NIL_STRGTH_CLRSF | 422268.6823 | 0 | 34.75 | 0 | Out = Nil, limit Clare SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
Q_9C3_10C21_MEWF | 417301.2772 | 0 | 34 | 0 | Limit Mt_Emerald 70% capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | System Strength | Qld
V_DUNDWF1_ZERO | 416720.5833 | 0 | 34.3333 | 0 | Dundonnell wind farm 1 upper limit of 0 MW | Outage | Unit Zero | Vic
V_DUNDWF3_ZERO | 413394.31 | 0 | 34 | 0 | Dundonnell wind farm 3 upper limit of 0 MW | Outage | Unit Zero | Vic
S>NIL_NIL_NWMH2 | 408645.2942 | 450786.0819 | 10.8333 | 59.5833 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
F_S_HPRL_LREG-5MW | 401975.8728 | 0 | 15.0833 | 0 | Out= NIL, Hornsdale Battery (Load Component) LREG Requirement <= 5MW | Outage | FCAS | FCAS
N_BROKENHSF_FLT_0 | 398917.9902 | 580557.7778 | 32.9167 | 44.8333 | Limit Broken Hill Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | NSW
F_S_HPRG_RREG-5MW | 394507.8971 | 0 | 11.9167 | 0 | Out= NIL, Hornsdale Battery (Generation Component) RREG Requirement <= 5MW | Outage | FCAS | FCAS
N^^N_NIL_3 | 394269.3632 | 0 | 104.4167 | 0 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse for contingency trip of Bendigo-Kerang 220kV line in NW Victoria | NIL | Voltage Stability | NSW
F_S+PPT_R6_1 | 393881.3577 | 156.5247 | 60.75 | 0.25 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 1 | Outage | FCAS | FCAS
T>T_NIL_110_1 | 393637.9652 | 3244766.4534 | 32.5833 | 251.5833 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Thermal | Tas
V_DUNDWF2_ZERO | 388169.6738 | 0 | 31.8333 | 0 | Dundonnell wind farm 2 upper limit of 0 MW | Outage | Unit Zero | Vic
V_BANNERTSF_FLT_0 | 387397.3851 | 950617.7562 | 32.1667 | 72.3333 | Limit Bannerton Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V_OAKHILL_TFB_42 | 387017.541 | 758019.1767 | 13.0833 | 48.4167 | Out = Nil, Oaklands Hill Windfarm upper limit of 42.7 MW due to Oaklands Hill windfarm TFB mode operation, DS only. Swamp out if TFB mode is OFF | NIL | Discretionary | Vic
F_T+NIL_MG_R6 | 384090.3434 | 318836.4857 | 787.75 | 743.25 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>NIL_HUWT_STBG2 | 383878.6628 | 178507.7541 | 42.25 | 15.3333 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL | Thermal | SA
NRM_NSW1_VIC1 | 381247.2023 | 39023.559 | 22.0833 | 2.75 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue | Negative Residue
NRM_QLD1_NSW1 | 381008.7281 | 31694.3993 | 5.9167 | 9.25 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue | Negative Residue
Q_STR_21138_EMSF50 | 375813.9969 | 0 | 30.5 | 0 | Limit Emerald SF to 50% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
Q_NIL_STRGTH_RGBSF | 370243.1578 | 0 | 49.4167 | 0 | Out = Nil, limit Rugby Run SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
F_S_LBBG1_RREG | 366852.4287 | 0 | 141 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S++MOPS1_R60 | 366607.98 | 0 | 17.0833 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Mortlake 1 is the largest generation risk in SA (MOPS connects to SA) | Outage | FCAS | FCAS
S^SETX_GEN_CAP | 361492.7868 | 138435.3051 | 79.4167 | 27.5 | Out= One South East 275/132kV transformer O/S, avoid local voltage collapse on trip of remaining South East transformer, | Outage | Thermal | SA
Q_9C3_10C21_HASF | 352199.4057 | 0 | 29.4167 | 0 | Limit Haughton70% Max capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | System Strength | Qld
N_DARLSF_FLT_80 | 344342.1393 | 0 | 27.5833 | 0 | Limit Darlington Pt Solar Farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_BROKENHSF_FLT_26 | 343260.7947 | 1429240.3057 | 28.1667 | 127.8333 | Limit Broken Hill Solar Farm upper limit to 26 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_Q++MUTW_L60 | 343223.5276 | 0 | 1115.5833 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
SA_ISLE_HPR_HIGH_SOC | 335079.3193 | 0 | 3.4167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Hornsdale battery of 2 MW, except when state of charge is above 70% | Outage | Other | SA
V_WEMENSF_FLT_45 | 325751.4221 | 2066.6556 | 28.5 | 1.25 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_MLMO_VS_LB_CAN_50 | 322408.5362 | 30348.9156 | 147.5 | 18.5 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS/DUNDWF generating. | Outage | System Strength | SA
Q>CMTX | 318973.5115 | 0 | 26.75 | 0 | Out = Clermont T1 or T2 132/66 kV transformer, limit to Clermont Solar Farm to 30MW to prevent overload on remaining transformer | Outage | Thermal | Qld
V>>V_NIL_9 | 316117.272 | 226.5974 | 147.9167 | 0.33333 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
F_Q++MUTW_R60 | 315245.2416 | 0 | 67.75 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
N::N_CRGR_2 | 314589.5344 | 0 | 45.8333 | 0 | Out = Crookwell to Gullen Range(3H), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | Transient Stability | NSW
V_BANSF_BBD_80 | 312338.3776 | 6436.0837 | 38.8333 | 0.5 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
F_T_NIL_MINP_R6 | 304090.6277 | 159708.0994 | 1530.0833 | 1227 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL | FCAS | FCAS
S:V_PA_SVC_420 | 301726.6067 | 2456.6519 | 362.4167 | 0.5 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
V_WEMENSF_FLT_0 | 300270.0245 | 906918.1398 | 24.4167 | 100.5833 | Limit Wemen Solar Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
T_T_FASH_10_N-2 | 297498.2673 | 60216.04 | 10.75 | 0.66667 | Out = NIL, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain John Butters and Bastyan to 0 MW as per TAS Networks advice | Outage | Discretionary | Tas
Q_STR_211383_10COLSF | 293985.8893 | 0 | 42.1667 | 0 | Limit Collinsville SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
F_S+PPT_R5 | 290521.4721 | 1971.6065 | 92.5 | 2.75 | Raise 5 min Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage | FCAS | FCAS
F_T+NIL_MG_RECL_R6 | 287533.6435 | 420950.384 | 727.6667 | 1669.3333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_MAIN++NIL_MG_R60 | 287325.6767 | 258953.8326 | 2523.25 | 2128.8333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
S>DVTX_NIL_DVTX | 285999.5094 | 0 | 23.25 | 0 | Out= One Davenport 275/132kV TX O/S, avoid O/L of remaining Davenport 132/275kV TX on NIL trip. | NIL | Thermal | SA
F_QNV++MG_R6 | 285237.4785 | 120.7411 | 126.6667 | 0.41667 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_I+NIL_MG_R60 | 281862.7419 | 218474.6851 | 6295.5 | 6098 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL | FCAS | FCAS
Q_NIL_STRGTH_SMSF | 278438.2312 | 152.9288 | 368.8333 | 0.16667 | Out = Nil, limit Sun Metal SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
V_MURRAWRWF_FLT_15 | 272491.7435 | 27267.3713 | 21.6667 | 37.4167 | Limit Murra Warra Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
Q_NIL_STRGTH_HAMSF | 271893.3255 | 0 | 22.3333 | 0 | Out = Nil, limit Hamilton SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
Q^^NIL_QNI_SRAR | 271555.5405 | 338816.6768 | 397.3333 | 800.5833 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Voltage Stability | Qld
S>V_NIL_NIL_RBNW | 271091.9958 | 894161.8111 | 284.6667 | 330.8333 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL | Thermal | SA
F_NQ+MG_R6 | 265561.7008 | 0 | 6.9167 | 0 | Raise 6 sec Service Requirement for separated NSW and Qld Generation Event | Outage | FCAS | FCAS
F_NQ+MG_R5 | 261871.8926 | 0 | 6.9167 | 0 | Raise 5 min Service Requirement for separated NSW and Qld Generation Event | Outage | FCAS | FCAS
N>>N_DPYC_99D_C_1 | 261362.3313 | 0 | 27.6667 | 0 | Out= Darlington Point to Yanco (99D) 132kV line.X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521, avoid O/L Darlington Point to Griffith (99K) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, Feedback | Outage | Thermal | NSW
Q:NIL_OAKEY2SF | 256814.6374 | 70202.6565 | 51.1667 | 41.9167 | Limit Oakey 2 solar farm to 0MW when Oakey GT is online to prevent transient instability for 3 phase fault at Tangkam | NIL | Transient Stability | Qld
V^^N_NIL_1 | 255990.578 | 96626.9711 | 585.4167 | 150.75 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Voltage Stability | Vic
F_S+PPT_R60 | 254806.4823 | 116.16 | 92.6667 | 2.9167 | Raise 60 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage | FCAS | FCAS
T::T_NIL_1 | 251799.7281 | 0 | 315.75 | 0 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Swamp if less than 3 synchronous West Coast units generating or Farrell 220kV bus coupler open or Hampshire 110kV line is closed. | NIL | Transient Stability | Tas
Q_STR_211383_10RGBSF | 249733.5183 | 0 | 53.25 | 0 | Limit Rugby Run SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
N_FINLYSF1_ZERO | 247664.3383 | 129062.464 | 3.75 | 4.6667 | Finley solar farm upper limit of 0 MW and all inverters disconnected. | Outage | Unit Zero | NSW
S^DVBG_SA_NTH | 247401.9834 | 0 | 20.1667 | 0 | Out = Davenport-Bungama 275kV line, Manage voltage collapse in northern SA for the trip of Robertstown-Mokota 275kV line. | Outage | Voltage Stability | SA
SA_ISLE_STRENGTH_LB | 244442.6488 | 21055.9345 | 41.5833 | 4.6667 | Maximum limit (0 MW) for Lake Bonney and Canunda Wind Farm for system strength requirements when SA is at risk of separation or when islanded. | Outage | System Strength | SA
NQ_VST_ISLE_A | 243420.5961 | 0 | 4.5833 | 0 | Separation between Vic and NSW, allow Vic-NSW to supply Wagga or Northern Victoria | Outage | Region Separation | NSW
V_KARADSF_FLT_45 | 242712.5147 | 290377.5484 | 22.3333 | 163.5833 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
SVML_ZERO | 241588.716 | 356708.3815 | 407.9167 | 141.75 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | SA
Q_STR_211383_10CLRSF | 241084.7886 | 0 | 18.5 | 0 | Limit Clare SF 80% If Stan>=2+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=8+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),swamp out if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad)>=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Zero otherwise | Outage | System Strength | Qld
F_S+TG_R6_150 | 237284.7868 | 0 | 198 | 0 | Raise 6 sec Service Requirement for a 150 MW SA Generation Event | Outage | FCAS | FCAS
V_GANWRSF_FLT_25 | 237159.1028 | 899364.8397 | 18.9167 | 231.6667 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_COLEASF1_FLT_30 | 234521.5836 | 0 | 18.6667 | 0 | Limit Coleambally solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_NIL_STRGTH_WHTSF | 231843.4766 | 0 | 21.9167 | 0 | Out = Nil, limit Whitsunday SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
F_S+MLMO_TL_L60 | 230539.8934 | 0 | 191.8333 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage | FCAS | FCAS
N_LIMOSF1_FLT_50 | 227155.0556 | 0 | 18.0833 | 0 | Limit Limondale 1 solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_21138_RGBSF50 | 224556.1049 | 0 | 36.8333 | 0 | Limit Rugby Run SF to 50% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
V_CWWF_FLT_0 | 219256.2057 | 0 | 17.5833 | 0 | Limit Crowlands Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_ESTN+MG_R5 | 217797.7296 | 127.11 | 405.4167 | 4.8333 | Raise 5 min Service Requirement for Eastern Generation Event | Outage | FCAS | FCAS
SA_ISLE_STRENGTH_BU | 217567.6826 | 1528.8189 | 17.6667 | 0.25 | Maximum limit (130 MW) for Bungala Solar Farm for system strength requirements when SA is at risk of separation or when islanded. | Outage | System Strength | SA
F_Q++MUTW_L6 | 214541.5296 | 0 | 1164.3333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
Q_NIL_STRGTH_RRSF | 212261.983 | 0 | 17.4167 | 0 | Out = Nil, limit Ross River SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
N_MBTE1_B | 205699.9648 | 334940.1455 | 119.5 | 475.75 | Out= one Directlink cable, Qld to NSW limit | Outage | Unit Zero | NSW
F_S_HPRG_RREG | 205493.9969 | 0 | 28.9167 | 0 | Out= NIL, Hornsdale Battery (Generation Component) RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q>NIL_SRMB_M020/1 | 204342.0903 | 176401.4941 | 17.3333 | 14.1667 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Thermal | Qld
F_S+SNS_TG_R6_1 | 192642.5063 | 25400.9143 | 63.9167 | 2.8333 | Raise 6 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line, Segment1 | Outage | FCAS | FCAS
SA_HYSE1 | 190327.8983 | 7920.981 | 76 | 2.9167 | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage | Region Separation | SA
I_QNI_ONE_PHASE_N-2 | 186847.9176 | 23900.1975 | 18.5833 | 33.9167 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage | Discretionary | Other
F_S++TIB4_R6_1 | 184788.0834 | 5682.2461 | 5.25 | 0.66667 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA, Segment 1 | Outage | FCAS | FCAS
Q>CPWO2_CPWU_CPWO1 | 181741.4265 | 0 | 40 | 0 | Out= Calliope River to Woolooga (814) line, avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (813) line, Feedback | Outage | Thermal | Qld
V_T_NIL_FCSPS | 180901.095 | 592891.9397 | 345.5 | 966.25 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Other | Vic
SA-GEN_RAMP_ZERO | 180054.4297 | 0 | 6.5833 | 0 | Ramp a number of SA scheduled/semi-scheduled generation to 0 MW and hold at zero when SA operational demand <=700 MW; Refer to TOA 397 | Outage | Unit Zero | SA
N_FINLYSF_FLT_30 | 177455.0468 | 0 | 14.4167 | 0 | Limit Finley solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_QNV+DYN_RREG | 177065.8396 | 0 | 171.5 | 0 | Qld, NSW and Vic Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | Outage | FCAS | FCAS
N::V_UTYS_2 | 173535.0758 | 0 | 20.75 | 0 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
S_WIMK_270 | 171590.9162 | 46482.0717 | 14.1667 | 3.6667 | Out =Willalo-Mokota 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF <= 270 MW | Outage | Discretionary | SA
V_WEMENSF_FLT_44 | 170743.4524 | 254537.5348 | 13.6667 | 97.25 | Limit Wemen Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | NIL | System Strength | Vic
Q_STR_32392_HASF | 169995.763 | 0 | 13.8333 | 0 | Limit Haughton SF to 75% of Max capacity if Stan>=3+CalB+C>=2+Glad>=3+ (Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise | Outage | System Strength | Qld
V_MTMERCER_ZERO | 167778.1325 | 1193661.6379 | 13.25 | 89.0833 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Unit Zero | Vic
Q_SMCSF1_ZERO | 164984.0697 | 0 | 153.25 | 0 | Sun Metals solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
NSA_Q_BARCALDN | 163305.5047 | 594049.7646 | 13.4167 | 40.0833 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Network Support | Qld
F_T++RREG_0050 | 163153.0447 | 98631.6362 | 1051.0833 | 535.3333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
Q_STR_211383_HAMSF80 | 162975.7047 | 0 | 13.3333 | 0 | Limit Hamilton SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
Q>EMBW_NIL_EMLV_DS | 162810.9239 | 102517.7769 | 16.9167 | 12.5 | Out= 6056 or 6011 Emerald - Comet - Blackwater 66kV line ,limit Emerald SF to 40MW avoid overloading on Emerald - Lilyvale 66kV line, swap if Emerald CBs S612 or S610 or Blackwater CB S605 is closed (DS only) | NIL | Thermal | Qld
S-DLBAT-L_0 | 161700 | 129.6855 | 0.91667 | 0.25 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW | Outage | Unit Zero | SA
V_YW_134_580 | 161476.3755 | 0 | 226.5833 | 0 | Upper limits of 580 MW on Yallourn units 1, 3 and 4 | Outage | Discretionary | Vic
N>>N-NIL_94T_947 | 159354.0133 | 0 | 129.6667 | 0 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | NIL | Thermal | NSW
Q_STR_211383_RGBSF80 | 157963.1491 | 0 | 15.5 | 0 | Limit Rugby Run SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
Q_STR_211383_RRSF80 | 157814.8429 | 0 | 12.9167 | 0 | Limit Ross River SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
F_S+TL_L60_0150 | 156570.118 | 0 | 74.6667 | 0 | Lower 60 sec Service Requirement for a 150 MW SA Network (Load) Event | Outage | FCAS | FCAS
Q_NIL_STRGTH_COLSF | 153290.1235 | 0 | 29.25 | 0 | Out = Nil, limit Collinsville SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
Q_STR_211383_DAYSF80 | 151547.0075 | 0 | 12.4167 | 0 | Limit Daydream SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
F_S+SNS_TG_R5 | 150000.2036 | 311.5798 | 65.75 | 0.66667 | Raise 5 min Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage | FCAS | FCAS
N_TARALGAWF_ZERO | 149161.839 | 26657.5946 | 11.9167 | 2 | Taralga WF upper limit of 0 MW | Outage | Unit Zero | NSW
S-WIWF_0 | 148828.8665 | 13286.6854 | 11 | 1.4167 | Discretionary upper limit for Willogolechi WF generation of 0 MW | Outage | Unit Zero | SA
F_S+LREG_0035 | 146457.6329 | 865.15 | 9.5833 | 0.083333 | SA Lower Regulation FCAS Requirement greater than 35 MW | Outage | FCAS | FCAS
F_ESTN+MG_R6 | 144066.0532 | 2473.2229 | 391.4167 | 4.8333 | Raise 6 sec Service Requirement for Eastern Generation Event | Outage | FCAS | FCAS
N>N-FLML_9R4 | 141890.0206 | 49802.609 | 11.3333 | 4 | Out= Finley to Mulwala (9R4) or Mulwala to Corowa(997/2) or Corowa to Albury (997/1), avoid O/L Coleambally to Darlington Point 132kV line (99T) on Nil trip, Feedback | Outage | Thermal | NSW
S>NIL_BWMP_HUWT | 141851.1296 | 140837.5144 | 10.6667 | 8.5 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
Q_STR_211383_WHTSF80 | 141759.8707 | 0 | 12.0833 | 0 | Limit Whitsunday SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
Q_STR_311393_MEWF | 140627.0545 | 0 | 12.1667 | 0 | Limit Mt Emerald SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
S_SECB_LG-2 | 133879.6817 | 199273.7355 | 10.4167 | 13.8333 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 2 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | Thermal | SA
V_OWF_TGTSNRBHTN_30 | 131563.512 | 795516.0394 | 10.6667 | 65.5833 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Discretionary | Vic
SV_420_DYN | 129504.5916 | 0 | 121.9167 | 0 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
Q_STR_21138_KIDSF80 | 129392.0263 | 0 | 10.5 | 0 | Limit Kidston SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
V_KIATA_ISL_0 | 127954.3821 | 270806.3781 | 82.9167 | 127.9167 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
F_NQ+MG_R60 | 127495.9303 | 0 | 6.9167 | 0 | Raise 60 sec Service Requirement for separated NSW and Qld Generation Event | Outage | FCAS | FCAS
N_SILVRWF_FLT_45_MAX | 125087.3295 | 0 | 9.9167 | 0 | Limit Silverton wind farm upper limit to 45 MW with one of the following solar farms generating: Broken Hill, Limondale 1, Limondale 2, Sunraysia, Darlington Pt, Finley SF. Swamp out if all these solar farms are off. | Outage | System Strength | NSW
F_S+SNS_TG_R60 | 123985.3943 | 25.64 | 66.3333 | 0.58333 | Raise 60 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage | FCAS | FCAS
N::N_BYCR_UTYS_2 | 123043.7879 | 0 | 15.5 | 0 | Out = Upper Tumut -Yass(2) and Bannaby to Crookwell(61) , stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
N^^V_NIL_1 | 122981.9435 | 2543881.3387 | 535.5 | 2105 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | Voltage Stability | NSW
F_S++ML_R5 | 120346.1244 | 0 | 77.0833 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA | Outage | FCAS | FCAS
V>V_NIL_7 | 120087.1616 | 219018.9261 | 1.5833 | 10 | Out = NIL, prevent overload of either MBTS-DDTS 220 kV line (flow north) for trip of the EPS-TTS 220 kV line, feedback. | NIL | Thermal | Vic
Q_STR_211383_COLSF80 | 117915.2015 | 0 | 11.9167 | 0 | Limit Collinsville SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
F_S+RREG_0035 | 116991.0386 | 246.4974 | 3.4167 | 0.33333 | SA Raise Regulation FCAS Requirement greater than 35 MW | Outage | FCAS | FCAS
T_GRANVH_ZERO | 116937.8323 | 0 | 11.1667 | 0 | Granville Harbour wind farm upper limit of 0 MW | Outage | Unit Zero | Tas
S>BRDV_BWPA_RHBR | 115582.0142 | 0 | 9.6667 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V_BULGWF_ISL_0 | 113000.7063 | 0 | 9.0833 | 0 | Bulgana Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
N_BKHSF_40INV | 111942.928 | 19590.0798 | 8.75 | 1.4167 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 40. Constraint swamp out otherwise. DS only | NIL | System Strength | NSW
SA_ISLE_STRENGTH | 111118.7289 | 158914.6217 | 8.9167 | 15.8333 | Maximum limit (1300 MW) for SA non-synchronous generation for system strength requirements when SA is at risk of separation or when islanded. | Outage | System Strength | SA
SA_ISLE_LBB_HIGH_SOC | 110079.652 | 0 | 20.3333 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Lake Bonney battery of 2 MW, except when state of charge is above 70% | Outage | Other | SA
V_NUMURKAH_ZERO | 108070.1121 | 0 | 8.5 | 0 | Numurkah Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
N_SILVERTWF_FLT_100 | 107240.7091 | 0 | 8.75 | 0 | Limit Silverton Wind Farm upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
V^^SML_NSWRB_2 | 106937.2868 | 240622.3496 | 50.8333 | 59.1667 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Voltage Stability | Vic
F_T+LREG_0050 | 106371.2263 | 353986.6038 | 210 | 1198.25 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N_BROKENHSF_FLT_30 | 104967.0834 | 550601.6203 | 8.6667 | 43.5833 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
VN_ZERO | 104851.7525 | 0 | 0.83333 | 0 | VIC to NSW upper transfer limit of zero MW | Outage | Interconnector Zero | Vic
Q_STR_211383_HAYSF80 | 104780.4851 | 0 | 8.5833 | 0 | Limit Hayman SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
N_X_MBTE2_A & N_X_MBTE2_B | 104762.4241 | 148266.3023 | 797.9167 | 212 | Out= two Directlink cables, NSW to Qld limit | Outage | Unit Zero | NSW
N_URANQ12_ZERO | 102900 | 0 | 0.58333 | 0 | Uranquinty unit 2 upper limit of 0 MW | Outage | Unit Zero | NSW
N_URANQ14_ZERO | 102900 | 0 | 0.58333 | 0 | Uranquinty unit 4 upper limit of 0 MW | Outage | Unit Zero | NSW
Q_NQ_SEMI_ZERO | 101291.299 | 0 | 8.25 | 0 | Limit all North Qld semi-scheduled generators to zero | Outage | Unit Zero | Qld
V_KARSF_12INV | 101092.7759 | 58515.0626 | 11.9167 | 17.25 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out otherwise. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
V::V_1900 | 99171.4782 | 507500 | 1.1667 | 2.9167 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Oscillatory Stability | Vic
F_T+RREG_0050 | 97839.1294 | 390284.4628 | 208.75 | 1145.6667 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_Q++MUTW_R6 | 97289.4127 | 0 | 57.5 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
Q_STR_211383_KIDSF80 | 97086.8731 | 0 | 7.9167 | 0 | Limit Kidston SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3. Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
Q>>NIL_CLWU_RGLC | 96119.0275 | 0 | 23.6667 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL | Thermal | Qld
Q_STR_311393_DAYSF | 95818.6937 | 0 | 7.75 | 0 | No upper limit to Daydream SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
V>V_NIL_8 | 95189.681 | 5548.4967 | 66.4167 | 4.3333 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
Q>>NIL_BCCP_RGLC | 95029.0468 | 0 | 23.5 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
Q_STR_311393_10HASF | 93063.397 | 0 | 7.6667 | 0 | Limit Haughton to 20%of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad)>=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG),50%if Stan>=3+CalB+C>=3+Glad>=3+(Stan+Cal+Glad)>=10+Kar>=3+Bar>=1,NQLD>650&670(AVG),Ross_FN>350&370(AVG),0 otherwise. | Outage | System Strength | Qld
S>NIL_SGBN_SGSE-T2 | 92231.959 | 99915.109 | 28 | 30.9167 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | Thermal | SA
V_GANWRSF_FLT_30 | 91742.4469 | 0 | 7.4167 | 0 | Limit Gannawarra solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_V_APD01_R6 | 87147.0587 | 98258.797 | 385.3333 | 598.25 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_Q++NIL_R6 | 85795.21 | 0 | 0.66667 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 6 sec requirement for loss of a NSW 750 MW unit | NIL | FCAS | FCAS
F_T+NIL_MG_RECL_R60 | 85186.7881 | 173964.476 | 854.4167 | 1711.25 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_Q++MUTW_L5 | 83455.227 | 0 | 312.4167 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 83284.3995 | 19520.3924 | 138.75 | 93.3333 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | Voltage Stability | NSW
N_BKHSF_40INV | 82510.5348 | 19590.0798 | 6.4167 | 1.4167 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 40. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
F_Q++NIL_R60 | 82467.3731 | 0 | 2.5 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL | FCAS | FCAS
N_GUNNING1_ZERO | 81647.386 | 166425.3591 | 6.4167 | 12.75 | Gunning unit upper limit of 0 MW | Outage | Unit Zero | NSW
V_KIATAWF_FLT_0 | 81313.1321 | 474476.6365 | 45.3333 | 271.1667 | Limit Kiata Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
F_I+NIL_MG_R5 | 81104.8282 | 201396.0639 | 7270.4167 | 6846.1667 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL | FCAS | FCAS
V_WEMENSF_5INV | 80031.066 | 0 | 6.3333 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 5. Constraint swamp out if number of inverter available not exceed 5. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
S:V_XPAVC_310 | 79847.3845 | 0 | 26.9167 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
F_T+NIL_WF_TG_R60 | 79765.1627 | 137687.9406 | 891.5833 | 1345.75 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N>>N_DPYC_99D_C_2 | 79748.2112 | 0 | 8.75 | 0 | Out= Darlington Point to Yanco (99D) 132kV line.X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521, avoid O/L Griffith to Yanco (99J) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, Feedback | Outage | Thermal | NSW
V>>V_NIL_3 | 79421.3301 | 788396.9359 | 1.0833 | 8.0833 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL | Thermal | Vic
Q_STR_NQ275_MEWF_25 | 78198.2299 | 0 | 6.25 | 0 | Out = One of the 275 kV feeders North of Calvale and Calliope, limit Mt Emerald WF to 25 % capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=2 +Bar>=1. Zero otherwise | Outage | System Strength | Qld
Q>CPWO_BI_INTACT | 77186.3934 | 0 | 15 | 0 | Out= 813 or 814,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, Feedback | Outage | Thermal | Qld
QNI_SOUTH_1150_DYN | 77156.8643 | 1873.1913 | 7.8333 | 2.5833 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL | Transient Stability | Qld
F_T++NIL_MG_RECL_R5 | 76671.9861 | 50776.277 | 125.0833 | 194.8333 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
SVML_ROC_80 | 75917.6914 | 92916.3038 | 71.9167 | 27.8333 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | SA
F_QNV++MG_R60 | 75827.2817 | 3149.0278 | 164.3333 | 3.6667 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
Q_NIL_STRGTH_DAYSF | 74784.8962 | 0 | 6.0833 | 0 | Out = Nil, limit Daydream SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
V^^N_HWSM_1 | 74584.8587 | 0 | 155.1667 | 0 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_STR_333104_SMSF25 | 74125.6718 | 0 | 79.4167 | 0 | Limit Sun Metals SF to 25 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | System Strength | Qld
N_URANQ13_ZERO | 73500 | 0 | 0.41667 | 0 | Uranquinty unit 3 upper limit of 0 MW | Outage | Unit Zero | NSW
F_V_APD01_R60 | 73403.6422 | 114404.9163 | 385.3333 | 598.6667 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T+NIL_MG_R60 | 72842.1198 | 29230.2554 | 847.5 | 855.25 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>>BGBW_TWPA_TPRS | 72658.0577 | 0 | 4.5833 | 0 | Out= Bungama - Blyth West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West- Para 275kV line, Feedback | Outage | Thermal | SA
S_SECB_LG-1 | 71254.832 | 20836.8819 | 5.6667 | 1.5 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | Thermal | SA
Q>>WOSP_WOPW_WOGP_2 | 71217.2671 | 77099.056 | 6.0833 | 2.75 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Thermal | Qld
SA_ISLE_HPR_LOW_SOC | 70178.1121 | 0 | 5.5 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Hornsdale battery of 2 MW, except when state of charge is below 30% | Outage | Other | SA
F_ESTN+MG_R60 | 70171.3164 | 700.616 | 366.9167 | 4.8333 | Raise 60 sec Service Requirement for Eastern Generation Event | Outage | FCAS | FCAS
F_MAIN++APD_TL_L60 | 70164.9076 | 3926.5747 | 2754.1667 | 2078 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
Q_CS_1850 | 69993.6855 | 1377378.7018 | 9.3333 | 212.9167 | Qld Central to Qld South upper transfer limit of 1850MW (discretionary) | Outage | Discretionary | Qld
Q_STR_311393_10MEWF | 69352.3077 | 0 | 5.6667 | 0 | Limit Mt Emerald to 20% if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad)>=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG),65%if Stan>=3+CalB+C>=3+Glad>=3+(Stan+Cal+Glad)>=10+Kar>=3+Bar>=1,NQLD>650&670(AVG),Ross_FN>350&370(AVG),0 otherwise. | Outage | System Strength | Qld
V_ARARATWF_ISL_0 | 68416.0808 | 22337.3374 | 30.3333 | 7.3333 | Limit Ararat Wind Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
N_COLEASF1_FLT_45 | 68366.0172 | 0 | 5.4167 | 0 | Limit Coleambally solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_X_MBTE_3A & N_X_MBTE_3B | 67542.3813 | 24983.0281 | 796.0833 | 172.4167 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | Unit Zero | NSW
F_ESTN+LREG_0210 | 67449.7534 | 1696.6658 | 389.5833 | 4.8333 | Eastern Lower Regulation Requirement greater than 210 MW | Outage | FCAS | FCAS
Q_STR_21138_CLRSF80 | 66505.5705 | 0 | 5.4167 | 0 | Limit Clare SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
Q_STR_311310_KIDSF | 66489.9054 | 0 | 5.8333 | 0 | No limit to Kidston SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
Q_STR_NQ275_HASF_25 | 66041.6501 | 0 | 5.3333 | 0 | Out = One of the 275 kV feeders North of Calvale and Calliope, limit Haughton SF to 25 % capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=2 +Bar>=1. Zero otherwise | Outage | System Strength | Qld
F_MAIN+NIL_DYN_LREG | 65383.6088 | 129647.1208 | 313.8333 | 328.8333 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL | FCAS | FCAS
V_MURRAWRWF_30WT | 65272.2507 | 20643.3149 | 6.0833 | 4.1667 | Limit Murra Warra Wind Farm upper limit to 0 MW if number of turbine ON exceed 30. Constraint swamp out if number of turbine ON not exceed 30. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
N^^V_DDSM1 | 63452.0056 | 22188.5309 | 74 | 34.3333 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | Voltage Stability | NSW
V_BANNERTSF_FLT_44 | 63304.8606 | 154575.839 | 5.0833 | 12.25 | Limit Bannerton Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | NIL | System Strength | Vic
F_S_LBBL1_LREG | 63160.3967 | 0 | 13.3333 | 0 | Out= NIL, Lake Bonney Battery (Load Component) LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q_STR_311310_CLRSF | 62604.8065 | 0 | 5.0833 | 0 | No limit to Clare SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
V_KIAMSF_FLT_40 | 62448.9258 | 0 | 6.25 | 0 | Limit Kiamal solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_MAIN+NIL_MG_R6 | 62312.1137 | 253671.0696 | 207.5 | 1199.6667 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
Q_STR_311310_DAYSF | 61919.4182 | 0 | 5 | 0 | No limit to Daydream SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 60907.9478 | 172627.6603 | 155.3333 | 230.75 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Transient Stability | Qld
DSNAP_V::S_NIL_MAXG1 | 60188.6671 | 0 | 0.66667 | 0 | DATASNAP NEVER TO BIND 10000 swamp; TESTING Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Transient Stability | SA
F_S_LBBL1_RREG | 60025.4402 | 0 | 35.5833 | 0 | Out= NIL, Lake Bonney Battery (Load Component) RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N::N_MNYS_2 | 59516.8436 | 0 | 2 | 0 | Out= Marulan-Yass (4 or 5), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | Transient Stability | NSW
Q_STR_311310_RRSF | 59452.3798 | 0 | 4.8333 | 0 | No limit to Ross River SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
N_NIL_TE_B | 58800 | 3382.5411 | 0.33333 | 15.0833 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | Other | NSW
Q:NIL_CS | 58462.8238 | 75571.0837 | 16 | 57.75 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW) | NIL | Transient Stability | Qld
N::N-X_MNYS_CNLT_2 | 58395.8602 | 0 | 3.5833 | 0 | Out= Marulan-Yass (4 or 5) and Canberra to Lower Tumut (07) or Upper Tumut (01) 330kV line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | Transient Stability | NSW
Q_STR_311310_HAMSF | 58146.6701 | 0 | 4.8333 | 0 | No limit to Hamilton SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
SA_ISLE_LBB_LOW_SOC | 57802.3042 | 0 | 11.1667 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Lake Bonney battery of 2 MW, except when state of charge is below 30% | Outage | Other | SA
Q_STR_311310_HAYSF | 55765.4586 | 0 | 4.6667 | 0 | No limit to Hayman SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
V>>V_NIL_18 | 55657.2206 | 0 | 35.6667 | 0 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
T_MRWF_QLIM_xx | 55606.9362 | 433109.7214 | 14.8333 | 30.9167 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Transient Stability | Tas
Q_STR_211383_CLRSF80 | 55218.245 | 0 | 4.5 | 0 | Limit Clare SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8, Kareeya>=3.Zero otherwise. Strathmore need to be OS. | Outage | System Strength | Qld
VSML_ROC_80 | 54043.0925 | 8611.0013 | 77.6667 | 28.5833 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | Vic
S_WATERLWF_RB | 53120.5966 | 100126.2333 | 6.3333 | 10.9167 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | Discretionary | SA
S>HUWT_BGTX_RHBR-T | 50969.3059 | 0 | 4.1667 | 0 | Out= Hummocks-Waterloo 132kV line, avoid O/L Redhill-Brinkworth T 132kV line on trip of Bungama 132/275kV TX, Feedback | Outage | Thermal | SA
Q_STR_333104_HASF70 | 49876.1978 | 0 | 4.0833 | 0 | Limit Haughton SF to 70 % capacity if Stan>=3+Cal>=3+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=4. Zero otherwise | Outage | System Strength | Qld
NV_0500 | 49740.7174 | 0 | 4.5833 | 0 | Discretionary NSW to Vic transfer upper limit of 500 MW | Outage | Discretionary | NSW
F_S++ML_L6_1 | 48468.0569 | 0 | 23 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 1 | Outage | FCAS | FCAS
F_S+MLMO_TL_L6_2 | 48102.0841 | 0 | 17.8333 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage | FCAS | FCAS
F_I+NIL_APD_TL_L60 | 46915.127 | 5347.0009 | 6570.9167 | 5905.1667 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
F_I+NIL_APD_TL_L5 | 46460.1323 | 16438.5076 | 7260.8333 | 6641.8333 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
S-LGAPWF1_0 | 44868.7948 | 0 | 2.9167 | 0 | Discretionary upper limit for Lincoln Gap Wind Farm of 0 MW | Outage | Unit Zero | SA
S-BUPV2_0 | 44868.7715 | 0 | 2.9167 | 0 | Discretionary upper limit for Bungala Stage 2 PV generation of 0 MW | Outage | Unit Zero | SA
S-BUPV1_0 | 44868.7712 | 30849.9068 | 2.9167 | 2.25 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | Unit Zero | SA
S_HDWF1_0 | 44868.7528 | 1063.2513 | 2.9167 | 0.083333 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
S-TBSF1_0 | 44868.7435 | 0 | 2.9167 | 0 | Discretionary upper limit for Tailem Bend (Coorong) Solar PV of 0 MW | Outage | Unit Zero | SA
NSA_V_BDL0xxx | 44685.5682 | 88242.7499 | 4.0833 | 3.5833 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Network Support | Vic
Q:N_NIL_OSC | 44100 | 0 | 0.25 | 0 | Out= Nil, QNI oscillatory stability limit of 1200 MW, limit reduced to 950 MW when any one SEQ SVC POD is out, limit is reduced to 853 MW when all three SEQ SVCs or PODs out. | NIL | Oscillatory Stability | Qld
Q_STR_21138_CMSF50 | 42326.5395 | 0 | 3.4167 | 0 | Limit Clermont SF to 50% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
F_T+COGT_TL_L6 | 42028.9627 | 0 | 5.5833 | 0 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+MG_R6 | 41964.0973 | 0 | 3.4167 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S_SECB_LG3 | 41819.2997 | 37181.6688 | 4.0833 | 2.6667 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | Thermal | SA
S>>NIL_RBTX_RBTX_1 | 41696.1705 | 0 | 5.3333 | 0 | Out= Nil, avoid O/L of one Robertstown 275/132kV TX on trip of other Robertstown 275/132kV TX, Feedback | NIL | Thermal | SA
F_ESTN+RREG_0220 | 41297.4164 | 2922.2523 | 243 | 4.5833 | Eastern Raise Regulation Requirement greater than 220 MW | Outage | FCAS | FCAS
N^^V_NIL_YW134_N-2 | 40963.9216 | 0 | 127.8333 | 0 | Out = Nil, avoid voltage collapse at Southern NSW for loss of Yallourn units 1, 3 and 4 when declared credible and are the largest contingency | NIL | Voltage Stability | NSW
S>X_DV-BR-PA_08 | 40719.0372 | 89176.8855 | 3.5833 | 6.25 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line, avoid O/L Hummocks-Waterloo 132kV lineon trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V_BANSF_22INV | 40445.2358 | 229987.8699 | 3.25 | 17.9167 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 22. Constraint swamp out if number of inverter available not exceed 22. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
V_ARARATWF_FLT_0 | 39979.3609 | 84613.4693 | 15.75 | 28.5833 | Limit Ararat Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_MAIN++LREG_0210 | 39614.393 | 17706.0574 | 647.5 | 181.1667 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
Q_STR_311310_WHTSF | 39600.8521 | 0 | 3.8333 | 0 | No limit to Whitsundays SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
V_WEMENSF_21INV | 38954.5615 | 3505.1512 | 3.0833 | 1 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 21. Constraint swamp out if number of inverter available not exceed 21. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
V_GANNSF_12INV | 38581.9719 | 11730.7768 | 3.0833 | 3 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out if number of inverter available not exceed 12. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
Q>NIL_YLMR | 38419.1447 | 0 | 63.5833 | 0 | Out= Nil, avoid overload on 110kV feeders between Yarranlea and Middle Ridge(733/1 and 734/1), Feedback | NIL | Thermal | Qld
T_T_FASH_7_N-2 | 38409.7639 | 20965.4193 | 6.6667 | 7.8333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation <= 110% of West Coast load | Outage | Other | Tas
T_MRWF_ZERO | 37830.0485 | 118190.6664 | 9.3333 | 8.6667 | Discretionary 0 MW upper limit on Musselroe Wind Farm | Outage | Unit Zero | Tas
F_QNV++MG_R5 | 36651.8054 | 49.6798 | 92.4167 | 1.25 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S-SNWWF_0 | 36317.2963 | 81857.4785 | 8.0833 | 6.25 | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | Unit Zero | SA
V_OWF_NRB_0 | 35715.7971 | 129875.9871 | 2.8333 | 9.6667 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Discretionary | Vic
NSA_Q_GSTONE34_xxx | 35227.5143 | 1361.0764 | 91.75 | 12.75 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Network Support | Qld
F_MAIN++APD_TL_L5 | 34682.9157 | 14563.731 | 2276.5833 | 2428.1667 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
S_AG_0 | 34323.937 | 0 | 2.5 | 0 | Discretionary upper limit for Angaston generation | Outage | Unit Zero | SA
S_PTSTAN_0 | 33920.7398 | 0 | 2.1667 | 0 | Discretionary upper limit for Port Stanvac generation | Outage | Unit Zero | SA
S_LONSD_0 | 33920.7349 | 0 | 2.1667 | 0 | Discretionary upper limit for Lonsdale generation | Outage | Unit Zero | SA
Q_STR_211383_RGBSF50 | 33479.4575 | 0 | 6.9167 | 0 | Limit Rugby Run SF to 50% capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8+Kar>=3. Zero otherwise | Outage | System Strength | Qld
N>N-NIL_LSDU | 33152.8373 | 2590.1799 | 101.9167 | 26.9167 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
N^N-LS_SVC | 32389.6039 | 2230.9698 | 638.5833 | 21.8333 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage | Voltage Stability | NSW
V_KIAMAL_ISL_0 | 31942.9404 | 0 | 2.5833 | 0 | Kiamal Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
Q_STR_311310_SMSF | 31501.8176 | 0 | 51.1667 | 0 | Limit Sun Metals SF to 25% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
V^^N_UTYS_1 | 31492.4201 | 0 | 76.75 | 0 | Out = Upper Tumut to Yass (2) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
F_T+NIL_ML_L6 | 31356.0764 | 9591.2301 | 184.5833 | 1199 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_MWWF_GFT1_115 | 31102.7311 | 0 | 2.3333 | 0 | Out= Murra Warra WF associated fast tripping scheme 1 (disabled), Limit Murra Warra Windfarm upper limit to 115 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Discretionary | Vic
Q_STR_21138_COLSF80 | 31025.6599 | 0 | 5.6667 | 0 | Limit Collinsville SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
S-HDWF2_0 | 30879.0196 | 0 | 2 | 0 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
V_GANNSF_10INV | 30582.9139 | 0 | 2.4167 | 0 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 10. Constraint swamp out if number of inverter available not exceed 10. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
N::N_SDUT_2 | 30306.3614 | 0 | 0.5 | 0 | Out = Upper Tumut -Stockdill(1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
N_FINLYSF_FLT_50 | 30247.7761 | 0 | 2.4167 | 0 | Limit Finley solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>>V_NIL_7 | 29810.3113 | 0 | 17.9167 | 0 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
F_T++NIL_MG_RECL_R6 | 29772.7638 | 70472.7016 | 66.75 | 215.8333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_S+NIL_HPR_G+L_LREG | 29635.63 | 14 | 0.25 | 0.083333 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS LowerReg ramping constraint | NIL | FCAS | FCAS
S_HDWF3_0 | 29578.0254 | 0 | 1.9167 | 0 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
F_Q+KC_R5 | 29400 | 0 | 0.16667 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Kogan Creek) | Outage | FCAS | FCAS
F_S+PPT_R6_2 | 29400 | 0 | 0.16667 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 2 | Outage | FCAS | FCAS
T_FAJB | 29400 | 0 | 0.16667 | 0 | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
S^DVBR_SA_NTH | 29260.6418 | 13297.3609 | 2.3333 | 1.8333 | Out = Davenport-Brinkworth 275kV line, Manage voltage collapse in northern SA for the trip of Davenport-Belalie 275kV line | Outage | Voltage Stability | SA
F_Q+ML_L60_0400 | 29200 | 0 | 0.16667 | 0 | Lower 60 sec Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS | FCAS
F_Q+ML_L5_0400 | 29000 | 0 | 0.16667 | 0 | Lower 5 min Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS | FCAS
V_GANNSF_11INV | 28735.4535 | 1655.5837 | 2.25 | 0.83333 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
SVML_095 | 28635.6466 | 0 | 38.5833 | 0 | SA to Vic on ML upper transfer limit of 95 MW | Outage | Discretionary | SA
V^V_NIL_ARWBBA | 28610.7315 | 0 | 17.25 | 0 | Out = Nil, limit NW Vic generation to 600 MW to avoid voltage collapse on trip of Ararat to Waubra to Ballarat 220 kV line | NIL | Voltage Stability | Vic
QNTE_ROC | 28587.4203 | 2611.0712 | 29.9167 | 13.5 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | Qld
N_COLEASF1_FLT_50 | 28121.8494 | 0 | 2.25 | 0 | Limit Coleambally solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_V_YWPS3_R6 | 27974.0992 | 0 | 39.1667 | 0 | Out= NIL, Yallourn W3 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>Q-MUTW_2 | 27883.0186 | 0 | 0.75 | 0 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage | Thermal | NSW
V::N_HWSM_xxx | 27739.8146 | 36734.1849 | 125 | 82.75 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_WEMENSF_ZERO | 27545.8527 | 27358.9677 | 2.1667 | 11.3333 | Wemen Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
S>>NIL_BWMP_BRTW | 26753.5643 | 0 | 3.1667 | 0 | Out= Nil, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
F_I+NIL_APD_TL_L6 | 26597.9656 | 0 | 1980.8333 | 0 | Lower 6 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
Q_DAYDSF1_ZERO | 26202.2941 | 0 | 2.5833 | 0 | Daydream solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_S++ML_L5 | 26137.7007 | 0 | 8.3333 | 0 | Lower 5 min Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage | FCAS | FCAS
S_HPRG1_E | 26071.5732 | 335197.7915 | 2.9167 | 8.6667 | Out= Nil, Hornsdale Battery generation energy target <= 30 MW | NIL | Other | SA
Q_STR_311310_COLSF | 26044.7547 | 0 | 5.0833 | 0 | No limit to Collinsville SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
N_BROKENHSF_FLT_26 | 25333.3544 | 1429240.3057 | 24.8333 | 127.8333 | Limit Broken Hill Solar Farm upper limit to 26 MW to manage post contingent voltage oscillation | NIL | System Strength | NSW
T_T_FASH_2_N-2 | 25241.4764 | 0 | 5.8333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh >= 90% of West Coast load | Outage | Other | Tas
N_NYNGANSF_010 | 25158.67 | 0 | 2 | 0 | Nyngan Solar Farm upper limit of 10 MW | Outage | Discretionary | NSW
VTBL_ROC | 24961.5429 | 6267.8093 | 9 | 8.9167 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Vic
S:V_550_HY_TEST_DYN | 24622.7428 | 172.0877 | 32.3333 | 0.25 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
F_S++ML_R60 | 24495.2283 | 0 | 27.1667 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA | Outage | FCAS | FCAS
S>>RBTX2_RBTX1_WEWT | 24423.3362 | 0 | 4.9167 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage | Thermal | SA
Q>ISTX | 24264.6405 | 0 | 1.9167 | 0 | Out = Isis T2 132/66 kV transformer, limit Childers Solar Farm to 46MW to prevent overload on remaining transformer | Outage | Thermal | Qld
Q_STR_211383_9_WHTSF | 24171.1287 | 0 | 1.9167 | 0 | Limit Whitsunday SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
F_Q++LDTW_L6 | 24166.0029 | 0 | 108.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
N_FINLEYSF_49_INV | 23992.5648 | 25433.54 | 1.9167 | 2 | Limit Finley Solar Farm upper limit to 0 MW if number of inverter available exceed 49. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
F_T++NIL_MG_R5 | 23670.4258 | 4554.2575 | 97.25 | 47.5833 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
S_DVRB2_270 | 23610.6569 | 305778.8316 | 5.4167 | 70.0833 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
F_T+NIL_MG_R5 | 23488.4663 | 92721.6834 | 1149.25 | 822.5 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
Q_STR_211383_9_RGBSF | 23158.4512 | 0 | 1.8333 | 0 | Limit Rugby Run SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_HAMSF | 23131.143 | 0 | 1.8333 | 0 | Limit Hamilton SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_RRSF | 23111.8209 | 0 | 1.8333 | 0 | Limit Ross River SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_COLSF | 23089.1972 | 0 | 1.8333 | 0 | Limit Collinsville SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_DAYSF | 23080.1003 | 0 | 1.8333 | 0 | Limit Daydream SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
S:VS_PA_SVC_570 | 23061.8302 | 0 | 31.3333 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage | Oscillatory Stability | SA
F_MAIN+NIL_MG_R60 | 23004.9927 | 232547.9869 | 202.5 | 1199.6667 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_MAIN+LREG_0210 | 22939.5099 | 244273.7961 | 195.6667 | 676.9167 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_Q++ARTW_L6 | 22397.3135 | 31023.7601 | 69.25 | 20.0833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
V_BANSF_5INV | 22176.9395 | 0 | 1.75 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 5. Constraint swamp out if number of inverter available not exceed 5. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
Q_STR_211383_9_HAYSF | 22052.2146 | 0 | 1.75 | 0 | Limit Hayman SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
F_MAIN++APD_TL_L6 | 21830.0835 | 0 | 984.9167 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
TVBL_ROC | 21609.9672 | 7280.3198 | 16.1667 | 9.8333 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Tas
S>RBTX1_RBTX2_WEMWP4 | 21557.8944 | 0 | 31.8333 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-MWP4 132kV line on trip of Robertstown 275/132kV TX2, | Outage | Thermal | SA
F_Q++ARTW_L60 | 21087.2181 | 19225.7743 | 72.1667 | 20.0833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
V_MWWF_115 | 20539.0055 | 0 | 1.5833 | 0 | Murra Warra Wind Farm upper limit of 115 MW | Outage | Islanding - Unit | Vic
F_I+ML_L6_0400 | 20534.1186 | 1819.5434 | 4191.0833 | 3775.75 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
F_TASCAP_LREG_0210 | 20119.1861 | 32160.6183 | 321.5 | 342 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS | FCAS
Q_STR_311393_RRSF | 19638.6731 | 0 | 1.5833 | 0 | No upper limit to Ross River SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
S>RB_275KV_N_BUS_1 | 19592.4362 | 4628.2799 | 13.8333 | 5.75 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | Thermal | SA
S:VS_700_HY_TEST_DYN | 19317.3071 | 0 | 4.3333 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
F_T++NIL_MG_R6 | 19271.9152 | 7452.9412 | 34.5833 | 21.25 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
T_LIPM1_SLOAD_1_N-2 | 18916.7465 | 5180.1089 | 9.5 | 10.75 | Out=Liapootah-Waddamana-Palmerston #1 220kV line and associated 220kV CBs at Waddamana I/S, loss of #2 parallel 220 kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Thermal | Tas
N_BODWF1_ZERO | 18772.7231 | 3271.4009 | 1.5 | 0.25 | Bodangora wind farm upper limit of 0 MW and all turbines disconnected | Outage | Unit Zero | NSW
F_S++MOPS1_R5 | 18613.5724 | 0 | 15.9167 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Mortlake 1 is the largest generation risk in SA (MOPS connects to SA) | Outage | FCAS | FCAS
VSML_220 | 18457.9096 | 1517.9106 | 55.75 | 3.5833 | Vic to SA on ML upper transfer limit of 220 MW | NIL | Discretionary | Vic
F_S++TIB2_R6_1 | 18359.8084 | 0 | 2.5833 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA, Segment 1 | Outage | FCAS | FCAS
N>N-NIL_MBDU | 18309.2436 | 28753.5321 | 8.4167 | 65.75 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
F_TASCAP_RREG_0220 | 18104.6907 | 28797.0184 | 249.5833 | 175.0833 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS | FCAS
V^^N_X_MNYS_CNUT_1 | 18067.4317 | 0 | 32.25 | 0 | Out = Canberra to Upper Tumut (01) and Marulan to Yass (4 or 5) 330kV lines, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N_CROOKWF2_ZERO | 17903.7049 | 0 | 1.4167 | 0 | Crookwell wind farm upper limit of 0 MW and all turbines disconnected | Outage | Unit Zero | NSW
VS_250_DYN | 17853.6237 | 0 | 13.0833 | 0 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
Q_STR_311393_KIDSF | 17587.2362 | 0 | 1.4167 | 0 | No upper limit to Kidston SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
F_NQ+RREG_0170 | 17477.8958 | 0 | 0.91667 | 0 | Separated NSW and Qld Raise Regulation Requirement greater than 170 MW | Outage | FCAS | FCAS
V_GANWR_BAT_L_FLT_0 | 17413.0058 | 0 | 7.5833 | 0 | Limit Gannawarra Battery (Load Component) upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_S+MLMO_TL_L5 | 17246.8887 | 0 | 45.75 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 5 min requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage | FCAS | FCAS
N^^V_BUDP_1 | 17122.4551 | 38102.1805 | 15.4167 | 36 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>BGTX_BGBR_HUWT | 17059.5743 | 0 | 4.0833 | 0 | Out= Bungama 275/132kV TX, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap windfarm), Feedback | Outage | Thermal | SA
T_T_TI_GH_RC12_250 | 17032.4349 | 0 | 4.1667 | 0 | Discretionary 250 MW upper limit on Tribute, Granville Harbour, Reece 1 and 2 generation | Outage | Discretionary | Tas
S>>X_RBTU+RB_SBUS_15 | 16982.1656 | 0 | 3.0833 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
V_BANSF_20INV | 16874.5664 | 7561.9134 | 1.3333 | 0.58333 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 20. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
N^^V_CNCW_1 | 16562.6901 | 18619.5632 | 19.25 | 16.3333 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V>>V_NIL_14 | 16301.8954 | 0 | 4.25 | 0 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
F_S++HYSE_L60 | 16153.8532 | 732902.7202 | 28.9167 | 433.9167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage | FCAS | FCAS
S_SNOWNTH1_ZERO | 16144.6325 | 0 | 9.3333 | 0 | Discretionary upper limit for Snowtown 2 North WF generation of 0 MW | Outage | Unit Zero | SA
V_MURRAWR_ZERO | 16005.9317 | 4384.0064 | 2.8333 | 0.33333 | Murra Warra wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
F_Q+MM2_R6 | 15984.4501 | 0 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Millmerran unit 2) | Outage | FCAS | FCAS
V_KARADSF_FLT_0 | 15815.68 | 245975.6804 | 4.1667 | 141.0833 | Limit Karadoc solar farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
F_T_LI_WY_CA_L6 | 15804.498 | 0 | 12.1667 | 0 | Out= NIL, Liapootah + Wayatinah + Catagunya L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN+RREG_0220 | 15797.6844 | 123237.0721 | 111.25 | 323.25 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S_DVRB_270 | 15648.2841 | 477046.6253 | 1.25 | 51.0833 | Out = DV-BL 275kV line Or MK-RB 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF + Hallet Hill WF (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
F_T_FISHER_L6 | 15613.8049 | 0 | 13.1667 | 0 | Out= NIL, Fisher L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N::N_CNSD_2 | 15468.6197 | 0 | 0.33333 | 0 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
F_T++FASH_N-2_TG_R60 | 15422.1425 | 93.419 | 6.3333 | 2.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_T++NIL_BLSPS_R6_1 | 15213.8905 | 0 | 0.16667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS | FCAS
T>T_GTSH_IMP_4K | 15212.995 | 4553.8742 | 37.6667 | 4.25 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
VSML_-150 | 15189.2745 | 0 | 4.5 | 0 | Vic to SA on ML upper transfer limit of -150 MW | Outage | Discretionary | Vic
T_T_MC_ZERO | 15169.6463 | 0 | 0.25 | 0 | Discretionary 0 MW upper limit on Macintosh generation | Outage | Discretionary | Tas
S>V_NWRB_RBMWP3 | 15080.9481 | 105345.3961 | 22.3333 | 9 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage | Thermal | SA
S_SNOWSTH1_ZERO | 14991.027 | 0 | 9 | 0 | Discretionary upper limit for Snowtown 2 South WF generation of 0 MW | Outage | Unit Zero | SA
F_T++LREG_0050 | 14990.5497 | 26070.6597 | 261.5 | 170.3333 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
N^^N_NIL_1 | 14945.7653 | 5933.0407 | 1 | 0.16667 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | Voltage Stability | NSW
VSML_100 | 14937.6633 | 0 | 1.75 | 0 | Vic to SA on ML upper transfer limit of 100 MW | Outage | Discretionary | Vic
F_T++GO_A752_TG_R5 | 14885.5284 | 0 | 0.25 | 0 | Out= Gordon CB A752, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_S++ML_R6_1 | 14776.2029 | 0 | 79.4167 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA, Segment 1 | Outage | FCAS | FCAS
NRM_VIC1_NSW1 | 14726.8185 | 286368.6673 | 0.16667 | 10.6667 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue | Negative Residue
F_Q+KC_R6 | 14700 | 0 | 0.083333 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Kogan Creek) | Outage | FCAS | FCAS
F_Q+MG_R6 | 14700 | 0 | 0.083333 | 0 | Raise 6 sec Service Requirement for Qld Generation Event | Outage | FCAS | FCAS
T_FAMA | 14700 | 0 | 0.083333 | 0 | Out=Farrell-Mackintosh 110KV line. Energy <= 0MW | Outage | Unit Zero | Tas
V>>V_NIL_1A | 14700 | 81413.6117 | 0.083333 | 0.5 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Thermal | Vic
S>WT-BUS_MNWT_SNBG-T | 14497.4113 | 0 | 1.1667 | 0 | Out= Waterloo 132kV South bus outage (this offloads TX 5), avoid O/L Snowtown-Bungama 132kV line on trip of Mintaro-Waterloo 132kV line (this offloads Hummocks-Waterloo 132kV line), Feedback | Outage | Thermal | SA
SA_ISLE_DAL_HIGH_SOC | 14391.8099 | 0 | 0.25 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Dalrymple battery of 2 MW, except when state of charge is above 70% | Outage | Other | SA
V_SV_MLMO_NETT | 14334.6565 | 153677.9979 | 4.1667 | 105.4167 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW. Swamp out when MOPS/DUNDWF not generating | Outage | FCAS | Vic
Q_STR_311393_COLSF | 14299.308 | 0 | 1.3333 | 0 | No upper limit to Collinsville SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
F_Q++LDTW_L60 | 14140.7366 | 0 | 104.6667 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
V_KIATAWF_FLT_15 | 14138.9855 | 74138.9107 | 7.4167 | 45.1667 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
T_GO_ZERO | 13875.5003 | 0 | 1.0833 | 0 | Discretionary 0 MW upper limit on total Gordon generation | Outage | Unit Zero | Tas
V_BANSF_20INV | 13838.8829 | 7561.9134 | 1.0833 | 0.58333 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 20. Constraint swamp out otherwise. DS only | NIL | System Strength | Vic
V_KARSF_19INV | 13678.63 | 5748.7892 | 1.0833 | 2.3333 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
N_SILVERWF_MAX | 13663.4642 | 3656611.4042 | 1.0833 | 267.0833 | Limit MW output of Silverton wind farm to not exceed 131 MW with Broken Hill solar generating | Outage | Discretionary | NSW
F_MAIN++NIL_MG_R5 | 13607.1409 | 27215.4973 | 1207.75 | 1121.75 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
N_GOONSF_9_INV | 13383.0513 | 0 | 1 | 0 | Limit Goonumbla Solar Farm upper limit to 0 MW if number of inverter available exceed 9. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
Q_HAMISF1_ZERO | 13302.6454 | 8614.1114 | 1.0833 | 2.0833 | Hamilton solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_T+NIL_MG_RECL_R5 | 13214.3086 | 63312.5873 | 742.0833 | 1506 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_QNV++ML_L6_0400 | 13021.3882 | 0 | 150.6667 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage | FCAS | FCAS
T^V_NIL_9 | 12738.8686 | 10599.887 | 36.3333 | 21.25 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Voltage Stability | Tas
V_GANWRSF_FLT_0 | 12660.0193 | 389691.807 | 1 | 166.5833 | Limit Gannawarra solar farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q^^NIL_CS | 12654.4734 | 0 | 1.5833 | 0 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation | NIL | Voltage Stability | Qld
V_KARADSF_FLT_45 | 12489.5331 | 290377.5484 | 9.1667 | 163.5833 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | NIL | System Strength | Vic
N>N-NIL_9R4_9R3 | 12404.2385 | 0 | 1 | 0 | Out= Nil, avoid O/L Finley to Mulwala 132kV line (9R4) trip of Finley to Deniliquin (9R3) line, Feedback | NIL | Thermal | NSW
T_T_FASH_1_N-2 | 12388.188 | 8048.555 | 13.1667 | 3.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Other | Tas
I_CTRL_ISSUE_ML | 12218.2672 | 1087.0519 | 16.8333 | 8.6667 | DC Link Control Issue Constraint for Murraylink | Outage | Other | Other
V_T_NIL_BL1 | 12215.5044 | 27621.4212 | 13.0833 | 61.3333 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL | Other | Vic
Q_HASMME_RAMP_ZERO | 12145.1249 | 21553.9997 | 1.0833 | 1.75 | Ramp Haughton, Sun Metals and Mt Emerald generators to zero and hold at zero. | Outage | Unit Zero | Qld
F_S++TIB3_R5 | 11963.894 | 0 | 3.4167 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA | Outage | FCAS | FCAS
S>VMLMHNW1 | 11842.9345 | 139616.8993 | 22.0833 | 76.9167 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | SA
N_WRWSF_055 | 11754.1035 | 13388.9248 | 16.6667 | 12.1667 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | Other | NSW
T_T_FASH_8_N-2 | 11711.2915 | 191.7601 | 3.75 | 0.083333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation >= 90% of West Coast load | Outage | Other | Tas
SVML^NIL_160 | 11646.0568 | 0 | 52.1667 | 0 | Out=NIL, SA to Vic on ML upper transfer limit of 160 MW to manage voltage collapse at Monash | NIL | Discretionary | SA
S>>RBTX2_NIL_RBTX1 | 11575.4343 | 0 | 11.0833 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Robertstown 275/132kV TX1 on Nil trip, Feedback | NIL | Thermal | SA
Q_CHILDSF1_ZERO | 11345.3732 | 0 | 0.91667 | 0 | Childers Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
Q_STR_21138_RRSF80 | 11318.6195 | 0 | 0.91667 | 0 | Limit Ross River SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
Q_NIL_STRGTH_HAYSF | 11164.4507 | 0 | 0.91667 | 0 | Out = Nil, limit Hayman SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
F_S+APD_TL_L60 | 11047.3755 | 0 | 0.5 | 0 | Lower 60 sec requirement in SA for loss of both APD potlines, Separation between Heywood (HYTS) and Moorabool (MLTS) | Outage | FCAS | FCAS
F_T++NIL_MG_RECL_R60 | 10931.8988 | 5564.0619 | 84.5 | 104.9167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_MAIN++ML_L6_0400 | 10739.0038 | 2554.0684 | 781.3333 | 1385.4167 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_ESTN+ML_L6_0400 | 10619.741 | 4.4 | 359.75 | 4.8333 | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS | FCAS
V_YENDONWF_ZERO | 10530.1933 | 0 | 10.4167 | 0 | Yendon Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V_KIAMSF_FLT_50 | 10463.4639 | 0 | 0.83333 | 0 | Limit Kiamal solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_WHITSF1_ZERO | 10334.2767 | 2070.0582 | 0.83333 | 2.0833 | Whitsunday solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_T+NIL_WF_TG_R5 | 10182.252 | 101872.1492 | 1076.0833 | 1315 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_GANWR_BAT_L_ISL_0 | 10127.3729 | 209.7165 | 26.9167 | 0.16667 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
F_S++TIB4_R60 | 10118.935 | 0 | 2.25 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA | Outage | FCAS | FCAS
Q>N-MUTE_757 | 10089.3386 | 0 | 56.5 | 0 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
F_MAIN++RREG_0220 | 10002.1351 | 14314.5077 | 151.1667 | 74.0833 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_S++ML_L60 | 9615.1288 | 0 | 2.25 | 0 | Lower 60 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage | FCAS | FCAS
N>>N-NIL_DPTX_2 | 9490.8491 | 1427.6925 | 4.6667 | 0.5 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | Thermal | NSW
F_T++NIL_MG_R60 | 9374.539 | 1252.8539 | 59.75 | 20 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
T^^V_GTSH_1 | 9330.3675 | 2152.5937 | 18.5 | 2.75 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Voltage Stability | Tas
V_GANWR_SF_BAT_50 | 9286.8834 | 894670.4805 | 6.1667 | 16.8333 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Discretionary | Vic
Q_STR_21138_HAMSF80 | 9171.4105 | 0 | 0.75 | 0 | Limit Hamilton SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
F_T++NIL_WF_TG_R6 | 8980.4142 | 14166.7623 | 24.4167 | 60.1667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_V++MOPS_R60 | 8668.8034 | 0 | 0.41667 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Mortlake Station is the largest generation risk in SA (MOPS connects to SA) | Outage | FCAS | FCAS
F_Q++BCDM_L6 | 8586.9572 | 43574.9958 | 44.75 | 142.75 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
N_FINLEYSF_6_INV | 8460.0748 | 0 | 0.66667 | 0 | Limit Finley Solar Farm upper limit to 0 MW if number of inverter available exceed 6. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
VSML_080 | 8425.531 | 0 | 3.6667 | 0 | Vic to SA on ML upper transfer limit of 80 MW | Outage | Discretionary | Vic
V::N_NIL_xxx | 8418.7299 | 4302.9745 | 37.9167 | 16.8333 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL | Transient Stability | Vic
V::N_BYPASS_HW_SY_xxx | 8414.0544 | 1354.6816 | 27.9167 | 3.0833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Transient Stability | Vic
Q_STR_211383_9_KIDSF | 8384.1814 | 0 | 0.66667 | 0 | Limit Kidston SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_311393_RGBSF | 8309.7638 | 0 | 0.66667 | 0 | No upper limit to Rugby Run SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_311393_HAMSF | 8309.7625 | 0 | 0.66667 | 0 | No upper limit to Hamilton SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_311393_CLRSF | 8262.532 | 0 | 0.66667 | 0 | No upper limit to Clare SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),Zero otherwise. . | Outage | System Strength | Qld
F_V_APD01_R5 | 8150.1193 | 14935.1152 | 385.3333 | 591.3333 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q_STR_311310_RGBSF | 8137.5376 | 0 | 1.75 | 0 | No limit to Rugby Run SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=10,NQLD>650&670(AVG),Ross_FN>350&370(AVG), Zero otherwise | Outage | System Strength | Qld
N>>N-NIL_DPTX | 8077.4937 | 0 | 0.083333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL | Thermal | NSW
F_S++TIB1_R5 | 8039.6205 | 0 | 3.6667 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 1 is the largest generation risk in SA | Outage | FCAS | FCAS
SVML_FLT_125 | 8010.4479 | 0 | 3.9167 | 0 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
F_MAIN+APD_TL_L60 | 7993.458 | 2679.4472 | 203.9167 | 1141.4167 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T+NIL_ML_L60 | 7925.1109 | 3680.0316 | 184.6667 | 1198.75 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_I+GFT_TG_R60 | 7774.985 | 0 | 162.9167 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
CA_BRIS_4D2AAD32_1 | 7608.5679 | 0 | 15.8333 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG MVPB on trip of DDTS-SMTS1 &DDTS-SMTS2 330KV LINES. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
F_QNV+DYN_LREG | 7580.0064 | 0 | 27.0833 | 0 | Qld, NSW and Vic Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | Outage | FCAS | FCAS
N>>N-PKWL_94K_1 | 7521.6193 | 0 | 11 | 0 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Forbes to Cowra (998) line, Feedback | Outage | Thermal | NSW
N^^V_DDWG | 7476.1559 | 5917.9992 | 10.6667 | 5.9167 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_311393_SMSF | 7475.5864 | 0 | 12.5833 | 0 | Limit Sun Metals SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
V_WEMENSF_19INV | 7378.3986 | 2060.4898 | 0.58333 | 0.91667 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
Q_STR_311393_WHTSF | 7272.3767 | 0 | 0.58333 | 0 | No upper limit to Whitsunday SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
F_VST+LREG_0160 | 7222.2889 | 0 | 6.9167 | 0 | Vic, SA and Tas Lower Regulation Requirement greater than 160 MW | Outage | FCAS | FCAS
F_T+CSGO_TG_R6_2 | 7185.0159 | 0 | 3.5 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS | FCAS
V_WEMENSF_19INV | 7064.6174 | 2060.4898 | 0.58333 | 0.91667 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | NIL | System Strength | Vic
V^^N_MNYS_1 | 6940.7366 | 0 | 20.6667 | 0 | Out = Marulan to Yass (4 or 5) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_BGWF_GFT_5 | 6847.1934 | 0 | 0.5 | 0 | Out= Bulgana WF associated fast tripping scheme (disabled), Limit Bulgana Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Discretionary | Vic
V_CWWF_GFT_5 | 6847.1924 | 245464.9989 | 0.5 | 18.5833 | Out= Crowlands WF associated fast tripping scheme (disabled), Limit Crowlands Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Discretionary | Vic
N^^V_NIL_ARWBBA | 6670.1638 | 0 | 39.6667 | 0 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL | Voltage Stability | NSW
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 6560.873 | 10224.5985 | 47.0833 | 36.5833 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Thermal | Vic
Q^^NIL_TR_CLHA | 6474.6263 | 0 | 0.5 | 0 | Out = Nil, Tarong voltage stability limit, Calvale-Halys contingency equation | NIL | Voltage Stability | Qld
T::T_NIL_3 | 6461.3917 | 9100.5075 | 20.4167 | 14.1667 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Transient Stability | Tas
VN_0450 | 6374.6919 | 0 | 12.0833 | 0 | Discretionary Vic to NSW transfer upper limit of 450 MW | Outage | Discretionary | Vic
V_WEMENSF_8INV | 6367.0838 | 0 | 0.5 | 0 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 8. Constraint swamp out otherwise. DS only | NIL | System Strength | Vic
Q_STR_311393_HAYSF | 6234.9321 | 0 | 0.5 | 0 | No upper limit to Hayman SF if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=9, Kareeya>=3NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
NQTE_ROC | 6220.5569 | 2598.3537 | 37.5 | 12.0833 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | NSW
F_Q++BCDM_L60 | 5972.6219 | 17764.8235 | 43.75 | 136.6667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
V_ARARAT_ZERO | 5968.9011 | 9930.8959 | 2.1667 | 3.1667 | Ararat Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
F_T++COGT_TL_L60 | 5891.9207 | 1.0039 | 44.3333 | 1.1667 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS | FCAS
V>>N-NIL_HA | 5729.3207 | 36418.491 | 18.1667 | 60.5 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Thermal | Vic
T_SHWI | 5652.9745 | 0 | 16 | 0 | Out-Sheffield-Wilmot 220KV line | Outage | Unit Zero | Tas
S>NIL_LKDV_CNRB | 5647.7679 | 76608.3841 | 0.58333 | 4.0833 | Out= NIL, avoid O/L Canowi-Robertstown 275kV on trip of Mt Lock-Davenport 275kV line, Feedback | NIL | Thermal | SA
V_KIATA_ZERO | 5626.2137 | 0 | 2.4167 | 0 | Kiata Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
F_S++TIB4_R5 | 5606.8248 | 0 | 4.4167 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA | Outage | FCAS | FCAS
F_S_LBBG1_LREG | 5574.1159 | 0 | 5.9167 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_VST+MG_R6 | 5539.8504 | 0 | 6.9167 | 0 | Raise 6 sec requirement for a Vic, SA and Tas Generation Event | Outage | FCAS | FCAS
F_T++COGT_TL_L6 | 5378.0784 | 12.3297 | 50.5 | 2.6667 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS | FCAS
S:V_550_HY_TEST | 5275.2791 | 27683.5912 | 19.75 | 0.5 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
V_GANNSF_11INV | 5275.0668 | 1655.5837 | 0.41667 | 0.83333 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Constraint swamp out otherwise. DS only | NIL | System Strength | Vic
CA_BRIS_4DE6DCA9_1 | 5257.4615 | 0 | 1.8333 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
F_T++NIL_ML_L6 | 5233.5314 | 1047.2038 | 221.75 | 241.75 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
S^DVMK_SA_NTH | 5227.1701 | 0 | 0.5 | 0 | Out = ONLY one line segment between Davenport-Belalie-Willalo-Mokota 275kV line, manage voltage collapse in northern SA for the trip of Robertstown-Canowie 275kV line. | Outage | Voltage Stability | SA
VSML_ZERO | 5224.9884 | 7964.3382 | 23.8333 | 26 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | Vic
V_KARSF_8INV | 5181.5624 | 5804.1163 | 0.41667 | 3.3333 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 8. Constraint swamp out if number of inverter available not exceed 8. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
F_MAIN++ML_L6_APD_LD | 5160.3279 | 1.26 | 173.8333 | 0.58333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage | FCAS | FCAS
V::N_MLTX_xxx | 5133.7855 | 0 | 22.6667 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_Q++LDTW_L5 | 5112.5677 | 0 | 31.3333 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
S>>BGTX_TWPA_TPRS | 5053.9147 | 0 | 0.58333 | 0 | Out= Bungana 275/132kV TX, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
F_Q++ARTW_L5 | 4856.9003 | 6808.3032 | 20.1667 | 16.4167 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
F_VST+RREG_0170 | 4845.6809 | 0 | 5.5833 | 0 | Vic, SA and Tas Raise Regulation Requirement greater than 170 MW | Outage | FCAS | FCAS
V::N_ESTN_MLMOHG_V | 4709.5486 | 0 | 17.9167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage | Transient Stability | Vic
N^^Q_NIL_A | 4656.9044 | 10777.3842 | 8.8333 | 24.75 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | Voltage Stability | NSW
F_VS++TL_L6_0600 | 4591.4434 | 0 | 2.3333 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V^^N_ESTN_MLMOHG_1 | 4504.2107 | 0 | 11.8333 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, avoid voltage collapse around Murray for loss of Basslink when Basslink exporting > 400MW to TAS, will swamp otherwise. | Outage | Voltage Stability | Vic
T>>T_NIL_BL_EXP_7C | 4488.0013 | 3848.5279 | 3.9167 | 11.0833 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
F_VS++APD_TL_L6 | 4462.1244 | 0 | 2.1667 | 0 | Lower 6 sec requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_V_YWPS4_R6 | 4432.2347 | 0 | 7.8333 | 0 | Out= NIL, Yallourn W4 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N^^Q_ARTW_B1 | 4242.5741 | 0 | 17.3333 | 0 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | Voltage Stability | NSW
V_MWWF_5 | 4193.3236 | 44138.227 | 0.33333 | 3.3333 | Murra Warra Wind Farm upper limit of 5 MW | Outage | Islanding - Unit | Vic
S>NIL_BWMP_RHBR-T | 4181.1827 | 0 | 0.33333 | 0 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
S^NIL_PL_MAX | 4163.4155 | 120722.2791 | 0.33333 | 2.75 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | Voltage Stability | SA
N_BKHSF_44INV | 4153.32 | 307464.4715 | 0.33333 | 22.1667 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 44. Constraint swamp out if number of inverter available not exceed 44. This is to manage voltage oscillation. DS only | Outage | System Strength | NSW
F_T++NIL_WF_TG_R5 | 4052.4066 | 8258.6123 | 64 | 94.1667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_S+APD_TL_L6 | 4000.32 | 0 | 0.5 | 0 | Lower 6 sec requirement in SA for loss of both APD potlines, Separation between Heywood (HYTS) and Moorabool (MLTS) | Outage | FCAS | FCAS
SA-GEN_030 | 3987.0215 | 0 | 0.25 | 0 | Discretionary 30 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | Discretionary | SA
VN_0900 | 3977.6579 | 0 | 8.3333 | 0 | Discretionary Vic to NSW transfer upper limit of 900 MW | Outage | Discretionary | Vic
V:S_600_HY_TEST_DYN | 3972.7477 | 15553.9445 | 23.25 | 20 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Oscillatory Stability | Vic
Q_STR_NQ275_SMSF_25 | 3905.6633 | 0 | 4.9167 | 0 | Out = One of the 275 kV feeders North of Calvale and Calliope, limit Sun Metals SF to 25 % capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Kar>=2 +Bar>=1. Zero otherwise | Outage | System Strength | Qld
V_S_HEYWOOD_UFLS | 3891.0423 | 0 | 7.8333 | 0 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC.Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL | Other | Vic
F_S+NIL_HPR_G+L_RREG | 3889.0325 | 0 | 0.33333 | 0 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS RaiseReg ramping constraint | NIL | FCAS | FCAS
VN_0500_DYN | 3846.9405 | 0 | 6.6667 | 0 | VIC to NSW interconnector upper transfer limit of 500 MW, dynamic headroom, DS formulation only. | Outage | Discretionary | Vic
SA-GEN_120 | 3761.729 | 0 | 0.25 | 0 | Discretionary 120 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | Discretionary | SA
F_S+RREG_0070 | 3745.1935 | 0 | 1.4167 | 0 | SA Raise Regulation Requirement greater than 70 MW | Other | FCAS | FCAS
F_MAIN+APD_TL_L5 | 3722.0793 | 7631.4908 | 204.8333 | 1162.5833 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V^SML_HORC_2 | 3659.7464 | 231.9672 | 1 | 9.3333 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage | Voltage Stability | Vic
S>>DVBG_RBTU_WEWT | 3658.1763 | 0 | 3 | 0 | Out= Davenport-Bungama 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
T^V_NIL_8 | 3643.6053 | 2819.4858 | 12.8333 | 6.5 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Voltage Stability | Tas
SA-GEN_090 | 3624.9903 | 0 | 0.25 | 0 | Discretionary 90 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | Discretionary | SA
F_QNV+MG_R60 | 3611.5991 | 0 | 3.4167 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
T>T_NIL_BL_110_4 | 3608.1804 | 31404.0446 | 3.3333 | 40.0833 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Thermal | Tas
V::N_EPMB_xxx | 3607.1259 | 540.6151 | 21.1667 | 0.66667 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_Q+TNT_R6 | 3540.4406 | 0 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Tarong North) | Outage | FCAS | FCAS
F_Q+CC4_R6 | 3526.7092 | 0 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Callide C unit 4) | Outage | FCAS | FCAS
T::T_HA_GT_PM_4 | 3476.7421 | 42057.2059 | 4.5 | 5.4167 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Transient Stability | Tas
SVML_120 | 3429.0829 | 0 | 0.83333 | 0 | SA to Vic on ML upper transfer limit of 120 MW | Outage | Discretionary | SA
N_LIMOSF11_ZERO | 3375.9093 | 0 | 0.33333 | 0 | Limondale 1 solar farm upper limit of 0 MW and all inverters disconnected. | Outage | Unit Zero | NSW
F_T++COGT_TL_L5 | 3294.741 | 0.43 | 39.9167 | 0.41667 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS | FCAS
S>>CGTB1_TUTB_MOTB | 3203.3772 | 0 | 9.6667 | 0 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
V^SML_BUDP_3 | 3181.9122 | 8444.5031 | 28.8333 | 43.25 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
S:VS_700_HY_TEST | 3172.9339 | 0 | 1.5833 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
F_MAIN++GFT_TG_R60 | 3150.6353 | 0 | 22.9167 | 0 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
S>>BRBG_BGTX_HUWT | 3083.6517 | 0 | 0.25 | 0 | Out= Brinkworth to Redhill to Bungama 132kV lines (this takes out Clements Gap WF), avoid O/L Hummocks to Waterloo 132kV on trip of Bungama 132/275kV TX2, Feedback | Outage | Thermal | SA
Q_STR_21138_DAYSF80 | 3072.8562 | 0 | 0.25 | 0 | Limit Daydream SF to 80% of Max capacity if Stan>=2+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=8. Zero otherwise | Outage | System Strength | Qld
F_T++CSGO_TG_R6 | 3057.1809 | 333.6329 | 6.8333 | 0.083333 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
Q>>NIL_LCCP_BCCP | 3040.884 | 0 | 0.5 | 0 | Out= Nil, avoid O/L Bouldercombe to Calliope River (812) on trip of Larcom Creek to Calliope River (8859) line, Feedback | NIL | Thermal | Qld
N>N-ARCH_87_TE_C1 | 3037.5939 | 0 | 1.5833 | 0 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage | Thermal | NSW
F_VS++MG_R60 | 3034.8865 | 0 | 3.25 | 0 | Raise 60 sec requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_VST+MG_R60 | 2882.9244 | 0 | 6.9167 | 0 | Raise 60 sec requirement for a Vic, SA and Tas Generation Event | Outage | FCAS | FCAS
F_Q++8C_L60 | 2879.4176 | 1201.6739 | 10.1667 | 3.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
S>>NIL_BWMP_TWPA | 2858.0007 | 1426.5189 | 1.1667 | 0.83333 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
S:VS_XPAVC_460 | 2820.539 | 0 | 4.4167 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood and Murraylink combined upper transfer limit of 460 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
VN_0900_DYN | 2781.9398 | 0 | 3.75 | 0 | VIC to NSW interconnector upper transfer limit of 900 MW, dynamic headroom, DS formulation only. | Outage | Discretionary | Vic
V_ELAINEWF_ZERO | 2772.2353 | 0 | 3.3333 | 0 | Elaine Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
F_T+CSGO_TG_R6_1 | 2757.0265 | 3061.3649 | 4.25 | 4.25 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS | FCAS
F_Q++8E_L6 | 2726.4541 | 0 | 14.5833 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
T>T_PMSH_IMP_4F | 2681.2327 | 0 | 4.3333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V_ARWF_FSTTRP_5 | 2650.1933 | 460.3213 | 0.83333 | 0.16667 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Discretionary | Vic
N^^Q_MUTW_1_B1 | 2637.3234 | 0 | 3.75 | 0 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage | Voltage Stability | NSW
VN_0500 | 2627.6022 | 0 | 10.5 | 0 | Discretionary Vic to NSW transfer upper limit of 500 MW | Outage | Discretionary | Vic
F_T+CSGO_TG_R60 | 2621.7915 | 837.3767 | 5.5 | 6 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>V_NIL_NIL_RBMW3 | 2620.0579 | 0 | 3.25 | 0 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL | Thermal | SA
F_Q++BCDM_L5 | 2613.9893 | 17119.827 | 11.1667 | 65.4167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
F_T++FASH_N-2_TG_R6 | 2577.5665 | 2350.1411 | 4.5 | 3.3333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_MAIN+NIL_MG_R5 | 2546.359 | 47082.6254 | 201.5 | 1198.6667 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_T++NIL_WF_TG_R60 | 2544.3088 | 5699.5178 | 26.4167 | 63.8333 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
T>T_NIL_BL_3C | 2543.1134 | 4364.4829 | 7.9167 | 2.1667 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
SA-GEN_060 | 2537.01 | 0 | 0.16667 | 0 | Discretionary 60 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | Discretionary | SA
S>>RBTX1_RBTX2_WEWT | 2528.4867 | 0 | 1.3333 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage | Thermal | SA
F_T++NIL_ML_L60 | 2526.6229 | 159.7304 | 152.0833 | 271.6667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
SA-GEN_150 | 2512.7291 | 0 | 0.16667 | 0 | Discretionary 150MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | Discretionary | SA
SA-GEN_180 | 2512.729 | 0 | 0.16667 | 0 | Discretionary 180MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | Discretionary | SA
F_I+ML_L6_APD_LD | 2510.2806 | 0.08 | 378.0833 | 0.33333 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage | FCAS | FCAS
T_FARC2_2 | 2505.4993 | 0 | 2.0833 | 0 | Out=Farrell - Reece 2 220KV line. Discretionary 144 MW limit on Reece 1 + Granville Harbour WF | Outage | Discretionary | Tas
F_Q+CC3_R6 | 2492.6925 | 0 | 0.083333 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Callide C unit 3) | Outage | FCAS | FCAS
F_Q+RREG_0110 | 2456.6999 | 0 | 0.083333 | 0 | Qld Raise Regulation Requirement greater than 110 MW | Outage | FCAS | FCAS
S^BGBW_SA_NTH | 2451.7421 | 0 | 0.33333 | 0 | Out = Bungama-Blyth West 275kV line, Manage voltage collapse in northern SA for the trip of Para-Templers West 275kV line | Outage | Voltage Stability | SA
F_Q+ML_L6_0400 | 2400 | 0 | 0.16667 | 0 | Lower 6 sec Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS | FCAS
VN_0800_DYN | 2348.4347 | 0 | 4.5833 | 0 | VIC to NSW interconnector upper transfer limit of 800 MW, dynamic headroom, DS formulation only. | Outage | Discretionary | Vic
N_MBTE1_A | 2338.1567 | 3243.9341 | 29.5833 | 3.0833 | Out= one Directlink cable, NSW to Qld limit | Outage | Unit Zero | NSW
F_Q++MUTW_R5 | 2292.4965 | 0 | 6.6667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage | FCAS | FCAS
V::N_DDSM_xxx | 2284.3298 | 1389.7642 | 11.0833 | 6.75 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_MAIN+APD_TL_L6 | 2216.6918 | 0 | 95.0833 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V^^N_X_DTSS_MNYS_1 | 2209.9906 | 0 | 5.0833 | 0 | Out = Dapto to Sydney South (11) and Marulan to Yass (4 or 5) 330kV lines, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q::N_AR_CP2_AR_2L-G | 2206.8446 | 0 | 9.4167 | 0 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
S_PPT270 | 2204.3972 | 0 | 0.58333 | 0 | SA Pelican Point generation <= 270 MW | Outage | Discretionary | SA
Q_EMERASF1_ZERO | 2163.5702 | 0 | 0.16667 | 0 | Emerald Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V_S_NIL_ROCOF | 2160.6409 | 303.4329 | 11.25 | 2.5833 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | Vic
S>>X_RBTU+RB_SBUS_16 | 2130.0641 | 0 | 2.8333 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage | Thermal | SA
N_COLEASF1_FLT_0 | 2116.4904 | 0 | 0.16667 | 0 | Limit Coleambally solar farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S_BRBG_CMWF_0 | 2091.2698 | 0 | 0.16667 | 0 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | Unit Zero | SA
V_BANNERTON_ZERO | 2089.5138 | 76995.7283 | 0.16667 | 5.6667 | Bannerton Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
F_S+MLMO_TL_L6_1 | 2087.0922 | 0 | 5.5833 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage | FCAS | FCAS
Q_STR_SMHAU_HASF_40 | 2068.5872 | 1058.2084 | 0.16667 | 0.083333 | Limit Haughton SF to 50% capacity (40 inverters) If Stan >= 3 + Cal >=3 + Glad >= 3 and (Stan+Cal+Glad) >=10, Zero otherwise | Outage | System Strength | Qld
T>T_CRNN_3 | 2064.0272 | 373.9716 | 3.25 | 0.83333 | Out= Creek Rd to New Norfolk 110 kV line, avoid O/L New Norfolk to Chapel St 110 kV line for loss of Waddamana to Palmerston 110 kV line, Feedback | Outage | Thermal | Tas
F_S++TIB2_R5 | 2049.0414 | 0 | 2.4167 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA | Outage | FCAS | FCAS
VN_1100 | 2024.2849 | 0 | 5.4167 | 0 | Discretionary Vic to NSW transfer upper limit of 1100 MW | Outage | Discretionary | Vic
F_NQ+LREG_0160 | 2009.0114 | 0 | 5.5833 | 0 | Separated NSW and Qld Lower Regulation Requirement greater than 160 MW | Outage | FCAS | FCAS
N::N_UTYS_2 | 1969.4338 | 0 | 8.3333 | 0 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
V_WEMENSF_FLT_44 | 1955.5359 | 254537.5348 | 0.16667 | 97.25 | Limit Wemen Solar Farm upper limit to 44 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N^^V_SMTXF2_1 | 1952.2309 | 12984.217 | 4.1667 | 11.1667 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V:S_600_HY_TEST | 1937.1832 | 7384.0735 | 17.8333 | 20.6667 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
S>>NIL_TWPA_TPRS | 1936.0536 | 0 | 0.58333 | 0 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
F_T++CSGO_TG_R60 | 1923.0864 | 72.3653 | 9.9167 | 0.33333 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
S>>BWMP_TWPA_TPRS | 1896.5051 | 115.7733 | 0.33333 | 0.41667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
N>N-NIL_DC | 1893.1196 | 58668.1414 | 4.5 | 83.75 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL | Thermal | NSW
F_T+COGT_TL_L60 | 1888.4138 | 0 | 5.5833 | 0 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
T>T_LIPM_110_2B | 1805.1405 | 0.04 | 4.4167 | 0.083333 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Thermal | Tas
Q:N_TW330_CB5102_OSC | 1791.0194 | 0 | 6.8333 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage | Oscillatory Stability | Qld
SVML_FLT_150 | 1788.9746 | 3678.9164 | 4.4167 | 3.4167 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | SA
N>>N-NIL_01N | 1770.7656 | 0 | 1.5833 | 0 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | Thermal | NSW
S>>X_RBTU+RB_SBUS_14 | 1768.6116 | 0 | 0.33333 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
T>T_FASH_1_N-2 | 1764.5968 | 50182.0448 | 3.0833 | 6.8333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, limit Bastyan, John Butters & Mackintosh to west coast load plus Hampshire link line rating | Outage | Thermal | Tas
F_T+FASH_N-2_TG_R6_2 | 1721.2699 | 3649.5333 | 1.0833 | 4.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS | FCAS
F_MAIN+ML_L6_0400 | 1705.6228 | 1902.5578 | 102.3333 | 1019.1667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_S++MOPS2_R5 | 1703.8675 | 0 | 4 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Mortlake 2 is the largest generation risk in SA (MOPS connects to SA) | Outage | FCAS | FCAS
N>>N-PKWL_94K_3 | 1696.7991 | 0 | 2.8333 | 0 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | Outage | Thermal | NSW
F_V_YWPS3_R60 | 1661.2822 | 0 | 2.6667 | 0 | Out= NIL, Yallourn W3 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_I+GFT_TG_R5 | 1621.3049 | 0 | 165.75 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
F_VST+MG_R5 | 1611.3527 | 0 | 6.9167 | 0 | Raise 5 min requirement for a Vic, SA and Tas Generation Event | Outage | FCAS | FCAS
T_V_FCSPS_RAMP | 1599.5917 | 0 | 2.3333 | 0 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Ramping | Tas
V^SML_HORC_3 | 1584.9093 | 16868.6121 | 0.83333 | 79.0833 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
F_QNV++MLMO_L6 | 1562.8325 | 0 | 19.75 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V>EPTT | 1561.0623 | 0 | 1.5 | 0 | Outage =Eildon to Thomastown 220kV line, avoid overloading a Mt Beauty to Dederang 220kV line for trip of the parallel line | Outage | Thermal | Vic
S>>V_CGTI_PPPG_TIPA | 1559.205 | 0 | 1.5833 | 0 | Out= Cherry Gardens - Torrens Island 275kV line, avoid O/L Torrens Island - Para 275kV line on trip of Pelican Point - Parafield Gardens West 275kV line, Feedback | Outage | Thermal | SA
SVML_015 | 1551.1693 | 0 | 1.5 | 0 | SA to Vic on ML upper transfer limit of 15 MW | Outage | Discretionary | SA
VN_0800 | 1550.9097 | 0 | 3.75 | 0 | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage | Discretionary | Vic
F_Q+MM1_R6 | 1516.44 | 0 | 0.16667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage | FCAS | FCAS
SA-GEN_210 | 1512.73 | 0 | 0.16667 | 0 | Discretionary 210 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397 | Outage | Discretionary | SA
V::N_X_HWSM_HWCB_xxx | 1505.3895 | 0 | 2.9167 | 0 | Out=Hazelwood-South Morang & Hazelwood-Cranbourne 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
QNI_ISLE_B | 1478.365 | 0 | 0.16667 | 0 | Qld / Southern separation, allow QNI to supply Northern NSW Load | Outage | Region Separation | Qld
F_QNV++LREG_0210 | 1456.1621 | 0 | 25.5833 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Outage | FCAS | FCAS
VN_0650 | 1448.1059 | 0 | 0.16667 | 0 | Discretionary Vic to NSW transfer upper limit of 650 MW | Outage | Discretionary | Vic
F_Q++LDMU_L60 | 1412.2247 | 0 | 7.6667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
V>>N-JNWG_RADIAL_1 | 1402.2246 | 0 | 4.4167 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
F_I+GFT_TG_R6 | 1395.1589 | 0 | 45.1667 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
VN_1100_DYN | 1393.6091 | 0 | 2.25 | 0 | VIC to NSW interconnector upper transfer limit of 1100 MW, dynamic headroom, DS formulation only. | Outage | Discretionary | Vic
F_MAIN++NIL_BL_L60 | 1385.5073 | 181.3166 | 181.9167 | 83.6667 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
V>>V_ROTS_TX_2A_R | 1375.2015 | 0 | 10.4167 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Thermal | Vic
S>>RB_275KV_S_BUS_10 | 1357.7131 | 0 | 1.5833 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage | Thermal | SA
VN_1000_DYN | 1326.8712 | 0 | 2.5 | 0 | VIC to NSW interconnector upper transfer limit of 1000 MW, dynamic headroom, DS formulation only. | Outage | Discretionary | Vic
F_T++FARE_N-2_TG_R6 | 1307.1104 | 1193.9755 | 0.66667 | 2.8333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_T++GO_A752_TG_R6 | 1300.9744 | 0 | 0.25 | 0 | Out= Gordon CB A752, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_VS++MG_R6 | 1295.4537 | 0 | 1.5 | 0 | Raise 6 sec requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_Q++8E_L60 | 1295.4472 | 0 | 14.5833 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
F_T++CO_752_TL_L6 | 1294.6978 | 0 | 6.5833 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS | FCAS
F_I+TG_R60_1000 | 1284.327 | 0 | 6.0833 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage | FCAS | FCAS
F_VST+TL_L6_0600 | 1283.5229 | 0 | 2.3333 | 0 | Lower 6 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 600 | Outage | FCAS | FCAS
N^^V_MSDD2 | 1282.5539 | 0 | 2.1667 | 0 | Out = Dederang to Murray 330 kV line, avoid voltage collapse at Darlington Point for loss of the remaining Dederang to Murray 330 kV line | Outage | Voltage Stability | NSW
F_T++NIL_TL_L6_DS | 1248.1287 | 0 | 5.25 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
SVML_100 | 1242.3445 | 0 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 100 MW | Outage | Discretionary | SA
F_VS++TL_L6_0500 | 1211.6387 | 0 | 1.0833 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_Q+LREG_0110 | 1197.75 | 0 | 0.083333 | 0 | Qld Lower Regulation Requirement greater than 110 MW | Outage | FCAS | FCAS
V^SML_BAWB_3 | 1189.4823 | 3467.1036 | 4.5 | 33.5833 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
F_I+TG_R6_1000 | 1187.7689 | 0 | 6.0833 | 0 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage | FCAS | FCAS
Q>>CLWU_BCRG_BCCP | 1181.9043 | 2149.7973 | 0.5 | 3.4167 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
T_V_NIL_BL1 | 1178.0546 | 3858.7799 | 3.5 | 7.3333 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL | Other | Tas
VSML_VFRB_OFF | 1166.1048 | 0 | 1.25 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL | Other | Vic
F_I+MG_R6_1000 | 1142.6661 | 0 | 0.66667 | 0 | Raise 6 sec Service Requirement for a NEM Generation Event, MG = 1000 | Outage | FCAS | FCAS
Q_STR_RSTVS_SMSF_76 | 1138.4976 | 0 | 1.25 | 0 | Limit Sun metal SF to 100% of max capacity (#76 inverters) if Kareeya > = 2 and Stanwell > = 3 and Callide > = 3 and Gladstone > = 3 and total of Stanwell, Callide and Gladstone > =10. Limit to zero otherwise. | Outage | System Strength | Qld
N_SAPHWF1_ZERO | 1131.9077 | 0 | 0.66667 | 0 | Sapphire wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
T>T_NIL_110_2 | 1125.3173 | 0 | 0.083333 | 0 | Out = NIL, avoid O/L Scottsdale Tee to Norwood 110 kV line (flow to Norwood) on trip of Scottsdale to Norwood 110 kV line or 110/22 kV txfmr at Scottsdale, feedback. Swamped when Musselroe Runback Control Scheme available | NIL | Thermal | Tas
VN_1000 | 1124.51 | 0 | 2.75 | 0 | Discretionary Vic to NSW transfer upper limit of 1000 MW | Outage | Discretionary | Vic
V>>V_KTS_TX_A2_2A_R | 1109.6678 | 2598.6936 | 10.8333 | 3.75 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Thermal | Vic
Q^^N_AR_SVC_1 | 1099.0697 | 227.0083 | 8.9167 | 1.5833 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
V_VS_LB_CAN_50 | 1097.7712 | 558165.3316 | 4.75 | 47.4167 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage | System Strength | SA
N-DBWL_94J | 1093.5952 | 0 | 1 | 0 | Out = Dubbo132 to Wellington (94J) 132 kV line, Upper limit of 80 on Nevertire SF, EE advice on 13/02/2020 | Outage | Other | NSW
S>>RB_275KV_N_BUS_3 | 1087.8058 | 200.5676 | 0.66667 | 0.41667 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | Thermal | SA
V>X_NWCB6022+6023_T1 | 1086.4626 | 0 | 0.66667 | 0 | Out = North West Bend 132 kV circuit breakers CB6022 and CB6023(Note: this takes out North West Bend-Monash #2 132kV line); limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB 132/66kV TX3. | Outage | Thermal | SA
V_GANWRSF_ISL_0 | 1084.5776 | 0 | 0.083333 | 0 | Gannawarra Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
NRM_SA1_VIC1 | 1081.1813 | 0 | 0.083333 | 0 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue | Negative Residue
N_FINLYSF_FLT_SC_25 | 1052.5321 | 0 | 0.083333 | 0 | Limit Finley solar farm upper limit to 25 MW to manage post contingent voltage oscillation. If Buronga Syncon 1 is out of service, limit Finley solar farm to 0 MW | Outage | System Strength | NSW
V_WEMENSF_FLT_10 | 1049.9035 | 0 | 0.083333 | 0 | Limit Wemen Solar Farm upper limit to 10 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V:T_NIL_BL_1 | 1049.8081 | 4542.1911 | 0.75 | 6.0833 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL | Other | Vic
F_Q+CC3_R60 | 1047.7507 | 0 | 0.083333 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Callide C unit 3) | Outage | FCAS | FCAS
Q_RRSF1_ZERO | 1047.2508 | 118142.3883 | 0.083333 | 9.25 | Ross River solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S_LB2WF_CONF | 1045.4921 | 11523.677 | 1.9167 | 4.3333 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | Voltage Stability | SA
V_KARADSF_FLT_20 | 1041.9934 | 0 | 0.083333 | 0 | Limit Karadoc solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_RGBYRSF1_ZERO | 1037.5837 | 101808.623 | 0.083333 | 8 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V>SML_NWRB_NWMWP1 | 1016.2256 | 0 | 0.83333 | 0 | Out=NWB - Robertstown 132kV #1 line, limit flow on ML to avoid OL North West Bend- MWP1 132 kV line. | Outage | Thermal | SA
N_BOMENSF1_ZERO | 1010.3221 | 0 | 1.6667 | 0 | Bomen SF upper limit of 0 MW and all inverters disconnected. | Outage | Unit Zero | NSW
Q>X_CPWO1_CPWU_CPWO2 | 974.7008 | 22446.1734 | 0.16667 | 8.5 | Out= Calliope River to Woolooga (813+815) line, avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (814) line, Feedback | Outage | Thermal | Qld
S>NIL_NIL_MYSG-T | 964.9986 | 0 | 0.083333 | 0 | Out = NIL; Limit LB2 and LB3 generation to avoid OL Mayura - Snuggery T 132kV line. | NIL | Thermal | SA
F_Q++8C_L5 | 951.386 | 330.6952 | 5.1667 | 2.1667 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage | FCAS | FCAS
F_Q++8C_L6 | 931.5213 | 2382.9562 | 12.5833 | 3.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
N>>N-WGYS_OPEN_4 | 926.4258 | 0 | 0.91667 | 0 | Out = Wagga-Yass 132 kV Parallel lines Opened, avoid O/L Lower Tumut to Canberra (07) on trip of Lower Tumut to Yass (3) line, Feedback | Outage | Thermal | NSW
Q>YLMR_YLMR_1 | 925.8194 | 0 | 1.3333 | 0 | Out= one of the 110kV feeder between Yarranlea and Middle Ridge(733/1 or 734/1), avoid O/L on the remaining feeder(733/1 or 734/1), Feedback | Outage | Thermal | Qld
F_QNV+MG_R5 | 892.69 | 0 | 3.4167 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
VN_0700_DYN | 887.9224 | 0 | 1.75 | 0 | VIC to NSW interconnector upper transfer limit of 700 MW, dynamic headroom, DS formulation only. | Outage | Discretionary | Vic
Q_STR_311393_10SMSF | 885.5221 | 0 | 1.4167 | 0 | Limit Sun Metals to 20% if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad)>=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG),50%if Stan>=3+CalB+C>=3+Glad>=3+(Stan+Cal+Glad)>=10+Kar>=3+Bar>=1,NQLD>650&670(AVG),Ross_FN>350&370(AVG),0 otherwise. | Outage | System Strength | Qld
F_T_LI_WY_CA_L5 | 872.7562 | 0 | 35.25 | 0 | Out= NIL, Liapootah + Wayatinah + Catagunya L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>>N-964_DC | 871.3134 | 5153.9772 | 4.75 | 3.9167 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage | Thermal | NSW
F_T++GO_A752_TG_R60 | 850.4735 | 0 | 0.33333 | 0 | Out= Gordon CB A752, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_WESTCOAST_RREG_0 | 846.4909 | 180.2281 | 1.3333 | 2.8333 | RREG FCAS of West Coast Generation limited to 0 MW | Outage | Unit Zero - FCAS | FCAS
F_ESTN+ML_L5_0400 | 836.8421 | 4.16 | 359.8333 | 4.6667 | Lower 5 min requirement for a Eastern Load Event, ML = 400 | Outage | FCAS | FCAS
F_ESTN+ML_L60_0400 | 836.7222 | 4.52 | 339.3333 | 4.6667 | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS | FCAS
T>T_TU_MB_NN_N-2_1 | 823.3665 | 0 | 0.91667 | 0 | Out= Nil, Loss of both Tungatinah - Meadowbank - New Norfolk 110kV lines declared credible, avoid O/L Tungatinah to New Norfolk No.3 110kV line on trip of both Tungatinah to Meadowbank to New Norfolk 110kV lines plus Meadowbank generation. | Outage | Thermal | Tas
N>LSDU9U6_LSDU9U7 | 812.1808 | 7567.7643 | 14.6667 | 29 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Thermal | NSW
F_MAIN+GFT_TG_R60 | 806.2414 | 0 | 5.4167 | 0 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V^SML_ARWB_3 | 770.2245 | 2666.0865 | 6.5 | 12.0833 | Out = Ararat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
F_VST+TL_L6_0500 | 768 | 0 | 1.3333 | 0 | Lower 6 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 500 | Outage | FCAS | FCAS
NQ_VST_ISLE_B | 760.4859 | 0 | 0.91667 | 0 | Separation between Vic and NSW, allow Vic-NSW to supply Wagga or Northern Victoria | Outage | Region Separation | NSW
Q>YLTX_DS | 759.6954 | 0 | 0.91667 | 0 | Out = Nil, limit to Maryrorough Solar Farm to dynamic runback limit of Yarranlea 110/33kV transformer(s), DS formulation only | NIL | Thermal | Qld
V::N_X_HWSM_HWRO_xxx | 717.6537 | 86.926 | 1.3333 | 0.16667 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_VS++LREG_0160 | 707.0818 | 0 | 0.58333 | 0 | Vic and SA Lower Regulation Requirement greater than 160 MW, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_VS++TL_L6_0550 | 705.1793 | 0 | 0.58333 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V^^N_CNUT_1 | 682.7097 | 0 | 1 | 0 | Out = Canberra to Upper Tumut (01) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
T>T_GTSH_IMP_4F | 677.8204 | 0 | 1.3333 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 2 220 kV line (flow North) for trip of Hadspen to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
QNI_SOUTH_1050_DYN | 669.2457 | 0 | 3.25 | 0 | QLD to NSW on QNI upper transfer limit of 1050 MW, dynamic headroom, DS formulation only. | Outage | Transient Stability | Qld
F_MAIN++MG_R6_1000 | 659.7918 | 0 | 0.66667 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 1000, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V>V_NIL_6 | 652.1015 | 0 | 0.33333 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
V::N_X_ARWBBA_xxx | 646.8815 | 0 | 3.0833 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_T++CO_752_TL_L60 | 639.2429 | 0 | 6.9167 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS | FCAS
F_MAIN++YW134_MGR60 | 632.5204 | 0 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
N^N_CHLS_1 | 627.6775 | 4807.6018 | 15.6667 | 30.25 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
F_NQ+ML_L6_0400 | 616.24 | 0 | 6.9167 | 0 | Lower 6 sec Service Requirement for a NSW and Qld Load Event, ML = 400 | Outage | FCAS | FCAS
SVML_060 | 615.6034 | 0 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 60 MW | Outage | Discretionary | SA
S>>V_NIL_NIL_RBNW1 | 610.0474 | 0 | 0.91667 | 0 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL | Thermal | SA
F_T+FARE_N-2_TG_R60 | 607.3474 | 211.2251 | 1.1667 | 5.1667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
N>>N_65+66_N-2_5 | 604.7926 | 91.5693 | 1.25 | 0.5 | Out= Nil, avoid O/L Wodonga to Jindera (060) on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL | Thermal | NSW
T_ROCOF_3 | 600.8217 | 256.962 | 0.41667 | 0.58333 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | ROC Frequency | Tas
F_VS++MG_R5 | 594.9781 | 0 | 2 | 0 | Raise 5 min requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
CA_BRIS_4DE47816_1 | 586.1466 | 0 | 1.75 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
F_NQ+ML_L5_0400 | 585.8006 | 0 | 6.9167 | 0 | Lower 5 min Service Requirement for a NSW and Qld Load Event, ML = 400 | Outage | FCAS | FCAS
F_S++TIB3_R6_1 | 585.5355 | 5736.0665 | 1.25 | 1 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA, Segment 1 | Outage | FCAS | FCAS
N^^Q_BCDM_B1 | 582.8093 | 0 | 0.25 | 0 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
F_T_LI_WY_CA_L60 | 577.6003 | 0 | 14.75 | 0 | Out= NIL, Liapootah + Wayatinah + Catagunya L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T+NIL_ML_L5 | 568.1329 | 915.3407 | 91.8333 | 1150.5 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V::N_SMSC_xxx | 562.5395 | 8592.6919 | 2.0833 | 20.25 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_T+COGT_TL_L5 | 560.3025 | 0 | 5.5833 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+ML_L6_0400 | 560.17 | 0 | 2.8333 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage | FCAS | FCAS
V^SML_KGRC_4 | 557.5654 | 367.6002 | 4.1667 | 5.3333 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Voltage Stability | Vic
V>>V_BUDP_6 | 556.8132 | 2631.5839 | 0.33333 | 3.6667 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
Q::N_ARSVC_AR_2L-G | 555.3302 | 27196.7862 | 1.5833 | 5.6667 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
T^V_HA_GT_220_1 | 541.3396 | 0 | 1.4167 | 0 | Out= one George Town to Hadspen 220kV line, limit post-contingency loading on Palmerston to Sheffield 220kV line (flow to north) to avoid voltage collapse on trip of the remaining Hadspen to George Town 220kV line. | Outage | Voltage Stability | Tas
F_T+FASH_N-2_RREG | 539.7649 | 41063.7043 | 3 | 17.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | Unit Zero - FCAS | FCAS
F_QNV+LREG_0210 | 535.6572 | 0 | 2.5833 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_S++HYSE_L5 | 531.9752 | 60428.4638 | 5.0833 | 99.8333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage | FCAS | FCAS
F_V_YWPS4_R60 | 516.7652 | 0 | 0.25 | 0 | Out= NIL, Yallourn W4 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S++ML_L6_2 | 512.889 | 0 | 0.75 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 2 | Outage | FCAS | FCAS
F_Q++LDMU_L6 | 512.147 | 0 | 6.5 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
S:V_PA_SVC_270 | 503.2412 | 0 | 1.5833 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage | Oscillatory Stability | SA
F_T+FARE_N-2_TG_R6_2 | 489.9693 | 1021.2978 | 0.66667 | 1.9167 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage | FCAS | FCAS
F_ESTN++MLMO_L6 | 485.0687 | 0 | 27.5 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_VST+APD_TL_L6 | 484.3233 | 0 | 2.6667 | 0 | Lower 6 sec requirement for a Vic, SA and Tas Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS | FCAS
F_T++NIL_TL_L60_DS | 470.2215 | 0 | 4.3333 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
V^SML_BEKG_4 | 468.1939 | 0 | 7 | 0 | Out = Bendigo to Kerang 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Voltage Stability | Vic
F_V_YWPS3_RREG | 463.5806 | 0 | 1.1667 | 0 | Out= NIL, Yallourn W3 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN+ML_L6_APD_LD | 452.18 | 0 | 6.3333 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_VS++TL_L5_0600 | 437.2771 | 0 | 1.9167 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage | FCAS | FCAS
VN_0700 | 436.0279 | 0 | 1.9167 | 0 | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage | Discretionary | Vic
NSA_V_NPSD_100 | 392.1172 | 143.1131 | 0.5 | 0.33333 | Newport unit >= 100 MW for Network Support Agreement | Outage | Network Support | Vic
T>T_NIL_BL_IMP_1B | 386.0351 | 0 | 0.41667 | 0 | Out = Nil, avoid O/L either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line with no SPS action, feedback | NIL | Thermal | Tas
F_MAIN++WIP_N-2_MLL6 | 372.7743 | 17.34 | 8.75 | 9.6667 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V>>V_ARCW_7 | 368.8471 | 0 | 3.75 | 0 | Out = Ararat to Crowlands 220kV line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage | Thermal | Vic
F_V++MOPS_R5 | 368.2142 | 0 | 0.33333 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Mortlake Station is the largest generation risk in SA (MOPS connects to SA) | Outage | FCAS | FCAS
F_I+WIP_N-2_ML_L6 | 367.7801 | 6.67 | 21.1667 | 14 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 6 sec requirement | Outage | FCAS | FCAS
F_T+FARE_N-2_RREG | 366.1498 | 166.5153 | 0.41667 | 5.1667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | Unit Zero - FCAS | FCAS
F_S++HYSE_L6_1 | 362.4869 | 457495.6124 | 5.4167 | 375.8333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage | FCAS | FCAS
T>T_PMSH_IMP_4D | 360.1977 | 0 | 0.91667 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
F_VS++TL_L60_0600 | 357.6662 | 0 | 1.0833 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V_KARSF_19INV | 357.4166 | 5748.7892 | 0.25 | 2.3333 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 19. Constraint swamp out otherwise. DS only | NIL | System Strength | Vic
S>>NIL_RBTU_WEWT | 356.5552 | 15660.0357 | 0.16667 | 2.75 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
F_ESTN+TL_L6_0600 | 349.7531 | 0 | 7.3333 | 0 | Lower 6 sec Service Requirement for a Eastern Network Event, TL = 600 | Outage | FCAS | FCAS
Q:N_1078 | 347.8793 | 11802.8422 | 2.4167 | 24.9167 | QNI oscillatory stability limit of 1078 MW | Outage | Oscillatory Stability | Qld
F_MAIN++NIL_BL_L6 | 346.2715 | 0 | 4.6667 | 0 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
F_T+GTTE_TL_L6 | 340.112 | 0 | 21.0833 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
CA_BRIS_4D69957C_1 | 337.1361 | 0 | 1.9167 | 0 | Constraint Automation, O/L 275KV_8875:8875:I:275@H73_RAGL@QLD for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
F_VST+TL_L6_0550 | 336 | 0 | 0.58333 | 0 | Lower 6 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 550 | Outage | FCAS | FCAS
F_S++TIB1_R60 | 326.6129 | 0 | 1.1667 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 1 is the largest generation risk in SA | Outage | FCAS | FCAS
T>T_PMSH_IMP_4E | 322.1332 | 0 | 0.5 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
F_QNV+RREG_0220 | 320.373 | 0 | 1.9167 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::N_SMF2_xxx | 320.1228 | 483.8453 | 4.0833 | 3.8333 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_T++CO_752_TL_L5 | 319.8199 | 0 | 5.4167 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS | FCAS
SVML_080 | 312.3683 | 0 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 80 MW | Outage | Discretionary | SA
CA_BRIS_4DE45CFF_1 | 307.7451 | 0 | 0.58333 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
F_T+FASH_N-2_TG_R60 | 305.5134 | 1281.5555 | 1.5833 | 5.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_ESTN++MLMO_L60 | 288.177 | 7.81 | 103.5833 | 14.0833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
F_I+TG_R5_1000 | 285.4225 | 0 | 6.0833 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1000 | Outage | FCAS | FCAS
V::S_PATU_MAXG | 284.9053 | 305.1713 | 0.25 | 2.1667 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
F_VS++APD_TL_L60 | 280.6381 | 0 | 2.25 | 0 | Lower 60 sec requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_S++TIB2_R60 | 276.9032 | 0 | 2.1667 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA | Outage | FCAS | FCAS
V:T_SHGT_BL_1 | 272.9692 | 337.4598 | 0.33333 | 0.91667 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
N^^Q_LS_VC_B1 | 267.5577 | 0 | 1.9167 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
F_VS++APD_TL_L5 | 265.9392 | 0 | 2.6667 | 0 | Lower 5 min requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T+GTTE_TL_L60 | 264.9428 | 0 | 21 | 0 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
N>N-GITN_TE_B1 | 260.8648 | 0 | 2 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | Thermal | NSW
F_T++GO_C752_TG_R6 | 258.1108 | 0 | 0.25 | 0 | Out= Gordon CB C752, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
S>>TBTU_TBCG_TBMO | 247.4226 | 20.4827 | 4.1667 | 0.16667 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage | Thermal | SA
CA_BRIS_4DE6D9E8_1 | 234.5684 | 0 | 0.16667 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
F_MAIN++TG_R60_1000 | 221.1777 | 0 | 1.3333 | 0 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V_GANWR_BAT_G_ISL_0 | 216.2049 | 6491.3653 | 0.33333 | 2.25 | Gannawarra Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
F_S++TIB1_R6_1 | 214.8116 | 0 | 1.3333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 1 is the largest generation risk in SA, Segment 1 | Outage | FCAS | FCAS
F_S++MOPS2_R60 | 214.75 | 0 | 2.5 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Mortlake 2 is the largest generation risk in SA (MOPS connects to SA) | Outage | FCAS | FCAS
F_T++BLSPS_EXP_L6_1 | 208.0931 | 0 | 2.0833 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS | FCAS
T>T_NIL_BL_IMP_7CC | 202.2107 | 12211.1617 | 1 | 22.3333 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
V>>N-NIL_HG | 201.1892 | 27066.8196 | 0.083333 | 15.5833 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Thermal | Vic
F_MAIN++GFT_TG_R6 | 200.3006 | 0 | 4.1667 | 0 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_QNV+TL_L6_0600 | 199.98 | 0 | 0.16667 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::N_LT_UT_MS_xxx | 196.4904 | 0 | 0.25 | 0 | Out = Lower Tumut - Murray (66) line or Upper Tumut - Murray (65) line, prevent transient instability for fault and trip of Upper Tumut - Murray (65) or Lower Tumut - Murray (66) line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_QNV+MLMO_L6 | 194.9283 | 0.16 | 1.8333 | 0.083333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
SVML_020 | 193.514 | 0 | 1 | 0 | SA to Vic on ML upper transfer limit of 20 MW | Outage | Discretionary | SA
F_T_GORDON_R6 | 192.8546 | 0 | 0.16667 | 0 | Out= NIL, Gordon R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_I+ML_L5_APD_LD | 185.4165 | 0 | 87.9167 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage | FCAS | FCAS
F_T+FARE_N-2_TG_R6_1 | 184.8742 | 51.3519 | 0.41667 | 2.8333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage | FCAS | FCAS
V::S_KHKN_MAXG | 181.3606 | 0 | 1.6667 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
T>T_NIL_BL_5C | 180.4481 | 0 | 3.4167 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
F_QNV++ML_L60_0400 | 179.3572 | 0.09 | 95 | 0.16667 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_QNV++MLTR_L6 | 179.0811 | 0 | 9.1667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T+CSGO_TG_R5 | 175.951 | 131.6912 | 5.4167 | 0.66667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
VSML_020 | 171.3371 | 0 | 3.3333 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage | Discretionary | Vic
F_S+APD_TL_L5 | 170.9792 | 0 | 0.16667 | 0 | Lower 5 min requirement in SA for loss of both APD potlines, Separation between Heywood (HYTS) and Moorabool (MLTS) | Outage | FCAS | FCAS
F_MAIN++YW134_MGR6 | 169.6553 | 0 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV++RREG_0220 | 168.8297 | 0 | 1.25 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink able transfer FCAS | Outage | FCAS | FCAS
Q>N-MUTE_758 | 163.9164 | 642.9178 | 2.5833 | 0.83333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
F_QNV++MLTR_L60 | 163.6431 | 5.9 | 4.9167 | 4.9167 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_Q++8E_L5 | 160.3815 | 0 | 2.5 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
T>T_HAPM_IMP_4L | 160.2526 | 0 | 0.58333 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V^^S_KHKN_SETB | 158.658 | 0 | 0.58333 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | Voltage Stability | SA
F_T++NIL_TL_L5_DS | 155.4612 | 0 | 4 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
F_Q++LDTW_R60 | 152.0987 | 0 | 4.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_Q++LDMU_L5 | 146.7542 | 0 | 1.1667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
T>T_HAPM_IMP_4N | 144.0698 | 0 | 0.5 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V>NWCB6024+25_TX1 | 141.412 | 0 | 1.3333 | 0 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #1 132/66kV TX on trip of Monash-North West Bend #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | Thermal | SA
V:SS_820_HY_TEST | 140.4273 | 28.6978 | 0.58333 | 0.16667 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
F_ESTN++MLTR_L60 | 130.6666 | 22.23 | 10.1667 | 28.1667 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
F_MAIN++MG_R60_1000 | 125.7404 | 0 | 0.66667 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 1000, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_L60_APD_LD | 125.355 | 0 | 68.3333 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage | FCAS | FCAS
N^^Q_LDMU_1_B1 | 124.818 | 0 | 1.3333 | 0 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of Kogan Creek generator | Outage | Voltage Stability | NSW
F_Q_W/HOE_R5 | 123.2047 | 1689.035 | 6 | 8.9167 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage | Unit Zero - FCAS | FCAS
V_EP_BUS1 | 122.182 | 0 | 0.25 | 0 | Eildon PS Unit 2 upper limit set to zero due to outage of Eildon No 1 220 kV Bus | Outage | Unit Zero | Vic
V::S_NIL_MAXG_xxx | 121.9668 | 3123.6259 | 2.0833 | 11.3333 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Transient Stability | SA
T_T_FASH_HM_OPEN_1 | 121.4203 | 0 | 0.75 | 0 | Out = one Farrell to Sheffield 220kV line, West Coast 220/110 kV parallel open, Farrell 220 kV bus not split, limit West Coast gen <= 110% of West Coast load | Outage | Other | Tas
T::T_NIL_2 | 119.9514 | 27285.7135 | 1.6667 | 51.4167 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL | Transient Stability | Tas
S>>V_CGTI_TIPA_PGPA | 119.1488 | 0 | 0.16667 | 0 | Out= Cherry Gardens - Torrens Island 275kV line, avoid O/L Parafield Gardens West-Para 275kV line on trip of Torrens Island A -Para 275kV line, Feedback | Outage | Thermal | SA
F_QNV++ML_L5_0400 | 117.9458 | 0 | 63.9167 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage | FCAS | FCAS
T^V_HAPM_220_1 | 115.3385 | 0 | 0.33333 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage | Voltage Stability | Tas
F_I+MG_R6_0850 | 113.5201 | 0 | 0.33333 | 0 | Raise 6 sec Service Requirement for a NEM Generation Event, MG = 850 | Outage | FCAS | FCAS
V:SS_820_HY_TEST_DYN | 113.4514 | 109.4279 | 0.25 | 0.58333 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Oscillatory Stability | Vic
V>>N-X_MSUT_LTUT | 104.1944 | 0 | 0.16667 | 0 | Out = Murray-Upper Tumut and Lower Tumut-Upper Tumut(65+64), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Thermal | Vic
F_I+MG_R60_1000 | 104 | 0 | 0.66667 | 0 | Raise 60 sec Service Requirement for a NEM Generation Event, MG = 1000 | Outage | FCAS | FCAS
F_T+CO_752_TL_L6 | 103.8198 | 0 | 0.083333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>X_NWCB6022+6023_T2 | 102.2924 | 0 | 1.3333 | 0 | Out = North West Bend 132 kV circuit breakers CB6022 and CB6023(Note: this takes out North West Bend-Monash #2 132kV line); limit SA to Victoria flow on Murraylink to avoid North West Bend transformer #2 O/L on trip NWB 132/66kV Transformer #3. | Outage | Thermal | SA
Q^^CS_-080 | 100.9735 | 0 | 0.16667 | 0 | Nominated Offset -80MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage | Voltage Stability | Qld
S>>CGTB1_TBTU_TBMO | 100.6205 | 0 | 1.5 | 0 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_ESTN+TL_L5_0600 | 98.4883 | 0 | 7.3333 | 0 | Lower 5 min Service Requirement for a Eastern Network Event, TL = 600 | Outage | FCAS | FCAS
SVML_140 | 98.305 | 0 | 2.75 | 0 | SA to Vic on ML upper transfer limit of 140 MW | Outage | Discretionary | SA
F_QNV++MLMO_L60 | 97.2151 | 0.13 | 20.9167 | 0.083333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_L5_0400 | 96.5094 | 27.8 | 46.75 | 35.8333 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
F_Q++LDMU_R6 | 95.5142 | 0 | 1.3333 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
T_FARC1 | 93.9033 | 30636.0259 | 0.083333 | 1 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
F_MAIN++ML_L60_0400 | 90.584 | 1.48 | 4.8333 | 1.4167 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_QNV++APD_TL_L6 | 87.6948 | 0 | 0.5 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_STHN+RREG_0220 | 85.5763 | 0 | 0.16667 | 0 | Southern Raise Regulation Requirement greater than 220 MW | Outage | FCAS | FCAS
F_NQ+ML_L60_0400 | 84.35 | 0 | 6.9167 | 0 | Lower 60 sec Service Requirement for a NSW and Qld Load Event, ML = 400 | Outage | FCAS | FCAS
F_Q++LDTW_R6 | 83.4619 | 0 | 2.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
F_I+ML_L60_0400 | 83.1277 | 9.18 | 40.1667 | 14.75 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
Q>NIL_BI_xxx | 81.1545 | 87292.2936 | 0.5 | 130.1667 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines | NIL | Thermal | Qld
V_VS_MLMO_NETT | 80.0667 | 67.2312 | 0.66667 | 1.9167 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage | FCAS | Vic
V>>V_ROTS_TX_3A_R | 80.038 | 0 | 1 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Thermal | Vic
F_STHN+LREG_0210 | 79.4496 | 0 | 0.16667 | 0 | Southern Lower Regulation Requirement greater than 210 MW | Outage | FCAS | FCAS
VS_250 | 79.0546 | 0 | 1.5 | 0 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Discretionary | Vic
F_MAIN+GFT_TG_R6 | 78.63 | 0 | 0.41667 | 0 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N>>N_65+66_N-2_2 | 77.1727 | 4524.2787 | 0.33333 | 7.5833 | Out= Nil, avoid O/L Dederang to Wodonga on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL | Thermal | NSW
S>NIL_NIL_SGMYSE-T2 | 77.0656 | 0 | 0.66667 | 0 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on Nil trip (for Line component SECS assumed O/S or I/S), Feedback | NIL | Thermal | SA
F_S++TIB3_R60 | 76.4271 | 0 | 0.83333 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA | Outage | FCAS | FCAS
N::V_DDMS | 73.3087 | 0 | 0.58333 | 0 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage | Transient Stability | NSW
F_QNV++APD_TL_L5 | 66.0503 | 0 | 10.75 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage | FCAS | FCAS
Q_YARANSF1_ZERO | 65.4655 | 0 | 0.083333 | 0 | Yarrenlea Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_V_YWPS4_RREG | 65.2298 | 0 | 0.58333 | 0 | Out= NIL, Yallourn W4 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T+FASH_N-2_TG_R6_1 | 62.5312 | 9597.3336 | 0.083333 | 5.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS | FCAS
F_T++CSGO_TG_R5 | 60.3995 | 73.5994 | 4.5833 | 0.33333 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
F_T++GO_C752_TG_R60 | 60.3237 | 0 | 0.16667 | 0 | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_S_DLBAT-G_R6 | 59.7715 | 0 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Generation Component) R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN+GFT_TG_R5 | 58.94 | 0 | 5.4167 | 0 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_I+TG_R60_0850 | 55.3244 | 0 | 0.5 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 850 | Outage | FCAS | FCAS
F_ESTN+TL_L60_0600 | 53.64 | 0 | 7.3333 | 0 | Lower 60 sec Service Requirement for a Eastern Network Event, TL = 600 | Outage | FCAS | FCAS
F_T++FASH_N-2_TG_R5 | 53.39 | 45.9321 | 5.25 | 0.83333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_MAIN++GFT_TG_R5 | 52.8203 | 0 | 7.5 | 0 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_I+MG_R60_0850 | 52 | 0 | 0.33333 | 0 | Raise 60 sec Service Requirement for a NEM Generation Event, MG = 850 | Outage | FCAS | FCAS
N_WR_30_WT-INV | 51.2917 | 0 | 0.083333 | 0 | Limit White Rock wind/solar farm upper limit to 0 MW if number of wind turbine + inverter available exceed 30. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
N>>N-NIL__3_OPENED | 50.9096 | 1928.1756 | 0.33333 | 1.4167 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | Thermal | NSW
T_GO_260 | 48.7815 | 0 | 0.16667 | 0 | Discretionary 260 MW upper limit on total Gordon generation | Outage | Discretionary | Tas
F_T+CO_752_TL_L5 | 48 | 0 | 0.083333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T+CO_752_TL_L60 | 48 | 0 | 0.083333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>V_NWRB2_RBNW1 | 47.9548 | 34426.9488 | 0.16667 | 9.8333 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage | Thermal | SA
F_MAIN++MG_R6_0850 | 45.9755 | 0 | 0.16667 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage | FCAS | FCAS
T>T_GTSH_IMP_4E | 45.404 | 0 | 0.16667 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of Hadspen to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
F_ESTN+APD_TL_L60 | 45.26 | 0.16 | 14.5 | 0.16667 | Lower 60 sec requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS | FCAS
F_NVS++LREG_0210 | 44.6504 | 0 | 0.16667 | 0 | NSW, Vic and SA Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_WESTCOAST_LREG_0 | 44.3985 | 584.4026 | 1.4167 | 1.8333 | LREG FCAS of West Coast Generation limited to 0 MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN+ML_L60_0400 | 44.3764 | 2.2 | 0.91667 | 3.0833 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_QNV++APD_TL_L60 | 42.16 | 0 | 11.25 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_ESTN+APD_TL_L5 | 41.94 | 0.16 | 14.5833 | 0.16667 | Lower 5 min requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS | FCAS
F_S_DLBAT-G_R60 | 41.5233 | 0 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Generation Component) R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N::V_MNYS_MSDD | 40.537 | 0 | 0.25 | 0 | Out=Marulan-Yass(4 or 5), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | Transient Stability | NSW
SVML_010 | 39.6947 | 0 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 10 MW | Outage | Discretionary | SA
F_V+NIL_APD01_R60 | 39 | 47.9618 | 0.083333 | 0.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS | FCAS
QN_1050 | 38.509 | 0 | 0.41667 | 0 | Qld to NSW on QNI upper transfer limit of 1050 MW | Outage | Discretionary | Qld
Q>>RGLC_CLWU_BCCP | 38.3571 | 0 | 0.33333 | 0 | Out= Raglan to Larcom Creek (8875), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
CA_SYDS_4EBD234F_1 | 38.0158 | 0 | 0.5 | 0 | Constraint Automation, O/L XFMR T_1@R_TOWN@SA for Nil Trip Base Case. Generated by STNET[BNECR2] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
N^N_KKLS_1 | 36.2329 | 171.0685 | 2.0833 | 0.58333 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
F_ESTN++MLTR_L6 | 35.5149 | 0 | 6.0833 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_QNV++HGML_L6 | 35.1911 | 0 | 1.3333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
T::T_PMSH_2 | 34.986 | 0 | 0.16667 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage | Transient Stability | Tas
F_ESTN++MLMO_L5 | 32.5526 | 0 | 14.1667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
I_CTRL_ISSUE_TE | 32.0542 | 6242.2966 | 1.6667 | 19.8333 | DC Link Control Issue Constraint for Terranora | Outage | Other | Other
T_GO_250 | 31.4553 | 0 | 0.083333 | 0 | Discretionary 250 MW upper limit on total Gordon generation | Outage | Discretionary | Tas
F_QNV++HGTR_L60 | 30.08 | 0 | 1.1667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_Q++ARTW_R60 | 29.3966 | 0 | 0.83333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_I+TG_R6_0850 | 28.9993 | 0 | 0.41667 | 0 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 850 | Outage | FCAS | FCAS
F_QNV++HGML_L60 | 28.78 | 0 | 1.3333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_V++MOPS_R6_1 | 27.469 | 0 | 0.41667 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Mortlake Station is the largest generation risk in SA (MOPS connects to SA), Segment 1 | Outage | FCAS | FCAS
S_CGTB_TBMO_N-2_1 | 27.3372 | 0 | 0.91667 | 0 | Out= NIL, avoid O/L Tailumbend-Tungkillo 275kV line on trip of Tailumbend-Cherry Gardens 275kV line and Tailem Bend-Mobilong 132kV lines, (Note: with both Black Range series caps I/S or O/S) | Outage | Thermal | SA
F_NVS++APD_TL_L6 | 27.0559 | 0 | 0.16667 | 0 | Lower 6 sec requirement for a NSW, Vic and SA Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage | FCAS | FCAS
SVML_160 | 25.238 | 0 | 0.083333 | 0 | SA to Vic on ML upper transfer limit of 160 MW | Outage | Discretionary | SA
F_MAIN++ML_L5_0400 | 25.039 | 5.07 | 5.0833 | 2.5833 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_ESTN++MLTR_L5 | 24.8064 | 9.7077 | 3.75 | 4.8333 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_T_FAJB_RREG | 21.6577 | 0 | 0.16667 | 0 | Out=Farrell-John Butters 220KV line. RREG <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_V+NIL_APD01_R6 | 20.7 | 48.9586 | 0.083333 | 0.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS | FCAS
F_QNV+TL_L5_0600 | 20 | 0 | 0.16667 | 0 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV++HGTR_L6 | 19.9599 | 0 | 1.1667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
N>Q-TEMU_757_758 | 19.1923 | 0 | 0.58333 | 0 | Out= 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line, avoid O/L on remaining T174 Terranora to H4 Mudgeeraba line (758 or 757), Feedback | Outage | Thermal | NSW
F_QNV+MLTR_L60 | 19.04 | 4.9955 | 0.25 | 1.4167 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V^^S_PAVC1_MAXG | 18.2853 | 0 | 0.33333 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
S>>NIL_CGTB_TUTB_1 | 17.7792 | 0 | 0.41667 | 0 | Out= Nil, avoid O/L Tungkillo - Tailem Bend 275kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | NIL | Thermal | SA
F_T+FASH_N-2_TG_R5 | 17.4321 | 550.2721 | 1.1667 | 5.3333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
T>T_NIL_BL_220_6B | 17.2766 | 67.3069 | 0.083333 | 0.16667 | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Thermal | Tas
VSML_010 | 16.9116 | 0 | 0.91667 | 0 | Vic to SA on ML upper transfer limit of 10 MW | Outage | Discretionary | Vic
F_QNV+MLTR_L6 | 15.0724 | 0 | 0.41667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V>SMLMHNW1 | 14.6464 | 2023.5184 | 1.9167 | 5.0833 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | SA
Q_CS_1700 | 13.9853 | 67012.6311 | 0.083333 | 41 | Qld Central to Qld South upper transfer limit of 1700MW (discretionary) | Outage | Discretionary | Qld
QNI_SOUTH_1100_DYN | 13.849 | 0 | 0.16667 | 0 | QLD to NSW on QNI upper transfer limit of 1100 MW, dynamic headroom, DS formulation only. | Outage | Transient Stability | Qld
F_Q+CC4_R60 | 13.73 | 0 | 0.083333 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Callide C unit 4) | Outage | FCAS | FCAS
V^^S_MLSY_2 | 12.3774 | 0 | 0.33333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Voltage Stability | Vic
T^V_NIL_11 | 12.1346 | 8179.3981 | 0.083333 | 5.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Voltage Stability | Tas
F_T++BLSPS_EXP_L60_1 | 11.99 | 0 | 2.0833 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS | FCAS
F_STHN+MG_R60 | 11.8 | 0 | 0.16667 | 0 | Raise 60 sec Service Requirement for a Southern Generation Event | Outage | FCAS | FCAS
F_T+FARE_N-2_TG_R5 | 11.3494 | 324.1627 | 1.1667 | 2.75 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>NIL_NIL_SGBN | 11.2907 | 20496.1987 | 0.16667 | 1.5833 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | Thermal | SA
F_QNV+MLMO_L60 | 10.97 | 37.0623 | 2.5833 | 9.5 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
N::Q_MUTW_1 | 10.8683 | 0 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | Transient Stability | NSW
V::S_PAVC1_MAXG | 10.7805 | 0 | 0.66667 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | Transient Stability | SA
Q>>WOSP_WOPW_WOGP_1 | 10.7629 | 0 | 0.25 | 0 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage | Thermal | Qld
F_T+GTTE_TL_L5 | 10.44 | 0 | 0.16667 | 0 | Out = one George Town to Temco 110 kV line, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
T^^V_PMSH_1 | 9.4174 | 0 | 0.083333 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of either one Sheffield to Georgetown 220kV line or one Hadspen to Georgetown 220kV line. | Outage | Voltage Stability | Tas
V_GANWR_BAT_G_FLT_0 | 9.1827 | 1274.8293 | 0.16667 | 3.0833 | Limit Gannawarra Battery (Generation Component) upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V^^S_KHKN_MAXG | 9.1362 | 0 | 0.083333 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
F_VST+TL_L60_0600 | 8.8538 | 0 | 2.3333 | 0 | Lower 60 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 600 | Outage | FCAS | FCAS
S_HPRL1_E | 8.2457 | 500.2828 | 0.16667 | 0.91667 | Out= Nil, Hornsdale Battery load energy target <= 40 MW | NIL | Other | SA
F_QNV+ML_L60_0400 | 7.89 | 0 | 2.6667 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_VST+TL_L5_0600 | 7.5995 | 0 | 2.3333 | 0 | Lower 5 min Service Requirement for a Vic, SA and Tas Network Event, TL = 600 | Outage | FCAS | FCAS
S>>NIL_TBTU_TBMO_1 | 7.4914 | 46853.8367 | 0.16667 | 3.9167 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
F_I+MG_R5_1000 | 7.38 | 0 | 0.66667 | 0 | Raise 5 min Service Requirement for a NEM Generation Event, MG = 1000 | Outage | FCAS | FCAS
F_T++BLSPS_EXP_L5 | 7.2916 | 0 | 2 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage | FCAS | FCAS
SVML_040 | 7.2496 | 0 | 0.16667 | 0 | SA to Vic on ML upper transfer limit of 40 MW | Outage | Discretionary | SA
QN_1100 | 7.2413 | 0 | 0.083333 | 0 | Qld to NSW on QNI upper transfer limit of 1100 MW | Outage | Discretionary | Qld
F_QNV+TL_L60_0600 | 7.19 | 0 | 0.16667 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V>>V_EPTT_1 | 7.03 | 0 | 0.083333 | 0 | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to South) for loss of the parallel line, feedback | Outage | Thermal | Vic
F_STHN+MG_R6 | 7 | 0 | 0.16667 | 0 | Raise 6 sec Service Requirement for a Southern Generation Event | Outage | FCAS | FCAS
S>NWCB6021+22_TX2 | 6.9379 | 0 | 0.16667 | 0 | Out= North West Bend 132kV CBs 6021 and 6022(this offloads NWB TX1), avoid O/L North West Bend #2 132/66kV TX on trip of North West Bend-Robertstown #1 132kV line (this splits NWB 132kV bus), | Outage | Thermal | SA
F_ESTN++HGTR_L60 | 6.87 | 0 | 1.25 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
VSML_015 | 6.523 | 0 | 0.5 | 0 | Vic to SA on ML upper transfer limit of 15 MW | Outage | Discretionary | Vic
F_QNV+ML_L5_0400 | 6.18 | 0 | 2.6667 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_S+HL_TG_R5 | 6.1447 | 0 | 0.083333 | 0 | Raise 5 min Service Requirement for the loss of Canowie to Hallett 275 kV line | Outage | FCAS | FCAS
F_MAIN+ML_L5_0400 | 6.08 | 6.09 | 0.91667 | 5.5833 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_I+TG_R5_0850 | 5.94 | 0 | 0.5 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 850 | Outage | FCAS | FCAS
F_VST+APD_TL_L60 | 5.7343 | 0 | 2.6667 | 0 | Lower 60 sec requirement for a Vic, SA and Tas Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS | FCAS
V>>V_MLSY_4BR | 5.0229 | 0 | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage | Thermal | Vic
F_I+TG_R60_0700 | 5 | 0 | 0.083333 | 0 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 700 | Outage | FCAS | FCAS
F_ESTN++HGTR_L5 | 4.9 | 0 | 1.0833 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_MAIN+ML_L5_APD_LD | 4.85 | 0 | 1.9167 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage | FCAS | FCAS
T_T_FASH_HM_OPEN_2 | 4.8148 | 0 | 0.33333 | 0 | Out = one Farrell to Sheffield 220kV line, West Coast 220/110 kV parallel open, Farrell 220 kV bus not split, limit West Coast gen >= 90% of West Coast load | Outage | Other | Tas
N::Q_BWSW_KC | 4.6401 | 0 | 0.16667 | 0 | Out= Bayswater to Sydney West (32), NSW to Qld Transient Stability Limit for trip of Kogan Creek | Outage | Transient Stability | NSW
F_Q++8C_R60 | 4.5986 | 0 | 0.16667 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_ESTN++HGML_L5 | 4.48 | 0 | 0.83333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_VST+TL_L60_0500 | 4.02 | 0 | 1.3333 | 0 | Lower 60 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 500 | Outage | FCAS | FCAS
F_Q_MACKAYGT_R5 | 4 | 31.68 | 0.16667 | 2.6667 | Out= NIL, Mackay GT R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V^S_HYCP | 3.9929 | 0 | 0.083333 | 0 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL | Voltage Stability | Vic
F_I+MG_R5_0850 | 3.87 | 0 | 0.33333 | 0 | Raise 5 min Service Requirement for a NEM Generation Event, MG = 850 | Outage | FCAS | FCAS
F_VS++TL_L5_0500 | 3.76 | 0 | 0.83333 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_ESTN++HGML_L60 | 3.65 | 0 | 1.3333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
V^^S_SEVC1_MAXG | 3.5235 | 0 | 0.16667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
N>Q_LSLS_9U8 | 3.353 | 5947.422 | 0.25 | 8.5833 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 directlink cable O/S. | Outage | Thermal | NSW
F_VST+TL_L5_0500 | 3.28 | 0 | 1.3333 | 0 | Lower 5 min Service Requirement for a Vic, SA and Tas Network Event, TL = 500 | Outage | FCAS | FCAS
F_MAIN++ML_L5_APD_LD | 3.1 | 0 | 1.9167 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_MAIN++YW134_MGR5 | 2.93 | 0 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV++HGML_L5 | 2.9113 | 0 | 0.66667 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
N>>Q-LDTW_2 | 2.892 | 0 | 0.083333 | 0 | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage | Thermal | NSW
F_QNV+MLTR_L5 | 2.89 | 0.44 | 0.16667 | 0.083333 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN++ML_L6_APD | 2.74 | 43.97 | 0.5 | 35 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS | FCAS
VS_050 | 2.6163 | 1.4748 | 0.083333 | 0.16667 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Discretionary | Vic
F_MAIN+ML_L60_APD_LD | 2.5694 | 0 | 1.75 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_QNV++MLTR_L5 | 2.55 | 0.41 | 0.41667 | 0.33333 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T_GORDON_R60 | 2.38 | 0 | 0.16667 | 0 | Out= NIL, Gordon R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>BRTW_BWPA_WTTP | 2.3489 | 10382.4902 | 0.25 | 0.83333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
Q::N_DM_CB_AR_2L-G | 2.2158 | 1011.0932 | 0.083333 | 1.6667 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
F_VST+APD_TL_L5 | 2.15 | 0 | 2.0833 | 0 | Lower 5 min requirement for a Vic, SA and Tas Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS | FCAS
F_S_DLBAT-G_R5 | 1.99 | 0 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Generation Component) R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_V+NIL_APD01_R5 | 1.89 | 12.45 | 0.083333 | 0.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS | FCAS
F_QNV++HGTR_L5 | 1.85 | 0 | 0.41667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_VS++TL_L5_0550 | 1.79 | 0 | 0.5 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN++MG_R60_0850 | 1.78 | 0 | 0.16667 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_STHN+MG_R5 | 1.69 | 0 | 0.16667 | 0 | Raise 5 min Service Requirement for a Southern Generation Event | Outage | FCAS | FCAS
F_NVS++APD_TL_L60 | 1.68 | 0 | 0.16667 | 0 | Lower 60 sec requirement for a NSW, Vic and SA Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_VS++TL_L60_0550 | 1.6362 | 0 | 0.41667 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV++MLMO_L5 | 1.6 | 0 | 0.5 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_STHN++MUTW_R60 | 1.56 | 0 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88) line, Southern Raise 60 sec Requirement | Outage | FCAS | FCAS
F_I+YW134_N-2_MG_R6 | 1.47 | 0 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Global Raise 6 sec requirement | Outage | FCAS | FCAS
F_VS++TL_L60_0500 | 1.37 | 0 | 0.58333 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_VST+TL_L5_0550 | 1.29 | 0 | 0.58333 | 0 | Lower 5 min Service Requirement for a Vic, SA and Tas Network Event, TL = 550 | Outage | FCAS | FCAS
F_MAIN++ML_L60_APD_L | 1.27 | 0 | 1.75 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_I+YW134_N-2_MG_R60 | 1.2449 | 0 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Global Raise 60 sec requirement | Outage | FCAS | FCAS
S>>BRTW_RBTU_WTTP | 1.2412 | 1487.2006 | 0.33333 | 0.083333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_ESTN++HGTR_L6 | 1.15 | 0 | 0.16667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_VST+TL_L60_0550 | 1.0938 | 0 | 0.58333 | 0 | Lower 60 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 550 | Outage | FCAS | FCAS
F_ESTN++HGML_L6 | 0.99 | 0 | 0.083333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_I+TG_R5_0700 | 0.95 | 0 | 0.083333 | 0 | Raise 5 min Service Requirement for a NEM Network Event, TG = 700 | Outage | FCAS | FCAS
F_NVS++APD_TL_L5 | 0.9 | 0 | 0.16667 | 0 | Lower 5 min requirement for a NSW, Vic and SA Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_QNV++TL_L5_0600 | 0.85 | 0 | 0.083333 | 0 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV+APD_TL_L60 | 0.64 | 0 | 0.16667 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_QNV+APD_TL_L5 | 0.63 | 0 | 0.16667 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_S+HL_TG_R60 | 0.5 | 0 | 0.083333 | 0 | Raise 60 sec Service Requirement for the loss of Canowie to Hallett 275 kV line | Outage | FCAS | FCAS
F_QNV+MLMO_L5 | 0.38 | 0.08 | 0.16667 | 0.083333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_S_DLBAT-L_L5 | 0.38 | 0 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Load Component) L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_DLBAT-L_L60 | 0.38 | 0 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Load Component) L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN++MG_R5_1000 | 0.36 | 0 | 0.33333 | 0 | Raise 5 min Service Requirement for a Mainland Generation Event, MG = 1000, Basslink able to transfer FCAS | Outage | FCAS | FCAS
CA_BRIS_4D2AA9D0_1 | 0.32753 | 0 | 0.16667 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG MVPB on trip of DDTS-SMTS1 &DDTS-SMTS2 330KV LINES. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
F_STHN+APD_TL_L60 | 0.32 | 0 | 0.16667 | 0 | Lower 60 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS | FCAS
F_QNV++TL_L60_0600 | 0.27 | 0 | 0.083333 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_L6_APD | 0.26 | 58.9 | 0.41667 | 165.8333 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS | FCAS
T>T_NIL_BL_110_8_1 | 0.2092 | 123.9994 | 0.16667 | 0.33333 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Thermal | Tas
F_T++FARE_N-2_TG_R5 | 0.13055 | 159.7208 | 0.25 | 1.3333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_S_DLBAT-L_L6 | 0.09 | 0 | 0.16667 | 0 | Out= NIL, Dalrymple Battery (Load Component) L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T_FAMA_R5 | 0.09 | 0 | 0.083333 | 0 | Out=Farrell-Mackintosh 110KV line. R5 <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_STHN+APD_TL_L6 | 0.06 | 0 | 0.16667 | 0 | Lower 6 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS | FCAS
F_I+YW134_N-2_MG_R5 | 0.03 | 0 | 0.25 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Global Raise 5 Min requirement | Outage | FCAS | FCAS
S>BRTW_BWPA_HUWT | 0.01759 | 55665.8181 | 0.66667 | 2.5 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
N>>V-NIL_0X1 | 0.00106 | 0 | 0.083333 | 0 | Out= NIL, avoid O/L Buronga to Redcliff (OX1) on Nil trip, Feedback | NIL | Thermal | NSW

## Summary By Region
Binding Hours
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Ad-Hoc |  |  |  |  | 0 | 0
Constraint Automation | 5.5 | 24.9167 | 4.75 | 1.3333 | 8.5833 | 22.75
Direction | 3.6 | 18.3333 | 1152.0833 | 8190.0833 | 4093.5833 | 6243.5
FCAS |  | 104367.5833 | 88959.4167 | 95124.9167 | 105057.75 | 103359.8333
NSW | 3112.1667 | 2768.5 | 4260.0833 | 3057.8333 | 4993.6667 | 5560.75
Negative Residue | 13.0833 | 46.8333 | 25.75 | 10.4167 | 24.1667 | 31.25
Non-Conformance | 228.6667 | 156.6667 | 97.3333 | 61.0833 | 93.75 | 110.5833
Other | 142.6667 | 50.5833 | 311.8333 | 115.25 | 64.3333 | 48.4167
Outage Ramping | 236.8333 | 251.8333 | 142.25 | 174.4167 | 475.0833 | 645.8333
Qld | 913.75 | 1756.6667 | 996.6667 | 511.3333 | 3120.5833 | 8015.5
Quick | 281.5 | 1000.0833 | 1918.25 | 12617.6667 | 10994.8333 | 9862.0833
SA | 3383.5833 | 3995.1667 | 2013.25 | 3285.75 | 3935.6667 | 4110
Tas | 354.5833 | 895.9167 | 923.1667 | 1027.6667 | 966.5833 | 1886.6667
Vic | 5660.4167 | 6854 | 2618 | 1914.5 | 5095.75 | 6439.6667
Binding Impact
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Ad-Hoc | 0 | 0 | 0 | 0 | 0 | 0
Constraint Automation | 61543.4159 | 64122.5584 | 6287.0142 | 4494.9703 | 59181.5539 | 14369.9689
FCAS | 11967737.2201 | 27702893.4048 | 24018595.0767 | 11563905.7935 | 14750181.9392 | 28959781.4212
NSW | 3008201.0876 | 2981579.7124 | 3811263.7887 | 4130424.9984 | 20853119.0897 | 20558572.6087
Negative Residue | 133618.843 | 159141.1919 | 65879.5695 | 190929.9383 | 357086.6257 | 778063.9302
Other | 5944.8762 | 35445.6298 | 19441.5552 | 11515.5764 | 31229.546 | 199098.2389
Qld | 17832407.3191 | 3412397.6405 | 1557960.0849 | 1092572.6105 | 14405785.5151 | 58969747.1872
SA | 7975370.452 | 19175976.6502 | 19603528.2545 | 49743082.8304 | 23177002.4614 | 19911748.8298
Tas | 2498349.5552 | 3312667.8479 | 4771966.3751 | 2671514.9731 | 5630711.8908 | 7676693.2707
Vic | 3149671.2278 | 6498415.4069 | 3681628.8597 | 3495766.3104 | 19701434.9435 | 29835220.6476
Total | 46632843.9969 | 63342640.0428 | 57536550.5786 | 72904208.0013 | 98965733.5652 | 166903296.1032
Note on A6: FCAS excluded as it will swamp the graph

## NIL vs Outage
Binding Hours
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Commissioning | 166.5 | 151.3333 | 501.9167 | 12116 | 10389.25 | 7565
FCAS - NIL | 78805.6667 | 98151.5 | 83335.5 | 89035.8333 | 86275.9167 | 87403.0833
FCAS - Outage | 2785.8333 | 6213.6667 | 5623.9167 | 6087.5833 | 18781.8333 | 15954.5833
System Normal | 7848.6667 | 9089.4167 | 6047.6667 | 4947.25 | 8902 | 12236.5
Network Support | 204.5 | 128.3333 | 55.6667 | 210.3333 | 74.25 | 123.4167
Negative Residues | 13.0833 | 46.8333 | 25.75 | 10.4167 | 24.1667 | 31.25
Outage | 5748.1667 | 7284.5833 | 5121.75 | 4817.0833 | 9302.6667 | 13833.9167
Total (non-FCAS) | 13980.9167 | 16700.5 | 11752.75 | 22101.0833 | 28692.3333 | 33790.0833
Binding Impact
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Commissioning | 1122946.4259 | 1067028.2274 | 933870.4383 | 48442546.0203 | 68138620.5509 | 20610054.6861
FCAS - NIL | 1523297.0635 | 4284769.1816 | 9691374.8176 | 8309289.3932 | 10234061.3339 | 8943329.8904
FCAS - Outage | 10444462.1066 | 23418124.2233 | 14327220.2591 | 3254616.4004 | 4516120.6054 | 20016451.5307
System Normal | 7628472.3458 | 13101240.0894 | 16979263.4586 | 20382744.3293 | 37998718.3151 | 76531698.5404
Network Support | 22261395.2873 | 8878912.2779 | 965379.2057 | 30414067.7368 | 683796.7041 | 243610.7044
Negative Residues | 134581.6187 | 159141.1919 | 65879.5695 | 190929.9383 | 357086.6257 | 778063.9302
Outage | 4643343.5874 | 13500453.0789 | 15507433.2681 | 10352560.2034 | 45175949.9811 | 60390141.5071
Total | 47758498.4352 | 64409668.2703 | 58470421.0169 | 121346754.0216 | 167104354.1161 | 187513350.7893

## Interconnector Binding
Interconnector Direction | Constraint Equation ID | 2020 Hours | 2019 Hours | Description | Type
N-Q-MNSP1 Export | N^N-LS_SVC | 630.0833 | 22.3333 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage
N-Q-MNSP1 Export | N_X_MBTE_3A | 240.0833 | 36.5 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 78.5833 | 76.1667 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
N-Q-MNSP1 Export | N>N-NIL_LSDU | 62.25 | 16.6667 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Export | N_X_MBTE2_A | 38.3333 | 11.3333 | Out= two Directlink cables, NSW to Qld limit | Outage
N-Q-MNSP1 Export | NQTE_ROC | 37.5833 | 11.75 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Export | F_Q++MUTW_R6 | 35.9167 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 29.5833 | 3.0833 | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N^N_CHLS_1 | 15.6667 | 29.5833 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage
N-Q-MNSP1 Export | N>LSDU9U6_LSDU9U7 | 10.8333 | 22.0833 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | N^^Q_ARTW_B1 | 9.9167 | 0 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
N-Q-MNSP1 Export | F_Q++MUTW_R60 | 8.0833 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N^^Q_NIL_A | 6 | 22.5833 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
N-Q-MNSP1 Export | N^^Q_MUTW_1_B1 | 3.0833 | 0 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage
N-Q-MNSP1 Export | F_Q++MUTW_R5 | 2.4167 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | N^N_KKLS_1 | 2.0833 | 0.83333 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage
N-Q-MNSP1 Export | N>N-GITN_TE_B1 | 1.9167 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R6 | 1.8333 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 1.6667 | 20.9167 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | N>N-ARCH_87_TE_C1 | 1.3333 | 0 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | N^^Q_LDMU_1_B1 | 1.3333 | 0 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of Kogan Creek generator | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R60 | 1.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B1 | 1.1667 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N>Q-MUTW_2 | 0.91667 | 0 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage
N-Q-MNSP1 Export | F_Q++LDMU_R6 | 0.75 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | #R020306_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 27/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R020471_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 27/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R020484_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R021180_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | N>Q-TEMU_757_758 | 0.58333 | 0 | Out= 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line, avoid O/L on remaining T174 Terranora to H4 Mudgeeraba line (758 or 757), Feedback | Outage
N-Q-MNSP1 Export | #R020765_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020896_003_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^N_CHLS_1, Effective Date: 29/09/2015, Version: 1 | Other
N-Q-MNSP1 Export | #R021889_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R021909_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020306_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 27/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R020471_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 27/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R020790_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R021159_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R021159_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R021341_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R021615_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020484_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020740_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R021510_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R022023_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022064_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #N-Q-MNSP1_I_E | 0.25 | 0 | N-Q-MNSP1.ENERGY * -1 >= 49 (Wt = 35) | Other
N-Q-MNSP1 Export | #R020784_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R021180_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R021582_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | N>Q_LSLS_9U8 | 0.25 | 8.5833 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 directlink cable O/S. | Outage
N-Q-MNSP1 Export | #R020516_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020790_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020964_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R021510_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R022054_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | CA_BRIS_4D69957C_1 | 0.16667 | 0 | Constraint Automation, O/L 275KV_8875:8875:I:275@H73_RAGL@QLD for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage
N-Q-MNSP1 Export | N>>N-NIL__3_OPENED | 0.16667 | 1.4167 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL
N-Q-MNSP1 Export | N>N-NIL_TE_E1 | 0.16667 | 6.1667 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST | NIL
N-Q-MNSP1 Export | QNI_ISLE_B | 0.16667 | 0 | Qld / Southern separation, allow QNI to supply Northern NSW Load | Outage
N-Q-MNSP1 Export | Q^^NIL_TR_CLHA | 0.16667 | 0 | Out = Nil, Tarong voltage stability limit, Calvale-Halys contingency equation | NIL
N-Q-MNSP1 Export | #R020490_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020498_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020500_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R020815_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_LDTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R021066_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R021086_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R021086_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R021096_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R021407_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022054_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | N::Q_MUTW_1 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
N-Q-MNSP1 Export | N^^Q_BCDM_B1 | 0.083333 | 0 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L6 | 925.75 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 763.1667 | 204.8333 | Out= two Directlink cables, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N_X_MBTE_3B | 557.0833 | 137.5 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L5 | 141.9167 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N_MBTE1_B | 119.6667 | 466.0833 | Out= one Directlink cable, Qld to NSW limit | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L6 | 91.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | Q>N-MUTE_757 | 56.5 | 0 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 46.6667 | 11.0833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | QNTE_ROC | 30 | 18.25 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | F_Q++LDTW_L5 | 15.4167 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N>N-NIL_MBDU | 8.8333 | 61.8333 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Import | Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 8.3333 | 19.0833 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 7.25 | 8 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 5.8333 | 8.4167 | Negative Residue Management constraint for QLD to NSW flow | NIL
N-Q-MNSP1 Import | F_Q++LDMU_L6 | 5.5 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L60 | 3.5 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L60 | 3.1667 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | Q>N-MUTE_758 | 2.5833 | 0.83333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | N>>N-964_DC | 2 | 3.8333 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage
N-Q-MNSP1 Import | F_Q++LDMU_L60 | 1.25 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | Q^^NIL_CS | 1.1667 | 0 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation | NIL
N-Q-MNSP1 Import | F_Q++LDMU_L5 | 0.75 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | #N-Q-MNSP1_RAMP_E_F | 0.58333 | 0 | N-Q-MNSP1 >= MIN(60, InitialFlow + 80) (Wt=35) | Other
N-Q-MNSP1 Import | #R020790_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020881_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | F_Q++LDTW_L60 | 0.5 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | #R020498_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021096_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021268_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021270_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021270_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021909_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020516_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020649_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021341_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021615_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021889_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R022025_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020490_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020500_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020500_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021096_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021268_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021889_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R022004_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | N::V_MNYS_MSDD | 0.25 | 0 | Out=Marulan-Yass(4 or 5), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
N-Q-MNSP1 Import | #R020765_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021615_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021909_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R022025_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | Q^^CS_-080 | 0.16667 | 0 | Nominated Offset -80MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage
N-Q-MNSP1 Import | #R020490_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020498_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020516_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R020765_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R021341_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 139.4167 | 100.8333 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
NSW1-QLD1 Export | F_Q++MUTW_R6 | 45.1667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | Q>>NIL_BCCP_RGLC | 23 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL
NSW1-QLD1 Export | Q>>NIL_CLWU_RGLC | 22.9167 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL
NSW1-QLD1 Export | N^^Q_ARTW_B1 | 17.3333 | 0 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
NSW1-QLD1 Export | F_Q++MUTW_R60 | 14.4167 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_NIL_A | 8.8333 | 24.4167 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
NSW1-QLD1 Export | Q>>WOSP_WOPW_WOGP_2 | 6.0833 | 2.75 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_MUTW_1_B1 | 3.75 | 0 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage
NSW1-QLD1 Export | F_Q++MUTW_R5 | 2.3333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | F_Q++LDTW_R6 | 2.25 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | #NSW1-QLD1_RAMP_I_F | 1.9167 | 0 | NSW1-QLD1 >= MIN(-246, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Export | CA_BRIS_4D69957C_1 | 1.9167 | 0 | Constraint Automation, O/L 275KV_8875:8875:I:275@H73_RAGL@QLD for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage
NSW1-QLD1 Export | F_Q++LDTW_R60 | 1.9167 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_LS_VC_B1 | 1.9167 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_LDMU_1_B1 | 1.3333 | 0 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of Kogan Creek generator | Outage
NSW1-QLD1 Export | F_Q++ARTW_R60 | 0.75 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | F_Q++LDMU_R6 | 0.75 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N>Q-MUTW_2 | 0.66667 | 0 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage
NSW1-QLD1 Export | #R020797_002_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint Q>>WOSP_WOPW_WOGP_2, Effective Date: 18/02/2020, Version: 1 | Other
NSW1-QLD1 Export | Q>>CLWU_BCRG_BCCP | 0.5 | 2.5833 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
NSW1-QLD1 Export | Q>>NIL_LCCP_BCCP | 0.5 | 0 | Out= Nil, avoid O/L Bouldercombe to Calliope River (812) on trip of Larcom Creek to Calliope River (8859) line, Feedback | NIL
NSW1-QLD1 Export | Q^^NIL_TR_CLHA | 0.5 | 0 | Out = Nil, Tarong voltage stability limit, Calvale-Halys contingency equation | NIL
NSW1-QLD1 Export | #R020740_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R020972_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022023_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022064_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | N>>N-NIL__3_OPENED | 0.33333 | 1.4167 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL
NSW1-QLD1 Export | Q>>RGLC_CLWU_BCCP | 0.33333 | 0 | Out= Raglan to Larcom Creek (8875), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | #R020784_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R020797_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q>>WOSP_WOPW_WOGP_2, Effective Date: 18/02/2020, Version: 1 | Other
NSW1-QLD1 Export | #R020964_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R020964_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R021023_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R021039_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | N::Q_BWSW_KC | 0.25 | 0 | Out= Bayswater to Sydney West (32), NSW to Qld Transient Stability Limit for trip of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_BCDM_B1 | 0.25 | 0 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | Q>>WOSP_WOPW_WOGP_1 | 0.25 | 0 | Out= Woolooga to South Pine (807) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to Palmwoods (810) 275kV line, Feedback | Outage
NSW1-QLD1 Export | #R020815_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_LDTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R021066_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R021086_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R022054_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | F_Q++8C_R60 | 0.16667 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | QNI_ISLE_B | 0.16667 | 0 | Qld / Southern separation, allow QNI to supply Northern NSW Load | Outage
NSW1-QLD1 Export | #R021066_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R021086_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R021086_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R021407_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022054_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | N::Q_MUTW_1 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
NSW1-QLD1 Export | N>>Q-LDTW_2 | 0.083333 | 0 | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage
NSW1-QLD1 Import | F_Q++MUTW_L6 | 1006.8333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | Q^^NIL_QNI_SRAR | 395.4167 | 770.75 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL
NSW1-QLD1 Import | F_Q++MUTW_L5 | 157.6667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 154.5 | 226.3333 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL
NSW1-QLD1 Import | F_Q++LDTW_L6 | 92.75 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L6 | 57.9167 | 11.8333 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++BCDM_L6 | 35.6667 | 107.8333 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 27.75 | 2.1667 | NSW1-QLD1 >= MIN(-246, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Import | I_QNI_ONE_PHASE_N-2 | 18.5 | 34 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage
NSW1-QLD1 Import | F_Q++LDTW_L5 | 15.5 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++8E_L6 | 13 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L5 | 11 | 8.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q::N_AR_CP2_AR_2L-G | 9.4167 | 0 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++8C_L6 | 9.3333 | 2.3333 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | Q^^N_AR_SVC_1 | 8.9167 | 1.5833 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage
NSW1-QLD1 Import | QNI_SOUTH_1150_DYN | 8 | 3.6667 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL
NSW1-QLD1 Import | Q:N_TW330_CB5102_OSC | 6.8333 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 5.9167 | 9.25 | Negative Residue Management constraint for QLD to NSW flow | NIL
NSW1-QLD1 Import | F_Q++LDMU_L6 | 5.75 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++NIL_R5 | 5.1667 | 1.8333 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | F_Q++BCDM_L5 | 4.75 | 32.25 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | N>>N-964_DC | 4 | 3.1667 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage
NSW1-QLD1 Import | N>N-NIL_DC | 3.75 | 63.1667 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
NSW1-QLD1 Import | F_Q++MUTW_L60 | 3.5833 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++8C_L5 | 3.25 | 1.25 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L60 | 3.1667 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | QNI_SOUTH_1050_DYN | 3.1667 | 0 | QLD to NSW on QNI upper transfer limit of 1050 MW, dynamic headroom, DS formulation only. | Outage
NSW1-QLD1 Import | Q:N_1078 | 2.1667 | 25.6667 | QNI oscillatory stability limit of 1078 MW | Outage
NSW1-QLD1 Import | F_Q++8E_L5 | 1.6667 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q::N_ARSVC_AR_2L-G | 1.5833 | 5.6667 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | Q^^NIL_CS | 1.5 | 0 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation | NIL
NSW1-QLD1 Import | F_Q++LDMU_L60 | 1.4167 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | V::N_ESTN_HYSE_QA | 1.4167 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
NSW1-QLD1 Import | V::N_ESTN_HYSE_QD | 0.91667 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, QLD accelerates, segment 1 | Outage
NSW1-QLD1 Import | F_Q++LDMU_L5 | 0.75 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | #R020689_003_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint Q:N_TW330_CB5102_OSC, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R021226_017_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint Q^^N_AR_SVC_1, Effective Date: 16/05/2019, Version: 1 | Other
NSW1-QLD1 Import | F_Q++LDTW_L60 | 0.5 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_E_F | 0.41667 | 0 | NSW1-QLD1 >= MIN(40, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Import | #R020945_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R020945_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021123_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint Q::N_DM_CB_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R020921_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | F_Q++NIL_R60 | 0.25 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | N::V_MNYS_MSDD | 0.25 | 0 | Out=Marulan-Yass(4 or 5), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
NSW1-QLD1 Import | V::N_BYPASS_HW_SY_Q3 | 0.25 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
NSW1-QLD1 Import | #R020880_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q::N_LDTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021152_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021324_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q::N_ARTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021719_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021770_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | QNI_SOUTH_1100_DYN | 0.16667 | 0 | QLD to NSW on QNI upper transfer limit of 1100 MW, dynamic headroom, DS formulation only. | Outage
NSW1-QLD1 Import | #R020722_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R020944_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R020946_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021029_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021380_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021501_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q:N_1078, Effective Date: 24/07/2013, Version: 1 | Other
NSW1-QLD1 Import | #R021614_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021707_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021921_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R021955_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | Q::N_DM_CB_AR_2L-G | 0.083333 | 1.6667 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | Q^^CS_-080 | 0.083333 | 0 | Nominated Offset -80MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 1384.25 | 1021.25 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 646.1667 | 526.8333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 477.3333 | 468.25 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_QNV++MG_R6 | 73.75 | 0.25 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 64.5 | 53 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_T++LREG_0050 | 56.4167 | 17.9167 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_QNV++MG_R60 | 50.5833 | 2.5 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 45.5833 | 67.25 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_QNV++MG_R5 | 43.25 | 0.83333 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 35.75 | 45.9167 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
T-V-MNSP1 Export | T^V_NIL_9 | 34 | 18.5833 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | F_MAIN++RREG_0220 | 25.3333 | 11.6667 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++COGT_TL_L6 | 19.75 | 2 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | T^^V_GTSH_1 | 17.8333 | 2.75 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage
T-V-MNSP1 Export | TVBL_ROC | 15.5833 | 9.3333 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Export | F_MAIN++GFT_TG_R60 | 12.8333 | 0 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++COGT_TL_L5 | 12.3333 | 0.16667 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L60 | 11.4167 | 0.5 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | T^V_NIL_8 | 11.1667 | 4.3333 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 10.1667 | 4.3333 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | V>>V_ROTS_TX_2A_R | 10.0833 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | T_V_NIL_BL1 | 3.4167 | 5.5 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL
T-V-MNSP1 Export | F_MAIN++GFT_TG_R5 | 3.1667 | 0 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | T_V_FCSPS_RAMP | 1.9167 | 0 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage
T-V-MNSP1 Export | F_T++CO_752_TL_L6 | 1.8333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_MAIN++GFT_TG_R6 | 1.5833 | 0 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++CO_752_TL_L60 | 1.5833 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_VS++MG_R60 | 1.5 | 0 | Raise 60 sec requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_VS++MG_R6 | 1.4167 | 0 | Raise 6 sec requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++TG_R60_1000 | 1.3333 | 0 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>V_ROTS_TX_3A_R | 0.91667 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | F_VS++MG_R5 | 0.58333 | 0 | Raise 5 min requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++MG_R60_1000 | 0.5 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 1000, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_1 | 0.5 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | F_T++CO_752_TL_L5 | 0.5 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | #R020418_019_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 10/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R020418_019_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 10/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R020499_019_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 10/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R020719_029_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | F_QNV++RREG_0220 | 0.41667 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink able transfer FCAS | Outage
T-V-MNSP1 Export | T^V_HAPM_220_1 | 0.25 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage
T-V-MNSP1 Export | #R020422_019_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 10/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R020427_019_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 10/12/2018, Version: 1 | Other
T-V-MNSP1 Export | F_MAIN++MG_R5_1000 | 0.16667 | 0 | Raise 5 min Service Requirement for a Mainland Generation Event, MG = 1000, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++MG_R60_0850 | 0.16667 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++YW134_MGR6 | 0.16667 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | #T-V-MNSP1_RAMP_E_F | 0.083333 | 0 | T-V-MNSP1 >= MIN(0, InitialFlow + 200) (Wt=35) | Other
T-V-MNSP1 Export | F_MAIN++YW134_MGR5 | 0.083333 | 0 | Out= Nil, loss of Yallourn units 1, 3 and 4 declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T^^V_PMSH_1 | 0.083333 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of either one Sheffield to Georgetown 220kV line or one Hadspen to Georgetown 220kV line. | Outage
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 1040.4167 | 378.1667 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 686.1667 | 919.0833 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L6 | 351.6667 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V_T_NIL_FCSPS | 268.4167 | 819.5 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 206.3333 | 241.0833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++RREG_0050 | 91.3333 | 31.75 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0210 | 86 | 23 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | VT_ZERO | 60.5 | 27.9167 | Vic to Tas on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD_LD | 59.0833 | 0.16667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 51.5 | 11 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | V::N_HWSM_V2 | 38.75 | 48.1667 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_NILxxx | 33.5833 | 6.5833 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R5 | 32.5833 | 63.1667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_QNV++ML_L6_0400 | 32.3333 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++ML_L60_0400 | 29.4167 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 24.25 | 14.1667 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_ESTN_HYSE_VD | 23.75 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R60 | 22.1667 | 27.4167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | T::T_NIL_3 | 19.9167 | 15.9167 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL
T-V-MNSP1 Import | V::N_HWSM_V1 | 19.5 | 17.0833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 17.1667 | 33.6667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_HWSM_S1 | 17 | 0.91667 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
T-V-MNSP1 Import | V::N_ESTN_MLMOHG_V | 15.4167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage
T-V-MNSP1 Import | F_QNV++ML_L5_0400 | 14 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R6 | 13.9167 | 50 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V_T_NIL_BL1 | 11.8333 | 45.9167 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 11.75 | 4.8333 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_EPMB_V2 | 10.1667 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_EPMB_S2 | 10 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L60 | 9.5833 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | VTBL_ROC | 8.9167 | 9.5 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Import | V::N_DDSM_V2 | 8.5833 | 6.5833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_MLTX_V1 | 7.25 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S3 | 6.9167 | 0.33333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L6 | 6.8333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R60 | 6.3333 | 0.16667 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 6 | 15.4167 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 5.8333 | 4.5 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_QNV++MLTR_L6 | 5.25 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_V3 | 5.1667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 4.8333 | 12.4167 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | T::T_HA_GT_PM_4 | 4.5 | 5.3333 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Import | V::N_HWSM_SD | 3.9167 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_SMF2_V1 | 3.9167 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_QNV++LREG_0210 | 3.1667 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R6 | 3 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 2.5 | 0.33333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 2.4167 | 0.58333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R5 | 2.25 | 0.16667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 2 | 8.9167 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_MLTX_V2 | 1.9167 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_MLTX_S2 | 1.8333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_QNV++MLTR_L60 | 1.6667 | 2.4167 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T::T_NIL_2 | 1.6667 | 45.1667 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 1.5 | 0.91667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R5 | 1.5 | 0.58333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_ESTN_HYSE_QA | 1.5 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_MAIN++NIL_BL_L6 | 1.4167 | 0 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | F_QNV++APD_TL_L5 | 1.25 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++APD_TL_L60 | 1.25 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++APD_TL_L5 | 1.0833 | 0 | Lower 5 min requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R6 | 0.91667 | 0.58333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_VS++TL_L6_0600 | 0.91667 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_ESTN_HYSE_QD | 0.91667 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, QLD accelerates, segment 1 | Outage
T-V-MNSP1 Import | V::N_X_HWSM_HWRO_V2 | 0.91667 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L60_APD_L | 0.83333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++APD_TL_L60 | 0.83333 | 0 | Lower 60 sec requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++TL_L60_0600 | 0.83333 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_ESTN_HYSE_VA | 0.83333 | 2.25 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_QNV++HGML_L6 | 0.75 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++WIP_N-2_MLL6 | 0.66667 | 1 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++APD_TL_L6 | 0.66667 | 0 | Lower 6 sec requirement for a Vic and SA Network Event, TL=loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++TL_L6_0500 | 0.66667 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_X_HWSM_HWCB_V1 | 0.66667 | 0 | Out=Hazelwood-South Morang & Hazelwood-Cranbourne 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R020604_002_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | F_VS++TL_L5_0600 | 0.58333 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_X_ARWBBA_V1 | 0.58333 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R020681_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R020734_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R021010_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R021598_020_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V:T_SHGT_BL_1, Effective Date: 20/10/2014, Version: 1 | Other
T-V-MNSP1 Import | #R021598_020_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V:T_SHGT_BL_1, Effective Date: 20/10/2014, Version: 1 | Other
T-V-MNSP1 Import | #R021873_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_HWSM_HWCB_V1, Effective Date: 08/04/2020, Version: 1 | Other
T-V-MNSP1 Import | #R021883_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R021891_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | V:T_NIL_BL_1 | 0.41667 | 4.6667 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL
T-V-MNSP1 Import | #R020283_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 02/12/2019, Version: 1 | Other
T-V-MNSP1 Import | #R020607_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R021965_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint T::T_PMSH_2, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 0.33333 | 4.9167 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++TL_L5_0500 | 0.33333 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T_ROCOF_3 | 0.33333 | 0.25 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL
T-V-MNSP1 Import | V::N_MLTX_S1 | 0.33333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V:T_SHGT_BL_1 | 0.33333 | 0.91667 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | #R021885_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V:T_PMSH_BL_1, Effective Date: 20/10/2014, Version: 1 | Other
T-V-MNSP1 Import | #R022032_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ML_L5_APD_LD | 0.25 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++HGML_L60 | 0.25 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++TL_L60_0500 | 0.25 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 500, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++TL_L60_0550 | 0.25 | 0 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_MLTX_SD | 0.25 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_SMSC_S2 | 0.25 | 4.3333 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R020604_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R020607_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_EPMB_SD, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R020734_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R021856_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R021856_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R021965_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V:T_PMSH_BL_1, Effective Date: 20/10/2014, Version: 1 | Other
T-V-MNSP1 Import | #R022032_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | F_NVS++APD_TL_L6 | 0.16667 | 0 | Lower 6 sec requirement for a NSW, Vic and SA Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R5 | 0.16667 | 0.83333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 0.16667 | 0.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++GO_A752_TG_R5 | 0.16667 | 0 | Out= Gordon CB A752, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++NIL_BLSPS_R6_1 | 0.16667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
T-V-MNSP1 Import | F_VS++TL_L5_0550 | 0.16667 | 0 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_VS++TL_L6_0550 | 0.16667 | 0 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 550, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T::T_PMSH_2 | 0.16667 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_Q3 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_V1 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_DDSM_V1 | 0.16667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R020607_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R020607_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_SD, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R020681_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R021856_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R021873_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_HWSM_HWCB_V1, Effective Date: 08/04/2020, Version: 1 | Other
T-V-MNSP1 Import | #R021891_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R022032_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R022043_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R022086_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++APD_TL_L6 | 0.083333 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++HGML_L5 | 0.083333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L5 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++MLTR_L5 | 0.083333 | 0.16667 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++TL_L5_0600 | 0.083333 | 0 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++GO_A752_TG_R6 | 0.083333 | 0 | Out= Gordon CB A752, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++GO_A752_TG_R60 | 0.083333 | 0 | Out= Gordon CB A752, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S1 | 0.083333 | 1.1667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | V::N_X_HWSM_HWRO_S2 | 0.083333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V^^N_NIL_1 | 494.8333 | 160.75 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
V-S-MNSP1 Export | V^^N_HWSM_1 | 145.4167 | 0 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | S>NIL_MHNW1_MHNW2 | 123.6667 | 0 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL
V-S-MNSP1 Export | VSML_ROC_80 | 71.8333 | 31.5 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Export | V^^N_UTYS_1 | 65.5833 | 0 | Out = Upper Tumut to Yass (2) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | VSML_220 | 55.0833 | 3.5833 | Vic to SA on ML upper transfer limit of 220 MW | NIL
V-S-MNSP1 Export | V::N_ESTN_HYSE_VD | 53.3333 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V^^SML_NSWRB_2 | 49.75 | 58.9167 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL
V-S-MNSP1 Export | V::N_HWSM_V2 | 45.75 | 55.0833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | VSML_ZERO | 39.4167 | 33.1667 | Vic to SA on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 35.4167 | 47.5 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-S-MNSP1 Export | V^^N_X_MNYS_CNUT_1 | 27.9167 | 0 | Out = Canberra to Upper Tumut (01) and Marulan to Yass (4 or 5) 330kV lines, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 27.4167 | 9.0833 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | V^SML_BUDP_3 | 27.0833 | 42.5833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | F_S++ML_R5 | 25.9167 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA | Outage
V-S-MNSP1 Export | V::N_NILxxx | 25.8333 | 16.25 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-S-MNSP1 Export | V::N_HWSM_V1 | 23.5833 | 28.3333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | F_S++ML_R6_1 | 22.8333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA, Segment 1 | Outage
V-S-MNSP1 Export | V::N_HWSM_S1 | 17.5833 | 0.83333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-S-MNSP1 Export | V::N_ESTN_MLMOHG_V | 15.9167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage
V-S-MNSP1 Export | CA_BRIS_4D2AAD32_1 | 15.75 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG MVPB on trip of DDTS-SMTS1 &DDTS-SMTS2 330KV LINES. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage
V-S-MNSP1 Export | V^^N_MNYS_1 | 14.9167 | 0 | Out = Marulan to Yass (4 or 5) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V>>N-NIL_HA | 14.25 | 69.3333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
V-S-MNSP1 Export | V::N_DDSM_V2 | 10.9167 | 7.1667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V^^N_ESTN_MLMOHG_1 | 10.6667 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, avoid voltage collapse around Murray for loss of Basslink when Basslink exporting > 400MW to TAS, will swamp otherwise. | Outage
V-S-MNSP1 Export | V::N_EPMB_V2 | 10.5833 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 10.5833 | 4.1667 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-S-MNSP1 Export | V::N_EPMB_S2 | 10.3333 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | F_S++ML_R60 | 9.8333 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_S3 | 9.6667 | 0.41667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V3 | 9.4167 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V^SML_BEKG_4 | 7 | 0 | Out = Bendigo to Kerang 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage
V-S-MNSP1 Export | V^SML_ARWB_3 | 6.3333 | 10.5 | Out = Ararat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V^SML_BAWB_3 | 4.9167 | 26.75 | Out = Ballarat to Waubra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | VSML_-150 | 4.5833 | 0 | Vic to SA on ML upper transfer limit of -150 MW | Outage
V-S-MNSP1 Export | V^^N_X_DTSS_MNYS_1 | 4.25 | 0 | Out = Dapto to Sydney South (11) and Marulan to Yass (4 or 5) 330kV lines, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V^SML_KGRC_4 | 4.1667 | 4.9167 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage
V-S-MNSP1 Export | V::N_SMF2_V1 | 4.0833 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_MLTX_V1 | 3.9167 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>RBTX2_RBTX1_WEWT | 3.8333 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage
V-S-MNSP1 Export | V::N_HWSM_SD | 3.75 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V>>V_ARCW_7 | 3.75 | 0 | Out = Ararat to Crowlands 220kV line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | VSML_080 | 3.6667 | 0 | Vic to SA on ML upper transfer limit of 80 MW | Outage
V-S-MNSP1 Export | VSML_020 | 3.3333 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage
V-S-MNSP1 Export | S>>NIL_BWMP_BRTW | 3.1667 | 0 | Out= Nil, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_MLTX_S2 | 2.5 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_MLTX_V2 | 2.5 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | #V-S-MNSP1_I_E | 2.3333 | 0 | V-S-MNSP1. * -1 >= 0 (Wt = 360) | Other
V-S-MNSP1 Export | S>>DVBG_RBTU_WEWT | 2.3333 | 0 | Out= Davenport-Bungama 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>SMLMHNW1 | 1.9167 | 4.5833 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-S-MNSP1 Export | VSML_100 | 1.75 | 0 | Vic to SA on ML upper transfer limit of 100 MW | Outage
V-S-MNSP1 Export | S>>RB_275KV_S_BUS_10 | 1.5833 | 0 | Out= Robertstown 275kV South Bus(i.e. CBs 6572, 6575, 6148 & 6149 OPEN & Robertstown 275/132 TX2 O/S), avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX1 (this offloads North West Bend-Robertstown 132kV line). | Outage
V-S-MNSP1 Export | V::N_ESTN_HYSE_QA | 1.5 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
V-S-MNSP1 Export | V::N_X_ARWBBA_V1 | 1.5 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_HWCB_V1 | 1.3333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Cranbourne 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>NWCB6024+25_TX1 | 1.3333 | 0 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #1 132/66kV TX on trip of Monash-North West Bend #1 132kV line (this splits NWB 132kV bus), Feedback | Outage
V-S-MNSP1 Export | N>>N_65+66_N-2_5 | 1.1667 | 0.5 | Out= Nil, avoid O/L Wodonga to Jindera (060) on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL
V-S-MNSP1 Export | V::N_X_HWSM_HWRO_V2 | 1.1667 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | VSML_VFRB_OFF | 1.1667 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL
V-S-MNSP1 Export | #R020646_002_RAMP_F | 1 | 0 | Hard Ramping constraint for constraint V>SMLMHNW1, Effective Date: 17/05/2019, Version: 1 | Other
V-S-MNSP1 Export | S>>RBTX1_RBTX2_WEWT | 1 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage
V-S-MNSP1 Export | V^SML_HORC_2 | 1 | 9.3333 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage
V-S-MNSP1 Export | V^^N_CNUT_1 | 1 | 0 | Out = Canberra to Upper Tumut (01) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | VSML_010 | 0.91667 | 0 | Vic to SA on ML upper transfer limit of 10 MW | Outage
V-S-MNSP1 Export | #R021393_017_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V^SML_ARWB_3, Effective Date: 15/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021881_022_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | V::N_ESTN_HYSE_QD | 0.83333 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, QLD accelerates, segment 1 | Outage
V-S-MNSP1 Export | V^SML_HORC_3 | 0.83333 | 78 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | #R020283_015_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 02/12/2019, Version: 1 | Other
V-S-MNSP1 Export | S>>NIL_BWMP_TWPA | 0.66667 | 0.83333 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>RB_275KV_N_BUS_3 | 0.66667 | 0 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2 (this offloads NWB-RB #1 132kV line). | Outage
V-S-MNSP1 Export | V::N_ESTN_HYSE_VA | 0.66667 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>SML_NWRB_NWMWP1 | 0.66667 | 0 | Out=NWB - Robertstown 132kV #1 line, limit flow on ML to avoid OL North West Bend- MWP1 132 kV line. | Outage
V-S-MNSP1 Export | V>X_NWCB6022+6023_T1 | 0.66667 | 0 | Out = North West Bend 132 kV circuit breakers CB6022 and CB6023(Note: this takes out North West Bend-Monash #2 132kV line); limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB 132/66kV TX3. | Outage
V-S-MNSP1 Export | #R020604_002_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R021857_022_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021870_022_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021896_023_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | S>>NIL_TWPA_TPRS | 0.58333 | 0 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | #R021370_017_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R020283_015_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 02/12/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020336_029_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020439_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R020681_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R020734_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R021002_039_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R021010_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R021457_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R021864_022_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021873_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_HWSM_HWCB_V1, Effective Date: 08/04/2020, Version: 1 | Other
V-S-MNSP1 Export | #R021883_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021891_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | VSML_015 | 0.41667 | 0 | Vic to SA on ML upper transfer limit of 15 MW | Outage
V-S-MNSP1 Export | #R020607_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R020646_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>SMLMHNW1, Effective Date: 17/05/2019, Version: 1 | Other
V-S-MNSP1 Export | #R021004_016_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 13/01/2020, Version: 1 | Other
V-S-MNSP1 Export | #R021173_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R021361_017_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021864_022_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | N>>N_65+66_N-2_2 | 0.33333 | 7.4167 | Out= Nil, avoid O/L Dederang to Wodonga on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL
V-S-MNSP1 Export | S>>BRTW_RBTU_WTTP | 0.33333 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>BWMP_TWPA_TPRS | 0.33333 | 0.41667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_MLTX_S1 | 0.33333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | #R020530_025_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R021160_030_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R021229_037_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R021244_037_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R021361_017_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021521_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S>>BGBW_TWPA_TPRS, Effective Date: 02/10/2019, Version: 1 | Other
V-S-MNSP1 Export | #R022032_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | S>>BRTW_BWPA_WTTP | 0.25 | 0.16667 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_LT_UT_MS_S2 | 0.25 | 0 | Out = Lower Tumut - Murray (66) line or Upper Tumut - Murray (65) line, prevent transient instability for fault and trip of Upper Tumut - Murray (65) or Lower Tumut - Murray (66) line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | #R020336_029_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020530_025_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R020604_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R020607_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_EPMB_SD, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R020734_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R021002_039_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R021856_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021856_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021873_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_X_HWSM_HWCB_V1, Effective Date: 08/04/2020, Version: 1 | Other
V-S-MNSP1 Export | #R021875_022_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R022032_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | CA_BRIS_4D2AA9D0_1 | 0.16667 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG MVPB on trip of DDTS-SMTS1 &DDTS-SMTS2 330KV LINES. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WEWT | 0.16667 | 2.6667 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>X_RBTU+RB_SBUS_14 | 0.16667 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_Q3 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_DDSM_V1 | 0.16667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_SMSC_S2 | 0.16667 | 4.75 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V:SS_820_HY_TEST_DYN | 0.16667 | 0.5 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-S-MNSP1 Export | V>>N-X_MSUT_LTUT | 0.16667 | 0 | Out = Murray-Upper Tumut and Lower Tumut-Upper Tumut(65+64), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
V-S-MNSP1 Export | #R020607_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R020607_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_SD, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R020681_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R021357_017_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021843_039_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R021856_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021870_022_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021883_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021891_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R021904_023_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 04/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R022032_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R022086_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | N>>N-NIL_DPTX | 0.083333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V1 | 0.083333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_HWRO_S2 | 0.083333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_HWRO_V1 | 0.083333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>N-NIL_HG | 0.083333 | 15.1667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | V>>V_MLSY_4BR | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage
V-S-MNSP1 Import | SVML_ZERO | 908.8333 | 619.4167 | SA to Vic on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Import | N^^V_NIL_1 | 445.25 | 0 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
V-S-MNSP1 Import | S>V_NIL_NIL_RBNW | 285.5 | 403.8333 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | N^^N_NIL_2 | 141.4167 | 0 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL
V-S-MNSP1 Import | N^^V_NIL_YW134_N-2 | 127.25 | 0 | Out = Nil, avoid voltage collapse at Southern NSW for loss of Yallourn units 1, 3 and 4 when declared credible and are the largest contingency | NIL
V-S-MNSP1 Import | V>>V_NIL_9 | 114.3333 | 0.58333 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | N^^N_NIL_3 | 75.0833 | 0 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse for contingency trip of Bendigo-Kerang 220kV line in NW Victoria | NIL
V-S-MNSP1 Import | SVML_ROC_80 | 71.9167 | 27 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Import | SVML^NIL_160 | 51.75 | 0 | Out=NIL, SA to Vic on ML upper transfer limit of 160 MW to manage voltage collapse at Monash | NIL
V-S-MNSP1 Import | SVML_095 | 38.5833 | 0 | SA to Vic on ML upper transfer limit of 95 MW | Outage
V-S-MNSP1 Import | S>RBTX1_RBTX2_WEMWP4 | 31.25 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-MWP4 132kV line on trip of Robertstown 275/132kV TX2, | Outage
V-S-MNSP1 Import | V>>V_NIL_18 | 28.9167 | 0 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | N>>N_DPYC_99D_C_1 | 25.8333 | 0 | Out= Darlington Point to Yanco (99D) 132kV line.X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521, avoid O/L Darlington Point to Griffith (99K) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, Feedback | Outage
V-S-MNSP1 Import | S:VS_PA_SVC_570 | 23.1667 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage
V-S-MNSP1 Import | S>VMLMHNW1 | 22.0833 | 104.3333 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-S-MNSP1 Import | S>V_NWRB_RBMWP3 | 22.0833 | 9.3333 | Out=NWB - Robertstown 132kV #1 line, Limit Murraylink SA to Vic flow to avoid OL Robertstown-MWP3 132kV line. | Outage
V-S-MNSP1 Import | S>RB_275KV_N_BUS_1 | 12.5 | 18.25 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L Waterloo East-MWP4 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage
V-S-MNSP1 Import | V>>V_NIL_7 | 11.4167 | 0 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL
V-S-MNSP1 Import | F_S++ML_L6_1 | 10.25 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 1 | Outage
V-S-MNSP1 Import | S>>RBTX2_NIL_RBTX1 | 10.25 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Robertstown 275/132kV TX1 on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>NIL_NIL_NWMH2 | 10.25 | 77.3333 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL
V-S-MNSP1 Import | F_S++ML_L5 | 9.8333 | 0 | Lower 5 min Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
V-S-MNSP1 Import | N>>N_DPYC_99D_C_2 | 8.0833 | 0 | Out= Darlington Point to Yanco (99D) 132kV line.X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521, avoid O/L Griffith to Yanco (99J) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, Feedback | Outage
V-S-MNSP1 Import | S>>NIL_RBTX_RBTX_1 | 4.8333 | 0 | Out= Nil, avoid O/L of one Robertstown 275/132kV TX on trip of other Robertstown 275/132kV TX, Feedback | NIL
V-S-MNSP1 Import | SVML_FLT_150 | 4.4167 | 8 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage
V-S-MNSP1 Import | N>>N-NIL_DPTX_2 | 4.25 | 0.5 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
V-S-MNSP1 Import | S:VS_XPAVC_460 | 3.8333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood and Murraylink combined upper transfer limit of 460 MW based on oscillatory stability. | Outage
V-S-MNSP1 Import | SVML_FLT_125 | 3.75 | 0 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage
V-S-MNSP1 Import | V>>V_NIL_14 | 3.75 | 0 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | NRM_SA1_VIC1 | 3.25 | 0.083333 | Negative Residue Management constraint for SA to VIC flow | NIL
V-S-MNSP1 Import | S>>V_NIL_NIL_RBMW3 | 3.25 | 0 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | S>>X_RBTU+RB_SBUS_15 | 3.0833 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Import | S>>X_RBTU+RB_SBUS_16 | 2.8333 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage
V-S-MNSP1 Import | SVML_140 | 2.75 | 0 | SA to Vic on ML upper transfer limit of 140 MW | Outage
V-S-MNSP1 Import | F_S++ML_L6_2 | 2 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 2 | Outage
V-S-MNSP1 Import | CA_BRIS_4DE6DCA9_1 | 1.8333 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage
V-S-MNSP1 Import | CA_BRIS_4DE47816_1 | 1.75 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage
V-S-MNSP1 Import | S>>V_CGTI_PPPG_TIPA | 1.5833 | 0 | Out= Cherry Gardens - Torrens Island 275kV line, avoid O/L Torrens Island - Para 275kV line on trip of Pelican Point - Parafield Gardens West 275kV line, Feedback | Outage
V-S-MNSP1 Import | SVML_015 | 1.5 | 0 | SA to Vic on ML upper transfer limit of 15 MW | Outage
V-S-MNSP1 Import | S>X_NWCB6022+6023_T2 | 1.3333 | 0 | Out = North West Bend 132 kV circuit breakers CB6022 and CB6023(Note: this takes out North West Bend-Monash #2 132kV line); limit SA to Victoria flow on Murraylink to avoid North West Bend transformer #2 O/L on trip NWB 132/66kV Transformer #3. | Outage
V-S-MNSP1 Import | S:VS_700_HY_TEST_DYN | 1.0833 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-S-MNSP1 Import | #R021710_001_RAMP_F | 1 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | F_S++ML_L60 | 1 | 0 | Lower 60 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
V-S-MNSP1 Import | SVML_020 | 1 | 0 | SA to Vic on ML upper transfer limit of 20 MW | Outage
V-S-MNSP1 Import | SVML_120 | 0.91667 | 0.16667 | SA to Vic on ML upper transfer limit of 120 MW | Outage
V-S-MNSP1 Import | V>>V_ROTS_TX_3A_R | 0.91667 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
V-S-MNSP1 Import | #R021468_001_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | S>>V_NIL_NIL_RBNW1 | 0.83333 | 0 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_3 | 0.83333 | 7.25 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Import | #R021832_022_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint SVML_FLT_125, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | #R020439_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R021457_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | CA_BRIS_4DE45CFF_1 | 0.58333 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage
V-S-MNSP1 Import | S:VS_700_HY_TEST | 0.58333 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-S-MNSP1 Import | SVML_010 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 10 MW | Outage
V-S-MNSP1 Import | SVML_060 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 60 MW | Outage
V-S-MNSP1 Import | #R021173_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | CA_SYDS_4EBD234F_1 | 0.5 | 0 | Constraint Automation, O/L XFMR T_1@R_TOWN@SA for Nil Trip Base Case. Generated by STNET[BNECR2] Host NORREGEEMP3(EMPSYD) | Outage
V-S-MNSP1 Import | I_CTRL_ISSUE_ML | 0.5 | 0 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Import | SVML_080 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 80 MW | Outage
V-S-MNSP1 Import | SVML_100 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 100 MW | Outage
V-S-MNSP1 Import | #R020911_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #V-S-MNSP1_I_E | 0.41667 | 0 | V-S-MNSP1. * -1 >= 0 (Wt = 360) | Other
V-S-MNSP1 Import | #R021250_031_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_BUDP_6, Effective Date: 01/06/2020, Version: 1 | Other
V-S-MNSP1 Import | V>>V_BUDP_6 | 0.33333 | 5.5 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | #R021468_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R020911_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R021874_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>X_RBTU+RB_SBUS_15, Effective Date: 26/10/2020, Version: 2 | Other
V-S-MNSP1 Import | CA_BRIS_4DE6D9E8_1 | 0.16667 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP1(EMPBRI) | Outage
V-S-MNSP1 Import | S>>V_CGTI_TIPA_PGPA | 0.16667 | 0 | Out= Cherry Gardens - Torrens Island 275kV line, avoid O/L Parafield Gardens West-Para 275kV line on trip of Torrens Island A -Para 275kV line, Feedback | Outage
V-S-MNSP1 Import | S>NWCB6021+22_TX2 | 0.16667 | 0 | Out= North West Bend 132kV CBs 6021 and 6022(this offloads NWB TX1), avoid O/L North West Bend #2 132/66kV TX on trip of North West Bend-Robertstown #1 132kV line (this splits NWB 132kV bus), | Outage
V-S-MNSP1 Import | S>V_NWRB2_RBNW1 | 0.16667 | 9.9167 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage
V-S-MNSP1 Import | SVML_040 | 0.16667 | 0 | SA to Vic on ML upper transfer limit of 40 MW | Outage
V-S-MNSP1 Import | #R021002_033_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_BUDP_6, Effective Date: 01/06/2020, Version: 1 | Other
V-S-MNSP1 Import | #R021221_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S:VS_XPAVC_460, Effective Date: 07/08/2018, Version: 1 | Other
V-S-MNSP1 Import | #R022045_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>X_NWCB6022+6023_T2, Effective Date: 21/10/2019, Version: 1 | Other
V-S-MNSP1 Import | SVML_160 | 0.083333 | 0 | SA to Vic on ML upper transfer limit of 160 MW | Outage
V-SA Export | #V-SA_I_E | 250.25 | 0 | V-SA. * -1 = 30 (Wt = 360) | Other
V-SA Export | V_MLMO_VS_LB_CAN_50 | 132.4167 | 17.9167 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS/DUNDWF generating. | Outage
V-SA Export | SA_HYSE1 | 57.6667 | 2.1667 | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage
V-SA Export | V::N_HWSM_V2 | 50.5833 | 67.4167 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_ESTN++MLMO_L60 | 36.3333 | 13.5833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::N_NILxxx | 36 | 17 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-SA Export | V::N_ESTN_HYSE_VD | 26.6667 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
V-SA Export | V::N_HWSM_V1 | 25.0833 | 34.8333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V:S_600_HY_TEST | 17.5833 | 20.0833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL
V-SA Export | V::N_HWSM_S1 | 15.5833 | 0.75 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-SA Export | V:S_600_HY_TEST_DYN | 14.5833 | 11.4167 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-SA Export | VS_250_DYN | 12.8333 | 0 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage
V-SA Export | V::N_BYPASS_HW_SY_S3 | 11.5833 | 0.41667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V_S_NIL_ROCOF | 11.25 | 0.083333 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL
V-SA Export | V::N_EPMB_V2 | 10.75 | 0.91667 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_MLTX_V1 | 9.8333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_BYPASS_HW_SY_V3 | 9.3333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::N_EPMB_S2 | 9.3333 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V_S_HEYWOOD_UFLS | 7.6667 | 0 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC.Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL
V-SA Export | F_QNV++MLMO_L6 | 6.5833 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_HWSM_SD | 4.3333 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | S>>TBTU_TBCG_TBMO | 4.1667 | 0.16667 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | V::N_SMF2_V1 | 4.0833 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | F_ESTN++MLMO_L6 | 4 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | V_VS_LB_CAN_50 | 3.8333 | 43 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage
V-SA Export | F_ESTN++MLTR_L60 | 3.3333 | 15.6667 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_QNV++MLMO_L60 | 3.3333 | 0.083333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++MLTR_L6 | 3 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_MLTX_S2 | 2.5 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_MLTX_V2 | 2.5 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_ESTN++MLMO_L5 | 2.1667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | V::S_NIL_MAXG_xxx | 2.0833 | 4.4167 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V::N_X_HWSM_HWCB_V1 | 1.5833 | 0 | Out=Hazelwood-South Morang & Hazelwood-Cranbourne 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | S>>CGTB1_TBTU_TBMO | 1.5 | 0 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage
V-SA Export | V::N_X_ARWBBA_V1 | 1.5 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_KHKN_MAXG | 1.5 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | VS_250 | 1.5 | 0 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage
V-SA Export | F_QNV++MLTR_L60 | 1.4167 | 1.9167 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_ESTN_HYSE_QA | 1.25 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
V-SA Export | F_ESTN++MLTR_L6 | 1.0833 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | S_CGTB_TBMO_N-2_1 | 0.83333 | 0 | Out= NIL, avoid O/L Tailumbend-Tungkillo 275kV line on trip of Tailumbend-Cherry Gardens 275kV line and Tailem Bend-Mobilong 132kV lines, (Note: with both Black Range series caps I/S or O/S) | Outage
V-SA Export | F_QNV+MLMO_L60 | 0.75 | 4.5 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | DSNAP_V::S_NIL_MAXG1 | 0.66667 | 0 | DATASNAP NEVER TO BIND 10000 swamp; TESTING Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V_VS_MLMO_NETT | 0.66667 | 1.9167 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage
V-SA Export | #R020604_002_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | F_ESTN++MLTR_L5 | 0.58333 | 0.41667 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | V::N_ESTN_HYSE_QD | 0.58333 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, QLD accelerates, segment 1 | Outage
V-SA Export | V^^S_KHKN_SETB | 0.58333 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage
V-SA Export | #V-SA_RAMP_E_F | 0.5 | 0.083333 | V-SA <= MAX(25, InitialFlow - 30) (Wt=35) | Other
V-SA Export | V::N_ESTN_HYSE_VA | 0.5 | 1 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | #R020681_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R020734_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R021010_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R021787_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R021873_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_HWSM_HWCB_V1, Effective Date: 08/04/2020, Version: 1 | Other
V-SA Export | #R021883_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R021891_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R022032_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | F_ESTN++HGML_L60 | 0.41667 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_QNV+MLMO_L6 | 0.41667 | 0.083333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | #R020607_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R021856_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R022111_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | V::N_MLTX_S1 | 0.33333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_X_HWSM_HWRO_V2 | 0.33333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V^^S_MLSY_2 | 0.33333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage
V-SA Export | V^^S_PAVC1_MAXG | 0.33333 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | #R020607_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_EPMB_SD, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R020773_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S>>TBTU_TBCG_TBMO, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Export | #R021873_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_X_HWSM_HWCB_V1, Effective Date: 08/04/2020, Version: 1 | Other
V-SA Export | #R022111_009_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | F_QNV++HGML_L6 | 0.25 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_MLTX_SD | 0.25 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::N_SMSC_S2 | 0.25 | 4.75 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_PATU_MAXG | 0.25 | 1 | Out= Para - Tungkillo 275kV line(Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | #R020295_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R020604_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R020734_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R021787_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R021883_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R022043_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | F_ESTN++HGML_L5 | 0.16667 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | F_QNV+MLTR_L6 | 0.16667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+MLTR_L60 | 0.16667 | 0.83333 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | S>>NIL_TBTU_TBMO_1 | 0.16667 | 3.8333 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL
V-SA Export | V::N_BYPASS_HW_SY_Q3 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::N_BYPASS_HW_SY_V1 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V^^S_SEVC1_MAXG | 0.16667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | #R020297_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 16/09/2019, Version: 1 | Other
V-SA Export | #R020607_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_SD, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R020681_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R020773_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>TBTU_TBCG_TBMO, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Export | #R021856_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R021891_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R022032_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R022086_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | F_ESTN++HGML_L6 | 0.083333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | F_QNV++HGML_L60 | 0.083333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++MLMO_L5 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+MLMO_L5 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+MLTR_L5 | 0.083333 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_BYPASS_HW_SY_S1 | 0.083333 | 1.3333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V::N_X_HWSM_HWRO_S2 | 0.083333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_X_HWSM_HWRO_V1 | 0.083333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V>>V_MLSY_4BR | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage
V-SA Export | VS_050 | 0.083333 | 0.25 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage
V-SA Export | V^S_HYCP | 0.083333 | 0 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL
V-SA Export | V^^S_KHKN_MAXG | 0.083333 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Import | S:V_PA_SVC_420 | 363.5 | 5.5 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage
V-SA Import | F_S+MLMO_TL_L60 | 157.25 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
V-SA Import | SA_HYSE2 | 94.3333 | 1.8333 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage
V-SA Import | SV_420_DYN | 70.8333 | 0 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 36.9167 | 46.0833 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-SA Import | S:V_550_HY_TEST | 33.0833 | 0.58333 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | S:V_XPAVC_310 | 26.5 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage
V-SA Import | F_S++HYSE_L60 | 24.3333 | 226.6667 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
V-SA Import | F_S+MLMO_TL_L5 | 21.8333 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 5 min requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
V-SA Import | S:V_550_HY_TEST_DYN | 19 | 0.16667 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | V::N_DDSM_V2 | 10.9167 | 7.1667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Import | V>>V_KTS_TX_A2_2A_R | 10.8333 | 4.3333 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | V>>V_ROTS_TX_2A_R | 10.0833 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
V-SA Import | S>>CGTB1_TUTB_MOTB | 9.6667 | 0 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage
V-SA Import | F_S+MLMO_TL_L6_2 | 7 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage
V-SA Import | S:VS_PA_SVC_570 | 5.6667 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage
V-SA Import | V_SV_MLMO_NETT | 4.0833 | 102.4167 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW. Swamp out when MOPS/DUNDWF not generating | Outage
V-SA Import | NRM_SA1_VIC1 | 3.1667 | 0.16667 | Negative Residue Management constraint for SA to VIC flow | NIL
V-SA Import | F_S++HYSE_L6_1 | 2.8333 | 184.5 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
V-SA Import | #V-SA_RAMP_I_F | 2.0833 | 19.4167 | V-SA >= MIN(-155, InitialFlow + 50) (Wt=35) | Other
V-SA Import | F_S++HYSE_L5 | 2.0833 | 44.6667 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
V-SA Import | F_S+MLMO_TL_L6_1 | 2.0833 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage
V-SA Import | S>>V_CGTI_PPPG_TIPA | 1.5833 | 0 | Out= Cherry Gardens - Torrens Island 275kV line, avoid O/L Torrens Island - Para 275kV line on trip of Pelican Point - Parafield Gardens West 275kV line, Feedback | Outage
V-SA Import | S:V_PA_SVC_270 | 1.5 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage
V-SA Import | S:VS_700_HY_TEST_DYN | 1.3333 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | S:VS_XPAVC_460 | 1.0833 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood and Murraylink combined upper transfer limit of 460 MW based on oscillatory stability. | Outage
V-SA Import | #R021469_002_RAMP_F | 1 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | V>>V_ROTS_TX_3A_R | 1 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
V-SA Import | #R021038_004_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint S>>CGTB1_TUTB_MOTB, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | S:VS_700_HY_TEST | 0.75 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | #R020283_015_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 02/12/2019, Version: 1 | Other
V-SA Import | #R021046_004_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S>>CGTB1_TUTB_MOTB, Effective Date: 06/07/2020, Version: 1 | Other
V-SA Import | #R021221_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R021421_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R020283_015_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 02/12/2019, Version: 1 | Other
V-SA Import | #R022055_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | S>>NIL_CGTB_TUTB_1 | 0.41667 | 0 | Out= Nil, avoid O/L Tungkillo - Tailem Bend 275kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | NIL
V-SA Import | #R021038_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>CGTB1_TUTB_MOTB, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R021046_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>CGTB1_TUTB_MOTB, Effective Date: 06/07/2020, Version: 1 | Other
V-SA Import | #R022021_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R022021_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R020925_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>V_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Import | S>>V_CGTI_TIPA_PGPA | 0.16667 | 0 | Out= Cherry Gardens - Torrens Island 275kV line, avoid O/L Parafield Gardens West-Para 275kV line on trip of Torrens Island A -Para 275kV line, Feedback | Outage
V-SA Import | V::N_DDSM_V1 | 0.16667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Import | #R021043_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250_DYN, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R021758_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250_DYN, Effective Date: 13/03/2019, Version: 1 | Other
V-SA Import | #R021958_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>CGTB1_TUTB_MOTB, Effective Date: 06/07/2020, Version: 1 | Other
VIC1-NSW1 Export | V^^N_NIL_1 | 566 | 164.4167 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
VIC1-NSW1 Export | V^^N_HWSM_1 | 144.3333 | 0 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N^^N_NIL_3 | 86.1667 | 0 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse for contingency trip of Bendigo-Kerang 220kV line in NW Victoria | NIL
VIC1-NSW1 Export | V^^N_UTYS_1 | 76.6667 | 0 | Out = Upper Tumut to Yass (2) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_ESTN_HYSE_VD | 55.6667 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V::N_HWSM_V2 | 46.6667 | 67 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | N::N_CRGR_2 | 38 | 0 | Out = Crookwell to Gullen Range(3H), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 36.1667 | 48.1667 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
VIC1-NSW1 Export | V^^N_X_MNYS_CNUT_1 | 32.1667 | 0 | Out = Canberra to Upper Tumut (01) and Marulan to Yass (4 or 5) 330kV lines, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_NILxxx | 31.0833 | 16.8333 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
VIC1-NSW1 Export | V::N_HWSM_V1 | 25.3333 | 34.4167 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V^^N_MNYS_1 | 20.25 | 0 | Out = Marulan to Yass (4 or 5) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N::V_UTYS_2 | 19.5 | 0 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | V::N_HWSM_S1 | 17.9167 | 0.91667 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
VIC1-NSW1 Export | V::N_ESTN_MLMOHG_V | 17.5 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage
VIC1-NSW1 Export | CA_BRIS_4D2AAD32_1 | 15.8333 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG MVPB on trip of DDTS-SMTS1 &DDTS-SMTS2 330KV LINES. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage
VIC1-NSW1 Export | V>>N-NIL_HA | 15.6667 | 73.6667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
VIC1-NSW1 Export | N::N_BYCR_UTYS_2 | 15.4167 | 0 | Out = Upper Tumut -Yass(2) and Bannaby to Crookwell(61) , stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | VN_0450 | 12.0833 | 0 | Discretionary Vic to NSW transfer upper limit of 450 MW | Outage
VIC1-NSW1 Export | V^^N_ESTN_MLMOHG_1 | 11.6667 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, Mortlake and APD connected to SA, avoid voltage collapse around Murray for loss of Basslink when Basslink exporting > 400MW to TAS, will swamp otherwise. | Outage
VIC1-NSW1 Export | V::N_DDSM_V2 | 10.9167 | 7.1667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S3 | 10.5833 | 0.41667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V::N_EPMB_V2 | 10.5833 | 0.91667 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2A_R | 10.4167 | 4.0833 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | V::N_EPMB_S2 | 10.3333 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | VN_0500 | 10.3333 | 0 | Discretionary Vic to NSW transfer upper limit of 500 MW | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V3 | 9.9167 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>V_ROTS_TX_2A_R | 9.75 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V::N_MLTX_V1 | 9.6667 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | VN_0900 | 8.1667 | 0 | Discretionary Vic to NSW transfer upper limit of 900 MW | Outage
VIC1-NSW1 Export | N::N_UTYS_2 | 7.4167 | 0 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | NQ_VST_ISLE_A | 6.25 | 0 | Separation between Vic and NSW, allow Vic-NSW to supply Wagga or Northern Victoria | Outage
VIC1-NSW1 Export | V^^N_X_DTSS_MNYS_1 | 5.0833 | 0 | Out = Dapto to Sydney South (11) and Marulan to Yass (4 or 5) 330kV lines, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | VN_1100 | 4.75 | 0 | Discretionary Vic to NSW transfer upper limit of 1100 MW | Outage
VIC1-NSW1 Export | V>>N-JNWG_RADIAL_1 | 4.3333 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Export | V::N_SMF2_V1 | 4.0833 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HWSM_SD | 3.9167 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | N::N-X_MNYS_CNLT_2 | 3.5833 | 0 | Out= Marulan-Yass (4 or 5) and Canberra to Lower Tumut (07) or Upper Tumut (01) 330kV line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage
VIC1-NSW1 Export | VN_0500_DYN | 3.5833 | 0 | VIC to NSW interconnector upper transfer limit of 500 MW, dynamic headroom, DS formulation only. | Outage
VIC1-NSW1 Export | VN_0800 | 3.5833 | 0 | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage
VIC1-NSW1 Export | N>>N-NIL_DPTX_2 | 3.4167 | 0.58333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
VIC1-NSW1 Export | VN_1000 | 3 | 0 | Discretionary Vic to NSW transfer upper limit of 1000 MW | Outage
VIC1-NSW1 Export | V::N_MLTX_S2 | 2.5 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_MLTX_V2 | 2.5 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | VN_0900_DYN | 2.25 | 0 | VIC to NSW interconnector upper transfer limit of 900 MW, dynamic headroom, DS formulation only. | Outage
VIC1-NSW1 Export | VN_0700 | 2 | 0 | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage
VIC1-NSW1 Export | VN_0800_DYN | 1.8333 | 0 | VIC to NSW interconnector upper transfer limit of 800 MW, dynamic headroom, DS formulation only. | Outage
VIC1-NSW1 Export | N::N_MNYS_2 | 1.6667 | 0 | Out= Marulan-Yass (4 or 5), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage
VIC1-NSW1 Export | N>>N-NIL_01N | 1.5833 | 0 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL
VIC1-NSW1 Export | V::N_X_HWSM_HWCB_V1 | 1.5833 | 0 | Out=Hazelwood-South Morang & Hazelwood-Cranbourne 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_X_ARWBBA_V1 | 1.5 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_ESTN_HYSE_QA | 1.4167 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
VIC1-NSW1 Export | N>>N-WGYS_OPEN_4 | 1.1667 | 0 | Out = Wagga-Yass 132 kV Parallel lines Opened, avoid O/L Lower Tumut to Canberra (07) on trip of Lower Tumut to Yass (3) line, Feedback | Outage
VIC1-NSW1 Export | N>>N_65+66_N-2_5 | 1.1667 | 0.5 | Out= Nil, avoid O/L Wodonga to Jindera (060) on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL
VIC1-NSW1 Export | V::N_X_HWSM_HWRO_V2 | 1.1667 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | VN_1000_DYN | 1.0833 | 0 | VIC to NSW interconnector upper transfer limit of 1000 MW, dynamic headroom, DS formulation only. | Outage
VIC1-NSW1 Export | V>>V_ROTS_TX_3A_R | 1 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V^^N_CNUT_1 | 1 | 0 | Out = Canberra to Upper Tumut (01) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_ESTN_HYSE_VA | 0.91667 | 2.25 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V::N_ESTN_HYSE_QD | 0.83333 | 0 | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, QLD accelerates, segment 1 | Outage
VIC1-NSW1 Export | #R020283_015_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 02/12/2019, Version: 1 | Other
VIC1-NSW1 Export | #R021632_027_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V^^N_X_DTSS_MNYS_1, Effective Date: 09/10/2020, Version: 1 | Other
VIC1-NSW1 Export | VN_1100_DYN | 0.66667 | 0 | VIC to NSW interconnector upper transfer limit of 1100 MW, dynamic headroom, DS formulation only. | Outage
VIC1-NSW1 Export | #R020604_002_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | VN_ZERO | 0.58333 | 0 | VIC to NSW upper transfer limit of zero MW | Outage
VIC1-NSW1 Export | N::N_CNSD_2 | 0.5 | 0 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | VN_0700_DYN | 0.5 | 0 | VIC to NSW interconnector upper transfer limit of 700 MW, dynamic headroom, DS formulation only. | Outage
VIC1-NSW1 Export | #R020283_015_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 02/12/2019, Version: 1 | Other
VIC1-NSW1 Export | #R020681_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R020734_006_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R021004_016_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 13/01/2020, Version: 1 | Other
VIC1-NSW1 Export | #R021010_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R021873_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_HWSM_HWCB_V1, Effective Date: 08/04/2020, Version: 1 | Other
VIC1-NSW1 Export | #R021883_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R021891_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R020607_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | N>>N_65+66_N-2_2 | 0.33333 | 7.5 | Out= Nil, avoid O/L Dederang to Wodonga on trip of Lower Tumut to Murray (66) and Upper Tumut to Murray (65) lines, Feedback | NIL
VIC1-NSW1 Export | V::N_MLTX_S1 | 0.33333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | #R021873_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_X_HWSM_HWCB_V1, Effective Date: 08/04/2020, Version: 1 | Other
VIC1-NSW1 Export | #R022032_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | N^^N_NIL_1 | 0.25 | 0.16667 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL
VIC1-NSW1 Export | V::N_LT_UT_MS_S2 | 0.25 | 0 | Out = Lower Tumut - Murray (66) line or Upper Tumut - Murray (65) line, prevent transient instability for fault and trip of Upper Tumut - Murray (65) or Lower Tumut - Murray (66) line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_MLTX_SD | 0.25 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | #R020604_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R020607_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_EPMB_SD, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R020734_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R021856_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R021856_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R022032_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R022043_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | CA_BRIS_4D2AA9D0_1 | 0.16667 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG MVPB on trip of DDTS-SMTS1 &DDTS-SMTS2 330KV LINES. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_Q3 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V1 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_DDSM_V1 | 0.16667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_SMSC_S2 | 0.16667 | 4.75 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-X_MSUT_LTUT | 0.16667 | 0 | Out = Murray-Upper Tumut and Lower Tumut-Upper Tumut(65+64), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
VIC1-NSW1 Export | VN_0650 | 0.16667 | 0 | Discretionary Vic to NSW transfer upper limit of 650 MW | Outage
VIC1-NSW1 Export | #R020607_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_EPMB_S2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R020607_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_EPMB_SD, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R020681_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R021856_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R021883_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R021891_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R022032_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_S3, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R022086_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL__H_15M | 0.083333 | 0.25 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL
VIC1-NSW1 Export | NRM_VIC1_NSW1 | 0.083333 | 11.9167 | Negative Residue Management constraint for VIC to NSW flow | NIL
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S1 | 0.083333 | 1.3333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V::N_X_HWSM_HWRO_S2 | 0.083333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_X_HWSM_HWRO_V1 | 0.083333 | 0 | Out=Hazelwood-South Morang & Hazelwood-Rowville 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HG | 0.083333 | 15.4167 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Import | N^^V_NIL_1 | 534.75 | 2056.9167 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
VIC1-NSW1 Import | N^^V_NIL_YW134_N-2 | 127.6667 | 0 | Out = Nil, avoid voltage collapse at Southern NSW for loss of Yallourn units 1, 3 and 4 when declared credible and are the largest contingency | NIL
VIC1-NSW1 Import | N^^V_DDSM1 | 74 | 32.8333 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage
VIC1-NSW1 Import | N^^V_NIL_ARWBBA | 38.9167 | 0 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 22 | 2.75 | Negative Residue Management constraint for NSW to VIC flow | NIL
VIC1-NSW1 Import | N^^V_CNCW_1 | 19.1667 | 16.3333 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_BUDP_1 | 15.5 | 35.1667 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | NV_0500 | 4.5833 | 0 | Discretionary NSW to Vic transfer upper limit of 500 MW | Outage
VIC1-NSW1 Import | N^^V_SMTXF2_1 | 4.1667 | 11.1667 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_DDWG | 2.5 | 0.66667 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_MSDD2 | 2.0833 | 0 | Out = Dederang to Murray 330 kV line, avoid voltage collapse at Darlington Point for loss of the remaining Dederang to Murray 330 kV line | Outage
VIC1-NSW1 Import | V::V_1900 | 1 | 0 | Out=Nil, upper limit into Vic of 1900 MW | NIL
VIC1-NSW1 Import | V>>V_NIL_3 | 0.83333 | 6.6667 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Import | #R021160_011_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | NQ_VST_ISLE_B | 0.66667 | 0 | Separation between Vic and NSW, allow Vic-NSW to supply Wagga or Northern Victoria | Outage
VIC1-NSW1 Import | #R020492_004_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^V_MSDD1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | N::V_DDMS | 0.58333 | 0 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage
VIC1-NSW1 Import | #R021253_013_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^V_DDWG, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021150_011_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021706_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021027_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021059_021_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021160_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021340_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021715_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | N::V_MNYS_MSDD | 0.25 | 0 | Out=Marulan-Yass(4 or 5), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
VIC1-NSW1 Import | NV_ZERO | 0.25 | 0 | NSW to VIC upper transfer limit of zero MW | Outage
VIC1-NSW1 Import | #R020506_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_MSDD2, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R020506_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_MSDD2, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021052_019_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021052_019_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021065_021_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021150_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021253_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_DDWG, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021706_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021715_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021843_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DDWG, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R020492_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_MSDD2, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R020530_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021059_021_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R021065_021_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | N>>N-NIL_DPTX | 0.083333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL
VIC1-NSW1 Import | N>>V-NIL_0X1 | 0.083333 | 0 | Out= NIL, avoid O/L Buronga to Redcliff (OX1) on Nil trip, Feedback | NIL
VIC1-NSW1 Import | V>>V_EPTT_1 | 0.083333 | 0 | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to South) for loss of the parallel line, feedback | Outage

## Outages
Constraint Set ID | 2020 Days | 2019 Days | Description
N-MBTE_1 | 333.1493 | 187.2778 | Out= one Directlink cable
V-MURRAWRWF_WT_MW | 240.7604 | 40.4549 | Limit MW output of Murra Warra wind farm to hold point levels during day/night
S-PA_VC1 | 162.1701 | 4.4722 | Out= One Para SVC , (Note: with both Black Range Series caps I/S)
N-X_MBTE_2 | 144.6354 | 27.6007 | Out= two Directlink cables
V-YENDONWF_WT_MW | 140.7188 | 7.5556 | Limit MW output of Yendon wind farm to hold point levels during day/night
N-STWF1_WT_MW | 139.7917 | 365 | Limit number of turbines online and upper MW for Silverton wind farm
F-T-GTTE | 114.7465 | 15.75 | Out = one George Town to Temco 110kV line OR loss of both Georgetown to Temco 110 kV lines or all Temco load declared credible
N-LS_VC1 | 97.7049 | 9.4514 | Out= Lismore SVC
V-HWSM | 83.1806 | 51.7535 | Outage = Hazelwood to South Morang 500kV line
Q-PWSP_808 | 77.9167 | 0.045139 | Out= 808 H2 South Pine to H9 Palmwoods 275 kV feeder (132 and 110 kV parallel between South Pine and Woolooga closed)
N-MUTW_88 | 59.1007 | 0 | Out = Muswellbrook to Tamworth (88) line
Q-SSRV_T | 52.0556 | 0 | Temporary derating of Susan River feeder M020/3
N-UTYS_2 | 51.8299 | 1.9167 | Out= Upper Tumut to Yass (2)
S-X_DVBR+BRTW+TWPA | 50.9479 | 14.1979 | Out= Davenport-Brinkworth 275kV line + Brinkworth-Templers West 275kV line (this offloads Brinkworth TX) + Templers West - Para 275kV line
S-CGTI | 50.2083 | 36.9653 | Out= Torrens Island to Cherry Gardens 275kV line
N-PKWL_94K | 48.1562 | 0 | Out = Parkes to Wellington (94K) 132kV line
I-SVML_095 | 48.0312 | 0 | SA to Vic on ML upper transfer limit of 95 MW
S-PATU | 43.5938 | 26.6215 | Out = Para to Tungkillo 275 kV line(Note: with both Black Range series caps I/S)
I-ML_ZERO | 41.1007 | 24.9479 | Limit Murraylink to zero in either direction
N-BU-SCON2-3 | 40.5799 | 0 | Out= Buronga Syncon 2-3, SCON2 and SCON3 are associated with Darlington Point SF
V-MLTX_A2_R | 39.0035 | 6.6215 | Out= Moorabool A2 500/220kV transformer, Radial Mode
Q-MKG_0 | 35.5799 | 20.941 | Discretionary, Mackay GT =< 0MW
N-X_MBTE_3 | 34.0382 | 7.3507 | Out= all three Directlink cables
V-BANNERT_50P_RISK | 25.7847 | 0 | System normal system strength. Limit Bannerton SF to 50% (both MW and inverter)
Q-YLMR_733/1_734/1 | 25.1736 | 0 | Out=733/1 or 734/1 (T10 Yarranlea to H14 Middle Ridge) 110kV
S-DVTX | 23.4132 | 7.8889 | Out= One Davenport 275/132kV TX O/S
N-CLDP_99T | 22.4583 | 0.125 | Out = Coleambally to Darlington Point (99T) 132kV line
S-BRDV | 22.125 | 10.5347 | Out = Brinkworth - Davenport 275 kV line
S-KHKN | 21.8611 | 6.0035 | Out = Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S)
F-I_ML_APD_LOAD | 20.0799 | 0.020833 | Out=Nil, Dynamic FCAS for APD Load Event, excluding Portland WF
F-ESTN_ISLE | 17.4826 | 0.19792 | Eastern separation between Heywood and South East (HYTS - SESS) - FCAS Requirements
F-SA_ESTN_ISLE_REG | 17.4826 | 0.19792 | SA / Eastern separation between Heywood and South East (HYTS - SESS) - Regulation FCAS Requirements
SA_ESTN_ISLE | 17.4757 | 0.19792 | SA / Eastern separation between Heywood and South East (HYTS - SESS)
F-SA_MOPS_ISLE | 17.4757 | 0 | SA separation between Heywood and Moorabool (HYTS - MLTS), with Mortlake generator connecting to SA - FCAS Requirements
V-MACARTHUR_ZERO | 17.4688 | 3.0833 | Macarthur Wind Farm upper limit of 0 MW
N-DPYC-99D-C | 16.3611 | 1.3299 | Out = Darlington Point to Yanco (99D) 132kV line. X5 trip scheme disarmed and Wagga to Darlington Point 132kV network solid, option C on OM521
V-ROTX_R | 15.9583 | 0 | Outage = Rowville 500/220kV (A) transformer, Radial
V-MLMO | 14.8785 | 7.2014 | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN
S-X-RBTX1+6616+6573 | 14.1736 | 0 | Out =Robertstown 275/132kV TX1 AND Robertstown 275kV CBs 8089, 6616 AND 6573 (Note:with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S)
S-BGDV | 11.625 | 7.625 | Out= Davenport-Bungama 275kV line, (i.e. with Blyth West CB8001 OPEN & Blyth West trip scheme I/S)
Q-BCNE_821 | 11.1181 | 0 | Out = 821 275kV fdr H10 Bouldercombe - H11 Nebo
V-EPMB | 10.5 | 1.5938 | Outage = Eildon to Mt Beauty 220kV line
S-X-RBTX2+6572+6575 | 10.5 | 0 | Out= Robertstown 275/132 TX2 and Robertstown CBs 8090, 6572 & 6575 O/S ONLY (NOTE: with MLK runback scheme I/S & MLK sever scheme I/S or O/S)
T-SHWI | 9.4549 | 0 | Out=Sheffield-Wilmot 220KV line
S-BGTX | 9.375 | 0 | Out = Bungama 275/132kV transformer O/S
Q-X_CPGG1_GGWO1 | 9.3576 | 11.2743 | Out= 813 (H67 Calliope River to H6 Gin Gin) and 815 (H6 Gin Gin to H5 Woolooga) 275kV lines
Q-WUBI | 8.816 | 31.5278 | Out= 865 or 866 H40 Wurdong to H8 Boyne Island 275kV feeder, CQ-SQ voltage stability limit, 2008/2009 implementation
V-KGTS_SVC | 8.7222 | 1.1597 | Out = Kerang 220kV SVC
I-VS_250 | 8.5139 | 2.5 | Victoria to SA on VicSA upper transfer limit of 250 MW
I-VS_050 | 8.5035 | 22.6146 | Victoria to SA on VicSA upper transfer limit of 50 MW
N-CNUT_01 | 8.5035 | 2.1806 | Out= Canberra to Upper Tumut (01) line
N-X_MNYS5_CNUT | 8.3021 | 0 | Out= One Marulan-Yass (4 or 5) and Canberra to Upper Tumut (01) 330kV lines
V-SMSC | 8.2882 | 7.809 | Outage = one South Morang 330kV series capacitor
I-MUTE_757 | 8.2465 | 0.67014 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line
Q-CPWO_814 | 8.2153 | 0 | Out = H67 Calliope River to H5 Woolooga 275kV line (814) feeder
V-KTTX_A2_OR_A4_R | 8.0451 | 17.9826 | Outage = Keilor 500/220kV A2 or A4 transformer, Radial
Q-CPWO_BI_INTACT | 7.8299 | 0 | Out= 813 or 814, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines for Boyne Island bus is intact, Feedback
Q-X_BCNE_BC275BUS | 7.4132 | 0 | Out = 821 (H10 Bouldercombe - H11 Nebo) and (one 275kV bus or one 275kV CB at Bouldercombe (CB 8202,CB 8112,CB 8482,CB 8122))
I-MUTE_758 | 7.3958 | 0.1875 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line
Q-H11NE_SVC | 7.0174 | 3.0069 | Out= H11 Nebo SVC OOS
V-BANNERT_0P_TEST | 6.9965 | 0 | West Murray (NW VIC) Solar Farm testing constraints. Limit Bannerton Solar farm output to 0% (0 MW)
V-DDSM | 6.9306 | 3.1042 | Out = Dederang to South Morang (DDTS-SMTS) 330 kV line
S-PGPP | 6.8056 | 2.4097 | Out= Parafield Gardens West-Pelican Point 275kV line(with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S).
F-T-COGT | 6.691 | 0.20833 | Out = one Comalco to George Town 220kV line OR loss of both Comalco to Georgetown 220 kV lines or all Comalco potlines declared credible
S-BRTW | 6.309 | 6.4722 | Out= Brinkworth- Templers West 275kV line
S-SE_VC1 | 6.0486 | 4.7569 | Out= Either one of South East SVC O/S (Note: with both Black Range series caps I/S)
N-BU-SCON1 | 5.9826 | 0 | Out= Buronga Syncon 1, SCON1 is associated with Finley SF
S-MHNW_1 | 5.9583 | 28.9618 | Out = Monash to North West Bend line 1, (Note: Murraylink runback scheme can be I/S or O/S)
Q-CMTX | 5.9167 | 0 | Out = Clermont T1 or T2 132/66 kV transformer
N-LDTW_84 | 5.3889 | 0 | Out = Liddell to Tamworth (84) 330kV line
Q-BS_275_CB_3 | 5.2014 | 0 | Out = one or more 275kV CB (CB88312 or CB88472)at H20 Broadsound
S-RB_275KV_N_BUS | 5.1944 | 11.1042 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, CBs 8089, 6616, 6573, 6005 and 6188 O/S) (Note:with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S)
T-GTSH | 5.1562 | 1.0938 | Out = One George Town to Sheffield 220kV line
V-EPTT_R | 4.8785 | 0 | Outage = Eildon to Thomastown 220kV line, Radial
Q-BSLV_SMVC | 4.5521 | 0 | Out = 833 or 850 H20 Broadsound - H15 Lilyvale 275kV line, with Strathmore SVC is taken out of service
S-RB_275KV_S_BUS | 4.4062 | 8.2188 | Out= Robertstown 275kV South Bus (i.e. CBs 8090, 6572, 6575, 6148 & 6149 OPEN and Robertstown 275/132 TX2 O/S).
Q-ISHW_M022 | 4.4062 | 0 | Out = M022 (T131 Isis to Howard Tee Childer SF) 66kV feeder
N-GITN_96R | 4.3194 | 1.3958 | Out= Glen Innes to Tenterfield (96R) line
S-NWRB | 4.309 | 3.2917 | Out= Robertstown-North West Bend #1 132kV line
S-WT_S_BUS | 4.2743 | 1.2222 | Out= Waterloo 132kV South bus O/S (Note: WITH/WITHOUT associated bus CBs I/S)
V-SMTS_BYPASS_HW_SY | 4.2535 | 0.88194 | Outage = SMTS 500kV bus or CB outages or SMTS bus bypass that creates risk of HWTS-SMTS and SMTS-SYTS combined line trip, Radial or Parallel
S-SE_132KV_BUS | 4.2326 | 0 | Out = ONLY One South East 132 kV bus (i.e. either East or West 132kV bus WITH/WITHOUT associated CBs)
Q-ISTX | 4.1528 | 0 | Out = Isis T2 132/66 kV transformer
N-CHLS_89 | 4.1354 | 0.30208 | Out= Coffs Harbour - Lismore (89) 330kV line
S-SE_TX_1 | 4.1319 | 4.0799 | Out = One South East 275/132kV transformer (NOTE: associated CBs I/S)
N-ARTW_86 | 4.1215 | 0.82986 | Out = Armidale to Tamworth (86) line
V-X_HWSM_HWRO3 | 3.9583 | 0.11458 | Out = One Hazelwood to South Morang and Hazelwood to Rowville 500kV lines
S-X_PA_VC_2 | 3.3021 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S)
S-HUBG | 3.2951 | 4.3472 | Out= Hummocks-Bungama 132kV line (Note: this offloads Snowtown WF)
Q-X_RSCH_CHWR | 3.2951 | 0 | Out= 857 or 858 (H13 Ross to H32 Chalumbin) and 877(H32 Chalumbin to H39 Woree) 275kV line
T-PMSH | 3.1806 | 0 | Out = Palmerston to Sheffield 220kV line
N-LSLS_9U8 | 3.1424 | 17.6146 | Outage= 9U8 or 9U9 or 9W1 132kV line
S-DVLK | 3.1215 | 3.0035 | Out = Davenport-Mt Lock 275kV line (Note:both Black Range series capacitors I/S)
N-AR_CP2 | 2.9653 | 2.4722 | Out = Armidale Capacitor Bank (120 MVAr)
Q-LVTX_SMVC | 2.9653 | 0 | Out = Lilyvale 275/132 kV Transformer T1 or T2, with Strathmore SVC is taken out of service
Q-X-BSLV_BCNE_BC_BUS | 2.9618 | 0 | Out = H20 Broadsound - H15 Lilyvale 275 kV feeder (850 or 833) or one Lilyvale 275kV transformer and Nebo - Bouldercombe feeder (821) and one H10 Bouldercombe Bus, Strathmore SVC is taken out of service
V-MLSY_NOEMTT_R | 2.9583 | 3.1146 | Out = One Moorabool to Sydenham 500 kV line, EMTT scheme not armed, Radial mode
N-DPWG_63_X5 | 2.7326 | 1.8715 | Out = Darlington Point to Wagga (63) 330kV line + line X5 opened
N-ARCH_87 | 2.7292 | 0 | Out= Armidale - Coffs Harbour (87) 330kV line
N-CLDE_99L_C | 2.5382 | 0.46875 | Out= Coleambally to Deniliquin(99L) 132kV line; X5 Trip Scheme Disarmed, 132 kV parallel Solid, option c OM521
I-BL_ZERO | 2.5174 | 1.1632 | Limit Basslink to zero in either direction
F-T-CSGO | 2.4618 | 0.56944 | Out = one Chapel St to Gordon 220kV line, FCAS Requirements
N-STWF1_ZERO | 2.4271 | 4.3299 | Silverton wind farm upper limit of 0 MW
N-X_BYCR_UTYS | 2.3299 | 0 | Out= Bannaby to Crookwell (61) and Upper Tumut to Yass (2) 330kV lines
N-AR_VC1 | 2.3229 | 1.5729 | Out = Armidale SVC
S-HUWT | 2.1562 | 1.7847 | Out= Hummocks-Waterloo 132kV line
V-YENDONWF_ZERO | 2.0833 | 0 | Yendon Wind Farm upper limit of 0 MW
Q-HASMME_ZERO | 2.0208 | 0 | Discretionary upper limit of 0MW on Haughton Solar Farm, Sun Metal Solar Farm and Mt Emerald Windfarm
I-NV_0500 | 2.0174 | 0 | Discretionary NSW to Vic transfer limit 500
V-BEKG | 2 | 0 | Outage = Bendigo to Kerang 220kV line
N-BWSW_32 | 1.9931 | 3.3368 | Out= Bayswater - Sydney West (32) 330kV line
S-PA_VC1_BC-2CP | 1.9236 | 0.71528 | Out= One Para SVC (Note: with both Black Range series caps O/S)
N-GUNNING1_ZERO | 1.9132 | 0.54861 | Gunning unit upper limit of 0 MW
V-MLTX_A1_R | 1.8958 | 2.3264 | Out= Moorabool A1 500/220kV transformer, Radial Mode
I-JNWO_RADIAL | 1.8715 | 0.77431 | Out = Jindera to Wodonga (060) line, Wagga-Yass 132kV network Split, X5 opened, 63 deenergised and with 2 Yass Transformer in service, OM521
V-DDMS | 1.8333 | 0 | Out = One Dederang - Murray (67 or 68) 330 kV line
N-CROOKWF2_ZERO | 1.8125 | 0.28819 | Crookwell wind farm upper limit of 0 MW
S-WIWG | 1.7986 | 0.22222 | Out = Willalo - Willogoleche 275kV line (i.e. Willogoleche WF <=0 MW)
Q-YL_CB4412 | 1.7257 | 0 | Out = T10 Yarranlea 110kV CB 4412
T-FAJB | 1.6736 | 0.11111 | Out=Farrell-John Butters 220KV line
V-ARARAT_ZERO | 1.5278 | 0.23958 | Ararat Wind Farm upper limit of 0 MW
N-TARALGAWF_ZERO | 1.4826 | 0.49306 | Taralga WF upper limit of 0 MW
V-MTMERCER_ZERO | 1.4618 | 3.7986 | Mt Mercer Windfarm upper limit of 0 MW
N-X_WGYS_132_OPEN | 1.4444 | 1.1493 | Wagga-Yass 132 kV Parallel lines Opened
S-BRBG | 1.4271 | 0 | Out = Brinkworth to Redhill to Bungama 132kV lines (Note: outage also takes out Clements Gap Windfarm).
V-AR_WB_BA | 1.3854 | 2.4861 | Out = Ararat to Waubra to Ballarat 220kV lines OR any 220kV line section between Ballarat and Ararat. Waubra wind farm disconnected/off
F-T-CO_CB752 | 1.3854 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard
S-NWBCB6024+6025 | 1.3715 | 1.3438 | Out= North West Bend 132kV CBs 6024 and 6025(this offloads NWB TX2), (Note: for Murraylink runback scheme I/S or O/S and Sever scheme I/S or O/S)
S-WIMK | 1.3681 | 2.4167 | Out= Willalow-Mokota 275kV line (Note: WITH/WITHOUT associated line CBs I/S); (Note: with both Black Range series caps I/S)
Q-X-BCNE_BC_BUS | 1.3611 | 0 | Out = 821 (H10 Bouldercombe - H11 Nebo) 275kV Fdr and H10 Bouldercombe Bus
V-KG_WE_RC | 1.3507 | 1.1111 | Outage = Kerang to Wemen to Red Cliffs 220 kV line section, entire line section
V-HO_MR_KM | 1.3021 | 0 | Out = Horsham to Murra Warra to Kiamal 220kV line
I-BCDM_ONE | 1.2986 | 0.79861 | Out = one Bulli Creek to Dumaresq (8L or 8M) line
Q-SPL_TX_2 | 1.2986 | 0 | Out= Springlands (TX2) 132/33kV transformer
V-HYTR | 1.2604 | 3.3681 | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line
Q-H13RS_SVC | 1.2604 | 3.3611 | Out= H13 Ross 275 kV SVC
N-TAPM_964 | 1.2569 | 7.9722 | Out = Taree to Port Macquarie (964) 132kV line
Q-MIMR_9907_9908 | 1.2465 | 0 | Out= 9907 or 9908 R4 Millmerran to H14 Middle Ridge 330kV feeder, or H14 Middle Ridge 330/275 kV #4 or #5 transformer
V-WEMENSF_ZERO | 1.2188 | 1.9688 | Wemen Solar Farm upper limit of 0 MW
I-CTRL_ISSUE_ML | 1.1424 | 0.36458 | DC Link Control Issue Constraint for Murraylink
T-LIPM | 1.1319 | 8.4549 | Out = Liapootah to Waddamana to Palmerston 220kV line, with associated 220kV CB I/S at Waddamana
N-FLML_9R4_ARMED | 1.1111 | 0.34375 | Out = Finley to Mulwala (9R4) or Mulwala to Corowa(997/2) or Corowa to Albury (997/1) And Finley Transfer Trip Scheme Armed
N-AR_TX | 1.1076 | 2.4549 | Out= Armidale No.3 or 6 330/132kV transformer
N-DP_TIETX | 1.0972 | 1.4722 | Out= DarlingtonPt 330/220/33 kV tie Tx (#3 or #4)
Q-NESTM | 1.0799 | 38.0347 | Out= one H11 Nebo to H35 Strathmore 275kV line (822 / 878 / 8845)
Q-WRWK | 1.0139 | 0.50694 | Out = 8902 (H39 Woree - H60 Walkamin) 275kV line
V-HGML | 0.92361 | 0 | Out = Haunted Gullly to Moorabool (HGTS-MLTS) 500kV line, MOPS 500kV centre CB fail timer set to zero
Q-RSCH | 0.90278 | 0.46875 | Out= 857 or 858 (H13 Ross to H32 Chalumbin) 275kV line
N-BODWF1_ZERO | 0.89931 | 0.87847 | Bodangora wind farm upper limit of 0 MW
N-DMSR_8J | 0.875 | 0 | Out= Dumaresq to Sapphire (8J) line
S-NWRB2 | 0.82986 | 0 | Out = North West Bend to Robertstown No.2 132kV line O/S
N-COFB_998 | 0.82639 | 0 | Out = Cowra to Forbes (998) 132kV line
V-HWRO3 | 0.8125 | 0 | Outage = Hazelwood to Rowville No.3 500kV line
V-EP_BUS1 | 0.79514 | 0 | Outage of Eildon PS No. 1 220 kV Bus
N-ARSR_8E | 0.78472 | 0 | Out= Armidale Sapphire (8E) line
N-JNWG_RADIAL | 0.75 | 1.6944 | Outage = Jindera - Wagga (62) line, Wagga-Yass 132kV network Split, X5 opened and with 2 Yass Transformer in service
T-MRWF_ZERO | 0.70833 | 0.35764 | Discretionary 0 MW upper limit on Musselroe Wind Farm
N-SAPHWF1_ZERO | 0.69444 | 0 | Sapphire wind farm upper limit of 0 MW
Q-RSTVS | 0.68056 | 6.8507 | Out= one H13 Ross to T56 Townsville South 132kV line (7156/7249)
S-PA_W_BUS_R | 0.63542 | 2.3333 | Out= Para 275kV West bus Right section(i.e.CBs 6601,8033,6510,6514 6542,6541, TX8 O/S),(NOTE: BW-MP 275kV line will also be taken O/S as per Electranet's OI 5.17 issued 19/07/2017),(Note: with both Para SVC 1 & 2 inservice and connected to Para East bus)
V-HOTS_SVC | 0.5625 | 2.1806 | Out = Horsham 220kV SVC
N-ARDM_8C | 0.54861 | 0.14583 | Out= Armidale to Dumaresq (8C) line
N-ARIV_96N | 0.54861 | 0.73958 | Out = Armidale to Inverell (96N) 132kV line
S-SE_CB6186_CB6187 | 0.52778 | 0.40972 | Out= South East 132kV CB 6186 Or CB 6187
S-X_MKRB+RB_N | 0.51736 | 0 | Out= Robertstown North 275kV Bus(275kV CBs ONLY O/S, associated 132kV CBs assumed I/S) + Robertstown TX1 + Robertstown-Mokota 275kV line O/S;(Note: with both Black Range series capacitors I/S)
Q-BS_CB88312 | 0.51389 | 0 | Out = H20 Broadsound 275kV CB 88312
Q-RRSF1_ZERO | 0.51389 | 0.72222 | Ross River solar farm upper limit of 0 MW
Q-CLWU | 0.51042 | 0.21875 | Out = 871 H24 Calvale to H40 Wurdong 275kV line
V-KMRC | 0.49653 | 0 | Out = Kiamal to Red Cliffs 220kV line
N-LDMU_83 | 0.49306 | 0 | Out = Liddell to Muswellbrook (83) line
V-ELAINEWF_ZERO | 0.48958 | 0 | Elaine Wind Farm upper limit of 0 MW
N-LIMOSF11_ZERO | 0.48958 | 0 | Limondale 1 solar farm upper limit of 0 MW
Q-HAURS | 0.48264 | 0 | Out = 8911 (H91 Haughton River to H13 Ross) 275kV line
N-LTWG_RADIAL | 0.47917 | 0.88889 | Out= Lower Tumut - Wagga (051) line, Wagga-Yass 132kV network Split, X5 opened and with 2 Yass Transformer in service
N-KKLS_967 | 0.47222 | 0.58333 | Out= Koolkhan to Lismore (967) 132kV line
Q-RGLC_8875 | 0.45833 | 0 | Out= Raglan to Larcom Creek (8875)
Q-SMHAU | 0.45486 | 0.53125 | Out = 879 (H35 Strathmore to H91 Haughton) 275kV line
T-FARC1 | 0.44792 | 12.934 | Out=Farrell-Reece 1 220KV line
Q-SMCK | 0.44097 | 0 | Out = 8906 (H35 Strathmore to H87 Crush Creek) 275kV line
N-X_BABU_BADP | 0.42361 | 0 | Out = Balranald to Buronga (X3) and Balranald to Darlington Point (X5) 220kV lines
S-X_RBTU+RB_S | 0.42014 | 0 | Out= Robertstown South 275kV Bus(Note:275kV CBs ONLY O/S & assoc. 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Tungkillo 275kV line O/S; (Note: with both Black Range Series caps I/S)
N-DEFI_9R3_C | 0.40972 | 2.8368 | Out= Finley to Deniliquin (9R3); X5 Trip Scheme Disarmed, 132 kV parallel Solid, option c OM521
Q-SMRS | 0.40625 | 0.45833 | Out = 8857 or 8858 (H35 Strathmore to H13 Ross) 275kV line, CQ-NQ limits.
Q-SPL_TX_1 | 0.40625 | 0 | Out= Springlands (TX1) 132/33kV transformer
S-SNOWNTH1_ZERO | 0.40625 | 0 | Discretionary upper limit for Snowtown 2 North WF generation of 0 MW
S-SNOWSTH1_ZERO | 0.40625 | 0 | Discretionary upper limit for Snowtown 2 South WF generation of 0 MW
V-KIATA_ZERO | 0.39583 | 0 | Kiata Wind Farm upper limit of 0 MW
V-BANNERTON_ZERO | 0.39583 | 1.9688 | Bannerton Solar Farm upper limit of 0 MW
V-X_HG_ML_TR | 0.39236 | 0 | Out = Haunted Gully to Moorabool and Haunted Gully to Tarrone 500kV lines, MOPS 500kV centre CB fail timer set to zero, APD-HYTS No.1 500kV line offloaded at APD
T-GTHA | 0.38542 | 0 | Out = One George Town to Hadspen 220kV line
N-TW_330_CB5102 | 0.38194 | 0 | Out= Tamworth 330kV CB 5102
Q-807_PARALLEL_CLOSE | 0.375 | 0.13889 | Out= 807 H2 South Pine to H5 Woolooga 275 kV feeder with parallel 132 kV network intact
Q-LVDS_SMVC | 0.375 | 0 | Out = 7150 (H15 Lilyvale to T35 Dysart tee Norwich Park) 132kV line, with Strathmore SVC is taken out of service
V-ARCW | 0.37153 | 0.66319 | Out = Ararat to Crowlands 220kV line
Q-NQ_SEMI_ZERO | 0.36806 | 0 | Limit all Northern Qld semi-scheduled generators to zero
F-WESTCOAST_REG_0 | 0.35069 | 0.37847 | Regulation FCAS of West Coast Generation limited to 0 MW
Q-STBS | 0.34028 | 23.1354 | Out= 856 or 8831 H29 Stanwell to H20 Broadsound 275 kV line
S-CGTB1 | 0.33681 | 0 | Cherry Gardens to Tailem Bend 275kV line O/S (NOTE: with both Black Range series caps I/S)
T-CRNN | 0.33333 | 0.32292 | Out = Creek Road to New Norfolk 110kV line
V-HYCB_210_213 | 0.33333 | 0.034722 | Out = Heywood (HYTS) 500 kV CB 210 or 213
I-SVML_120 | 0.32986 | 0.0069444 | SA to Vic on ML upper transfer limit of 120 MW
N-X_DTSS_MNYS4 | 0.32986 | 0 | Out= Dapto to Sydney South (11) and Marulan to Yass (4) 330kV lines, short term 15 min ratings used on 5 and 3W lines as per OM 302
S-CGTB1_BC-2CP | 0.32639 | 0 | Cherry Gardens to Tailem Bend 275kV line O/S (Note: with both Black Range series capacitors O/S)
T-FAMA | 0.32639 | 0 | Out=Farrel-Mackintosh 110KV line
Q-ST_275BUS_CB | 0.31944 | 0 | Out = one 275kV bus or one or more 275kV CB at H29 Stanwell
Q-WR_VC | 0.30903 | 1.2674 | Out= H39 Woree 132 kV SVC
N-ARGI_96T | 0.30903 | 1.1181 | Out= Armidale to Glen Innes (96T) line
S-NW_CB6021+CB6022 | 0.30903 | 0 | Out= North West Bend 132kV CBs 6021 and 6022(this offloads NWB TX1)(Note: for Murraylink runback scheme I/S or O/S and Sever scheme I/S or O/S)
S-TBTU | 0.30903 | 0.48264 | Out= Tailem Bend - Tungkillo 275kV line (Note: WITH/WITHOUT associated line CBs I/S), (NOTE: with both Black Range series caps I/S)
F-ESTN_TL_0600 | 0.30903 | 0 | FCAS Lower Requirements for a Eastern Network Event, TL = 600
S-NWCB6022+6023 | 0.30208 | 0 | Out = North West Bend 132 kV circuit breakers CB6022 and CB6023(Note: this takes out North West Bend-Monash #2 132kV line).(Note: for Murraylink runback scheme I/S or O/S and Sever scheme I/S or O/S)
S-BGBW | 0.30208 | 0.37153 | Out = Bungama - Blyth West 275kV line O/S, (i.e. with Blyth West CB8001 OPEN & Blyth West trip scheme I/S)
I-BURC | 0.29167 | 0.94792 | Out = Buronga to Redcliffs (0X1) 220kV line
F-NQ_VST_ISLE_REG | 0.28472 | 0 | Separation between Qld + NSW and Victoria + SA + Tasmania, FCAS Regulation Requirements
NQ_VST_ISLE | 0.28472 | 0 | Separation between Qld + NSW and Victoria + SA + Tasmania
F-VST_ISLE | 0.28472 | 0 | Victoria + SA + Tasmania Contingency FCAS requirements for VIC - NSW separation between Murray and Upper/Lower Tumut
F-NQ_ISLE | 0.28472 | 0 | Qld + NSW Contingency FCAS requirements for VIC - NSW separation between Murray and Upper/Lower Tumut
N-FLUR-99A-C | 0.28125 | 0.40278 | Out = Finley to Uranquinty (99A), X5 trip scheme disarmed and Wagga - Darlington point parallel solid, option c on OM521
V-DDWO_RADIAL | 0.27778 | 0 | Out = Dederang to Wodonga 330kV line O/S. TL63 330kV line and X5 opened. See OM 526 and OM 608
T-HAPM_220 | 0.27778 | 0.60764 | Out = One Hadspen to Palmerston (No.1 or No.2) 220kV line
SA-GEN_RAMP_ZERO | 0.26736 | 0 | Ramp down a number of SA scheduled/semi-scheduled generation to 0 MW and hold at zero && Murraylink set to 0 MW from VIC to SA when SA Demand <=800 MW; Refer to TOA 397
I-QN_1050 | 0.26736 | 0 | Qld to NSW on QNI limited to 1050 MW, includes constraint with dynamic headroom
S-X_CGTB+PATU+VC | 0.23611 | 0 | Out= Cherry Garden-Tungkillo 275kV line + Para-Tungkillo 275kV line + one Para SVC O/S, (NOTE: with both Black Range series caps I/S)
Q-EMERASF1_ZERO | 0.22917 | 0 | Emerald Solar Farm upper limit of 0 MW
Q-NQ_275BUS_CB | 0.22917 | 0 | Out = one 275kV Bus or one or more 275kV CB at north of Calvale and Calliope River resulting loss of two 275kV feeders in the next contingency.
N-BROKENH1_ZERO | 0.22222 | 1.4375 | Broken Hill Solar Farm upper limit of 0MW
Q-NQ_275BUS | 0.21528 | 0 | Outage of one 275kV Bus north of Calvale and Calliope River resulting loss of two 275kV feeders in the next contingency.
I-SVML_100 | 0.20833 | 0 | SA to Vic on ML upper transfer limit of 100 MW
T-GO_250 | 0.17708 | 0 | Discretionary 250 MW upper limit on total Gordon generation
SA-GEN_210 | 0.17708 | 0 | Discretionary 210 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397
T-GO_260 | 0.17361 | 0 | Discretionary 260 MW upper limit on total Gordon generation
SA-GEN_180 | 0.17014 | 0 | Discretionary 180MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397
V-KIAMAL_SC | 0.16667 | 0 | Outage = Kiamal Syncon
I-X_MSUT_LTUT | 0.16319 | 0 | Out= Murray - Upper Tumut (65) & Lower Tumut-Upper Tumut (64) line
Q-NQ_275CB | 0.16319 | 0 | Outage of any 275kV CB north of Calvale and Calliope River resulting loss of two 275kV feeders in the next contingency. Except Broadsound (H20) CBs 88312, 88472, 8332, 8562 and Stanwell (H29) CBs 88312, 88732, 8562, 8642.
SA-GEN_150 | 0.16319 | 0 | Discretionary 150MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397
I-SVML_140 | 0.16319 | 0 | SA to Vic on ML upper transfer limit of 140 MW
SA-GEN_120 | 0.15625 | 0 | Discretionary 120 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397
V-X_HWSM_HWCB | 0.15625 | 0 | Out = One Hazelwood to South Morang and Hazelwood to Cranbourne 500kV lines
Q-LVDS | 0.15278 | 0 | Out =7150 (H15 Lilyvale to T35 Dysart tee Norwich Park) 132kV line
T-FARC2 | 0.14931 | 13.2292 | Out=Farrell-Reece 2 220KV line
V-MURRAWR_ZERO | 0.14931 | 1.3229 | Murra Warra wind farm upper limit of 0 MW
SA-GEN_090 | 0.14583 | 0 | Discretionary 90 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397
S-DLN_BUS | 0.14236 | 0 | Out = Dalrymple North 33kV Bus or Dalrymple-Dalrymple North 33kV line
F-S_DLBAT-L_ZERO | 0.14236 | 0 | Dalrymple Battery (Load Component) FCAS <= 0MW
F-S_DLBAT-G_ZERO | 0.14236 | 0 | Dalrymple Battery (Generation Component) FCAS <= 0MW
F-T-GO_CB_C752 | 0.13889 | 0.086806 | Out= Gordon CB C752, FCAS Requirements
I-SVML_160 | 0.13542 | 0 | SA to Vic on ML upper transfer limit of 160 MW
SA-GEN_060 | 0.13542 | 0 | Discretionary 60 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397
N-NYNGANSF_010 | 0.13194 | 0 | Nyngan Solar Farm upper limit of 10 MW
F-T-GO_CB_A752 | 0.12847 | 0 | Out= Gordon CB A752, FCAS Requirements
SA-GEN_030 | 0.12847 | 0 | Discretionary 30 MW limit on a number of SA scheduled/semi-scheduled generation when SA Demand <=800 MW; Refer to TOA 397
SA-GEN_ZERO | 0.11806 | 0 | 0 MW constraints on a number of SA scheduled/semi-scheduled generation & Murraylink set to a limit of 0 MW VIC to SA when SA Demand <=800 MW; Refer to TOA 397
F-N-LDMU_83 | 0.097222 | 0 | Out = Liddell to Muswellbrook (83) 330kV line - FCAS Requirements
Q-WHITSF1_ZERO | 0.09375 | 0.20486 | Whitsunday solar farm upper limit of 0 MW
F-VS_TL_0600 | 0.09375 | 0 | Local FCAS Lower Requirements for a separated Vic and separated SA Network Event, TL = 600
F-N-8E_ONE | 0.09375 | 0 | Out = Armidale to Sapphire (8E) 330kV line - FCAS Requirements
T-FCSPS_RAMP | 0.090278 | 0 | Ramp down Basslink for outage of FCSPS
N-ARTW_85 | 0.079861 | 0 | Out = Armidale to Tamworth (85) line
I-SVML_015 | 0.076389 | 0 | SA to Vic on ML upper transfer limit of 15 MW
I-BL-FCSPS_NO_ACTION | 0.076389 | 0 | Constrains Basslink transfers to levels where no FCSPS action is required for loss of Basslink
N-DBWL-94J | 0.072917 | 0 | Out = Dubbo132 to Wellington (94J) 132 kV line
I-SVML_020 | 0.0625 | 0 | SA to Vic on ML upper transfer limit of 20 MW
Q-SMSPL | 0.059028 | 0 | Out = 7457 (H35 Strathmore to T242 Springlands) 132kV line O/S
I-CTRL_ISSUE_TE | 0.059028 | 0.82986 | DC Link Control Issue Constraint for Terranora
F-VS_TL_0500 | 0.052083 | 0 | Local FCAS Lower Requirements for a separated Vic and separated SA Network Event, TL = 500
Q-STR_CB88452_8792 | 0.052083 | 0 | Out = Strathmore 275kV CB88452 or CB8792
Q-MEWF1_ZERO | 0.052083 | 1.4722 | Mt Emerald Wind Farm upper limit of 0 MW
N-COLEASF1_ZERO | 0.048611 | 3.2986 | Coleambally solar farm upper limit of 0 MW
Q-HASMME_RAMP_ZERO | 0.045139 | 0.069444 | Ramp Haughton, Sun Metals and Mt Emerald generators to zero and hold at zero.
F-T_GORDON_ZERO | 0.041667 | 0 | Gordon FCAS <= 0MW
T-GO_ZERO | 0.041667 | 0 | Discretionary 0 MW upper limit on total Gordon generation
I-SVML_010 | 0.041667 | 0 | SA to Vic on ML upper transfer limit of 10 MW
F-I_ML_APD | 0.041667 | 13.0729 | Out=Nil, Dymanic FCAS for APD Load Event
I-SVML_080 | 0.034722 | 0 | SA to Vic on ML upper transfer limit of 80 MW
N-SDUT_1 | 0.034722 | 0 | Out= Stockdill to Upper Tumut (1) line
N-CNSD_3C | 0.034722 | 0 | Out= Canberra to Stockdill (3C) line
I-QN_1100 | 0.03125 | 0 | Qld to NSW on QNI limited to 1100 MW, includes constraint with dynamic headroom
V-DUNDWF3_ZERO | 0.027778 | 0 | Dundonnell wind farm 3 upper limit of 0 MW
V-CWHO | 0.027778 | 1.6354 | Out = Crowlands to Horsham 220kV line
F-I_MG_1000 | 0.024306 | 0 | FCAS Raise Requirements for a Generation Event, MG = 1000
I-SVML_060 | 0.020833 | 0 | SA to Vic on ML upper transfer limit of 60 MW
F-VS_TL_0550 | 0.020833 | 0 | Local FCAS Lower Requirements for a separated Vic and separated SA Network Event, TL = 550
F-I_MG_0850 | 0.010417 | 0 | FCAS Raise Requirements for a Generation Event, MG = 850
F-STHN_ISLE | 0.0034722 | 0 | Southern separation between Armidale and Bulli Creek (8C and 8E or 8L and 8M) - FCAS Contingency Requirements
S-RB_TX1 | 0.0034722 | 2.2535 | Out =Robertstown #1 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
F-QLD_STHN_ISLE_REG | 0.0034722 | 0 | Qld / Southern separation between Armidale and Bulli Creek (8C and 8E or 8L and 8M) - FCAS Regulation Requirements
QLD_AR_STHN_ISLE | 0.0034722 | 0 | Qld / Southern separation between Armidale and Liddell (84 and 83/88 or 85 and 86)
F-QLD_ISLE | 0.0034722 | 0 | Qld separation between Armidale and Bulli Creek (8C and 8E or 8L and 8M) - FCAS Contingency Requirements
I-SVML_040 | 0.0034722 | 0 | SA to Vic on ML upper transfer limit of 40 MW
N-BADP | 0 | 0.052083 | Out = Balranald to Darlington Point (X5) 220kV line
N-DM_CB | 0 | 1.566 | Out = one Dumaresq 330kV CB (5312, 5322, 5332 or 5342) O/S

## Outage stats
Column1 | Unplanned | Short Notice | ≤ 30 days | > 30 days
APT 2016 | 24 | 36 | 7 | 1
2017 | 20 | 33 | 5 | 4
2018 | 21 | 74 | 15 | 3
2019 | 17 | 58 | 24 | 1
2020 | 13 | 23 | 13 | 2
ElectraNet 2016 | 110 | 266 | 309 | 176
2017 | 281 | 687 | 907 | 426
2018 | 417 | 863 | 973 | 804
2019 | 352 | 852 | 1077 | 835
2020 | 269 | 654 | 958 | 839
Essential E 2016 | 3 | 26 | 40 | 0
2017 | 4 | 28 | 61 | 0
2018 | 8 | 5 | 29 | 0
2019 | 4 | 17 | 39 | 0
2020 | 3 | 22 | 62 | 1
Powerlink 2016 | 273 | 885 | 2265 | 17
2017 | 1796 | 5071 | 11266 | 195
2018 | 2020 | 5841 | 13383 | 222
2019 | 2040 | 5250 | 8042 | 2334
2020 | 1897 | 6642 | 8078 | 4245
AusNet 2016 | 170 | 876 | 695 | 97
2017 | 316 | 1484 | 1208 | 80
2018 | 304 | 1467 | 970 | 54
2019 | 364 | 1387 | 1588 | 69
2020 | 370 | 1128 | 1689 | 78
TasNetworks 2016 | 19 | 88 | 166 | 32
2017 | 89 | 472 | 602 | 323
2018 | 171 | 577 | 637 | 238
2019 | 198 | 500 | 1069 | 340
2020 | 108 | 1231 | 890 | 438
TransGrid 2016 | 116 | 472 | 973 | 506
2017 | 277 | 911 | 1365 | 856
2018 | 326 | 820 | 1730 | 522
2019 | 327 | 1066 | 1868 | 837
2020 | 411 | 1061 | 1635 | 843

## NEM Changes
PROJECT | DATE | REGION | NOTES
Wild Cattle Hill Wind Farm | 7 January 2020 | Tasmania | New Generator
Yarrenlea Solar Farm | 7 January 2020 | Qld | New Generator
Pieman Substation | 2020-01-24 | Tasmania | Piemen 220 kV substation teed into the existing Farrell - Reece No 1 and No 2 220 kV lines to form the Farrell - Pieman -Reece No 1 and No 2 220 kV lines.
Maryrorough Solar Farm | 25 February 2020 | Qld | New Generator
Dundonnell Wind Farm 1-3 | 10 March 2020 | Victoria | New Generator
Bomen Solar Farm | 17 March 2020 | NSW | New Generator
Elaine Wind Farm | 7 April 2020 | Victoria | New Generator
Cherry Tree Wind Farm | 28 April 2020 | Victoria | New Generator
Bulgana Wind Farm | 12 May 2020 | Victoria | New Generator
Goonumbla Solar Farm | 12 May 2020 | NSW | New Generator
Gullen Range 2 Wind Farm | 19 May 2020 | NSW | New Generator
Buronga No.1 syn con | 2020-06-01 | NSW | Syn con to support system strength in south west NSW
Limondale 1 Solar Farm | 30 June 2020 | NSW | New Generator
Buronga No.2 and 3 syn cons | 2020-07-01 | NSW | Syn cons to support system strength in south west NSW
Davenport R5 275 kV reactor | 2020-07-06 | SA | Commissioning of a new 50MVar 275kV bus reactor at Davenport substation. Currently connected to the 275 kV Davenport No.1 and No.2 bus tie. It will be connected to the future Davenport - Mt Gunson South 275 kV line.
Wurdong – Teebar Creek 275 kV line | 2020-07-17 | Qld | H40 Wurdong – H63 Teebar Creek No.819 275 kV line has been commissioned. H40 Wurdong – H6 Gin Gin No. 819 275 kV line and the H6 Gin Gin – H63 Teebar Creek No. 826 275 kV line have been decommissioned.
Darlington Point Solar Farm | 11 August 2020 | NSW | New Generator
Berrybank switching station | 2020-08-14 | Victoria | Commissioning of new Berrybank switching station which cuts into the existing Ballarat - Terang 220 kV line. This forms the new Ballarat - Berrybank Switching Station 220 kV line and Terang - Berrybank Switching Station 220 kV line.
Davenport - Mt Gunson South 275 kV line | 2020-08-24 | SA | Commissioning of equipment at Mt Gunson South 275 kV Substation which includes Mt Gunson South - North 275 kV Bus and Mt Gunson South - South 275 kV Bus.
Kiamal Solar Farm | 1 September 2020 | Victoria | New Generator
Kiamal syn con | 2020-09-11 | Victoria
Warwick Solar Farm 1 | 22 september 2020 | Qld | New Generator
Warwick Solar Farm 2 | 22 september 2020 | Qld | New Generator
Torrens Island A Unit 2 | 30 September 2020 | SA | Deregistered Generator
Torrens Island A Unit 4 | 30 September 2020 | SA | Deregistered Generator
Gin Gin bypass project (feeder 813 & 815 bypassed) | 2020-10-01 | Qld | Feeder 813 from Calliope River to Gin Gin joined to feeder 815 from Gin Gin to Woolooga to form a single feeder.
SA Water Morgan Whyalla Pump Station | 26 October 2020 | SA | New Generator
Collector Wind Farm Substation | 2020-10-27 | NSW | Collector Wind Farm substation has been cut into the existing Marulan - Yass (4) 330 kV Line to form the following lines: Collector WF - Marulan (4) 330 kV line Collector WF - Yass (3L) 330 kV line
Haunted Gully No 1 and No 2 Capacitor Banks | 2020-10-28 | Victoria | Haunted Gully No.1 and No.2 132 kV 50 MVAr harmonic filter capacitor banks
Stockdill Substation | 2020-10-29 | NSW | Stockdill Substation has been cut into the existing Canberra - Upper Tumut (01) 330 kV line to form the following lines: Canberra - Stockdill (3C) 330 kV line Stockdill - Upper Tumut (1) 330 kV line
Wellington Solar Farm | 4 November 2020 | NSW | New Generator
Collector Wind Farm | 10 November 2020 | NSW | New Generator
Sunraysia 1 Solar Farm | 10 November 2020 | NSW | New Generator
Molong Solar Farm | 10 November 2020 | NSW | New Generator
Yatpool Solar Farm | 17 November 2020 | Victoria | New Generator
Moorabool Wind Farm | 19 November 2020 | Victoria | New Generator
Crudine Ridge Wind Farm | 24 November 2020 | NSW | New Generator
Jemalong Solar Project | 2 December 2020 | NSW | New Generator
Middlemount Solar Farm | 8 December 2020 | Qld | New Generator
Bango 973 Wind Farm | 15 December 2020 | NSW | New Generator
Glenrowan West Solar Farm | 22 December 2020 | Victoria | New Generator
Cohuna Solar Farm | 22 December 2020 | Victoria | New Generator

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.