## Index
The National Electricity Market Constraint Report 2023
Electronic Material
This spreadsheet provides (for each calendar year):
* Constraint equation changes year on year comparison
* Binding constraint equations (energy and FCAS separately)
* Binding Impact of constraint equations
* Summary of binding/binding impact constraint equations by region
* Summary of binding/binding impact constraint equations for System Normal vs Outages
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
* Network and generation augmentations
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page
Binding constraints:
A constraint equation is a linear equation, with a left hand side (LHS) and a right hand side (RHS). A constraint is binding when LHS=RHS, which means it has reached its upper limit.
In some cases, the binding results for several constraint equation IDs have been combined. This is due to some limits being represented by several constraint equations, to either:
• Move each generator from a maximum calculation onto the LHS of separate constraint equations (such as the New South Wales to Queensland voltage stability limit).
• Manage the same limit under different network configurations (such as Yallourn W1 switched into 500 kV or 220 kV mode).
• Combine different values of network support for the same generator(s).
Binding Impact:
Binding Impact is used to distinguish between the severities of different binding constraint equations. It represents the financial pain associated with that binding constraint equation and can be a good way of picking up congestion issues. It is a relative term, not an absolute term.

## Constraint Changes
Constraint changes by region and year
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Ad-Hoc | 1 | 0 | 0 | 0 | 0 | 0
Constraint Automation - Real Time | 37744 | 32817 | 53504 | 40710 | 48882 | 58629
Constraint Automation | 48 | 49 | 39 | 23 | 67 | 37
DATASNAP | 92 | 90 | 62 | 60 | 67 | 91
FCAS | 486 | 1192 | 730 | 418 | 700 | 1057
NSW | 8206 | 5092 | 7926 | 6562 | 3873 | 8421
Negative Residue | 0 | 0 | 12 | 0 | 0 | 0
Non-Conformance | 35 | 29 | 31 | 40 | 52 | 64
Other | 3 | 1 | 0 | 16 | 0 | 9
Outage Ramping | 19368 | 25718 | 23622 | 33118 | 28264 | 33982
PASA | 0 | 0 | 0 | 1 | 1 | 1
Qld | 1716 | 582 | 937 | 1305 | 1850 | 1356
Quick | 1032 | 865 | 1072 | 862 | 2592 | 770
SA | 3239 | 7132 | 2309 | 6564 | 4980 | 2441
Tas | 193 | 629 | 25 | 351 | 115 | 35
Vic | 6280 | 5656 | 1418 | 2312 | 2115 | 3571
Total constraint eqns | 11467 | 12348 | 13127 | 14297 | 15160 | 14802
Total changes without outage ramping and CA-RT | 20299 | 20452 | 13489 | 17652 | 13820 | 17083
Total number of constraints
| 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Constraint Equations | 7746 | 7697 | 8275 | 8902 | 9523 | 9745 | 9935 | 10303 | 11231 | 11660 | 11578 | 11467 | 12348 | 13127 | 14297 | 15160 | 14695
Constraint Sets | 3366 | 3369 | 3431 | 3559 | 3657 | 3597 | 3410 | 3424 | 3630 | 3778 | 3917 | 4036 | 4390 | 4603 | 4973 | 5498 | 5703
Constraint Functions |  |  | 347 | 382 | 390 | 401 | 366 | 359 | 364 | 373 | 387 | 505 | 585 | 588 | 641 | 638 | 647
Increase in Constraint Equations |  |  | 578 | 627 | 621 | 222 | 190 | 368 | 928 | 429 | -82 | -111 | 881 | 779 | 1170 | 863 | -465

## Binding
Constraint Equation ID | 2023 Hours | 2022 Hours | Description | Type | Limit Type | Region
#BLUEGSF1_E | 4535.0833 | 0 | QCBS1B.ENERGY * 1 <= 148 (Wt = 360) | Other | DEFAULT | Quick
#GSWF1A_E | 3522.6667 | 0 | SROB1G.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
N^N-LS_SVC | 3095 | 4518 | Out= Lismore SVC O/S or reactive power control mode,avoid Voltage collapse on TL 87/89 trip;[Swamped for 3 DLK cables are O/S Or when ECS is enabled with DLK is exporting to QLD,sets DLK to -29 MW for -29< DLK FLOW<0, checks ETS status & unswamps if O/S) | Outage | Voltage Stability | NSW
#MINTARO_D_E | 2129.0833 | 0 | SMPS.ENERGY * 1 = 30 (Wt = 755) | Other | DEFAULT | Direction
#TALWB1_E | 1982.9167 | 0 | NDTB1T.ENERGY * 1 <= 240 (Wt = 360) | Other | DEFAULT | Quick
N>NIL_94T | 1703.25 | 1657 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | NIL | Thermal | NSW
T::T_NIL_1 | 1650 | 282.6667 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Swamp if less than 3 synchronous West Coast units generating or Farrell 220kV bus coupler open or Hampshire 110kV line is closed. | NIL | Transient Stability | Tas
N>NIL_969 | 1644.75 | 1303.4167 | Out= Nil, avoid O/L Gunnedah to Tamworth (969) on trip of Nil, Feedback. Metering is used as specified in OM520 [Note: swamped with 96M or 9UJ or 9UH is O/S] | NIL | Thermal | NSW
#TORRB3_D_E | 1588.8333 | 2167.3333 | STSB3.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
#TORRB4_D_E | 1543.5 | 1590.8333 | STSB4.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
#TORRB2_D_E | 1370.9167 | 1179.0833 | STSB2.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
S>NIL_MHNW1_MHNW2 | 1336.5833 | 1558.5833 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL | Thermal | SA
#MAPS3PV1_E | 1317.25 | 0 | SMA31M.ENERGY * 1 <= 0 (Wt = 360) | Other | DEFAULT | Quick
N>NIL_94K_1 | 1253.5833 | 907.5833 | Out= Nil, avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | NIL | Thermal | NSW
V^^V_NIL_KGTS & V^^V_NIL_KGTS_2 | 1140.4167 | 863.75 | Out= Nil, avoid voltage collapse for loss of Horsham - Murra Warra - Kiamal 220kV line. Murraylink VFRB disabled. Swamp if Murraylink VFRB enabled. | NIL | Voltage Stability | Vic
N^^N_NIL_X5_xxx | 1041.25 | 1522.0833 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of Bendigo to Shepparton 220kV line in NW Victoria | NIL | Voltage Stability | NSW
SVML_ZERO | 1029.4167 | 619.75 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | SA
N>>NIL_9XX_051 | 914.1667 | 0 | Out= NIL, avoid O/L Burrinjuck to Yass (970) on trip of Wagga to Lower Tumut (051) line, Feedback | NIL | Thermal | NSW
#HBESSG1_E | 845.5 | 0 | VHW21H.ENERGY * 1 <= 150 (Wt = 360) | Other | DEFAULT | Quick
#HBESSL1_E | 840.5 | 0 | VHW22H.ENERGY * 1 <= 150 (Wt = 360) | Other | DEFAULT | Quick
Q_STR_7C0K_HASF | 834.0833 | 306.5833 | No limit to Haughton Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N>>NIL_964_84_S | 807.1667 | 0 | Out= NIL, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Liddell (84) line, Feedback | NIL | Thermal | NSW
Q>NIL_YLMR | 676.9167 | 604.5833 | Out= Nil, avoid overload on 110kV feeders between Yarranlea and Middle Ridge(733/1 and 734/1), Feedback | NIL | Thermal | Qld
#FLYCRKWF_E | 653.9167 | 0 | NONF1F.ENERGY * 1 <= 42 (Wt = 360) | Other | DEFAULT | Quick
Q>NIL_EMCM_6056 | 628.1667 | 969.5833 | Out= NIL, avoid thermal overload on Emerald to Comet (6056) 66 kV Feeder | NIL | Thermal | Qld
N>NIL_PKTX_LV | 612.8333 | 631.0833 | Out= Nil, avoid O/L either Parkes 132kV/66kV Transformer on NIL trip, Feedback. | NIL | Thermal | NSW
N>NIL_9R6_9R5 | 605.25 | 300.6667 | Out= Nil, avoid O/L Wagga North to Wagga132 (9R6) on trip of Wagga North to Wagga330 (9R5) line, Feedback | NIL | Thermal | NSW
V^^N_NIL_1 | 585 | 402 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Voltage Stability | Vic
SVML^NIL_MH-CAP_ON | 520.6667 | 472.25 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL | Voltage Stability | SA
N>NIL_997_99A | 517.0833 | 686.9167 | Out= Nil, avoid O/L Corowa to Albury 132kV line (997/1) on trip of Finley to Uranquinty 132kV line (99A), Feedback | NIL | Thermal | NSW
N>NIL_9R6_991 | 438.5833 | 0 | Out= Nil, avoid O/L Wagga North to Wagga (9R6) 132kV line on trip of Wagga North to Murrumburrah (991) 132kV line, Feedback | NIL | Thermal | NSW
V_T_NIL_FCSPS | 411.3333 | 207.4167 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Other | Vic
N_X_MBTE_3A & N_X_MBTE_3B | 392.5833 | 441.9167 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | Unit Zero | NSW
S>NIL_NWRB2_NWRB1 | 376.75 | 220.4167 | Out= NIL, avoid O/L North West Bend-Roberstown #1 132kV line on trip of North West Bend-Robertstown #2 132kV line (this trips MWP1-3 SFs), Feedback | NIL | Thermal | SA
S>NIL_HUWT_STBG3 | 368.25 | 379.0833 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Constraint Swamped when Wattle PT when generating >=60 MW) | NIL | Thermal | SA
V::N_NIL_xxx | 321.4167 | 23.75 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL | Transient Stability | Vic
V^^V_MLNK_KGTS | 319.1667 | 128.0833 | Out= Murraylink, avoid voltage collapse for loss of Horsham - Murra Warra - Kiamal 220kV line | Outage | Voltage Stability | Vic
NSA_S_PORxxx | 317.3333 | 421.6667 | Port Lincoln >= 15 MW for Network Support Agreement | Outage | Network Support | SA
#TIBG1_E | 292.5 | 0 | STPB1T.ENERGY * 1 <= 250 (Wt = 360) | Other | DEFAULT | Quick
NC_S_BOWWPV1 | 288.75 | 1.1667 | Non Conformance Constraint for BOLIVAR WWTP PV1 | Other | Non-Conformance | Non-Conformance
N>94K2_94T_NIL | 286.4167 | 0 | Out= Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only), avoid O/L on Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
Q_KEP-HYB_25MW | 266.4167 | 645.4167 | Kennedy Energy Park upper limit of 25MW | Outage | Discretionary | Qld
V^^N_LTUT_1 | 265.5833 | 0 | Out = Lower to Upper Tumut (64) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V>>NIL_ARWB_KGBE | 255.25 | 488.0833 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
T_MRWF_GCS | 237.3333 | 113.8333 | Musselroe wind farm Generator Control Scheme (GCS) constraint to maintain TAS FOS for a Tasmania generator event. Limit Musselroe wind farm based on load available/armed by Musselroe GCS | NIL | Other | Tas
NRM_NSW1_VIC1 | 229.75 | 80.4167 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue | Negative Residue
V>>NIL_ELML_BAML2 | 219.0833 | 26.6667 | Out= Nil, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | NIL | Thermal | Vic
N_MBTE1_B | 208.4167 | 102.4167 | Out= one Directlink cable, Qld to NSW limit | Outage | Unit Zero | NSW
S:V_PA_SVC_470 | 198.25 | 219.25 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 470 MW | Outage | Oscillatory Stability | SA
V^^V_NIL_SWVIC | 192.5 | 20.5833 | Out = Nil, manage flow towards Moorabool across Haunted Gully to Moorabool and Mortlake to Moorabool 500kV lines to avoid voltage instability for the loss of Haunted Gully to Moorabool 500kV line and both APD potlines | NIL | Voltage Stability | Vic
S_ISLE_CRK_10 | 188.4167 | 281.5 | Discretionary upper limit on Cathedral Rocks windfarm<=10 MW when 2-4 syn cons I/S for SA is at risk of islanding or in islanded mode(Note: this equation is swamped when 0-1 sync cons are I/S) | Outage | Discretionary | SA
S:V_550_HY_TEST_DYN | 187.9167 | 10.1667 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
V_BANSF_BBD_S1 | 182.9167 | 0 | Out = Nil, Bannerton SF limitation segment 1 if Boundary Bend (BBD) loading is less than 5 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
#GLENSF1_E | 179.8333 | 0 | VGN21G.ENERGY * 1 <= 102 (Wt = 360) | Other | DEFAULT | Quick
V_CWWF_FLT_0 | 179 | 8.5833 | Limit Crowlands Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#OSB-AG_D_E | 176.25 | 35.9167 | SNBN1.ENERGY * 1 = 145 (Wt = 755) | Other | DEFAULT | Direction
V_ARARATWF_FLT_0 | 175.9167 | 7.8333 | Limit Ararat Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V:S_600_HY_TEST | 172.0833 | 64 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
#TIBL1_E | 171.0833 | 0 | STPB2T.ENERGY * 1 <= 250 (Wt = 360) | Other | DEFAULT | Quick
V_KIATA_ISL_0 | 162 | 1.5 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V:S_600_HY_TEST_DYN | 161.5 | 58.5 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Oscillatory Stability | Vic
V_KIAMSF_DYN | 160.4167 | 0.33333 | Out = Kiamal Syncon, Limit Kiamal solar farm to 135 MW when Murra Warra 2 WF syncon I/S. Limit Kiamal solar farm to 100 MW when Murra Warra 2 WF syncon O/S | Outage | Discretionary | Vic
N>>DPTX1-2_TX_NIL | 159.5833 | 0 | Out= one Darlington Pt 132/330kV TX1 or TX2, avoid O/L remaining Darlington Pt 132/330kV TX on trip of Nil, Feedback | Outage | Thermal | NSW
#QPS5_D_E | 157.5 | 260.4167 | SQPS5Q.ENERGY * 1 = 74 (Wt = 755) | Other | DEFAULT | Direction
S_WATERLWF_RB | 157 | 17.5833 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | Discretionary | SA
#PIBESSG1_E | 153.4167 | 0 | VMWT10.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
V^SML_BUDP_3 | 153.4167 | 16.5833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
N>NIL_LSDU | 151.3333 | 172.25 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
#COLUMSF1_E | 145.6667 | 0.75 | QCBR1C.ENERGY * 1 <= 162 (Wt = 360) | Other | DEFAULT | Quick
V_KIAMSF_FLT_50 | 144.0833 | 27.3333 | Limit Kiamal solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_GOONSF1_ZERO | 144 | 0 | Goonumbla solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
#PIBESSL1_E | 140.9167 | 0 | VMWT11.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
V::S_SETB_TBSE_2 | 139.8333 | 71 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Transient Stability | SA
Q>CMTX | 138.75 | 0 | Out = Clermont T1 or T2 132/66 kV transformer, limit to Clermont Solar Farm to 30MW to prevent overload on remaining transformer | Outage | Thermal | Qld
Q_YARANSF1_RB | 136.8333 | 206.25 | Yarrranlea Run Back limit | NIL | Discretionary | Qld
NSA_Q_GSTONE34_xxx | 136.3333 | 99.0833 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Network Support | Qld
VT_ZERO | 131.6667 | 100.3333 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Interconnector Zero | Vic
S^NIL_SA_NTH_N-2 | 131.3333 | 0 | Out = NIL, Manage voltage collapse in northern SA for the loss of Robertstown - Tungkillo 275kV line 1 and 2 and the Robertstown No.1 and No.2 synchronous condensers declared credible | Outage | Voltage Stability | SA
V_YATPSF_FLT_25 | 130.4167 | 43.25 | Limit Yatpool solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N^^Q_LS_SVC_KPP_1 | 125.0833 | 1.1667 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage Collapse on loss of Kogan Creek MW | Outage | Voltage Stability | NSW
V>>NIL_WBBA_RCWEKG | 122.8333 | 113.8333 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
#WYASF1_E | 122 | 0 | NWGJ4W.ENERGY * 1 <= 53 (Wt = 360) | Other | DEFAULT | Quick
V^^N_DTKV_1 | 121.25 | 136 | Out = Dapto - Kangaroo Valley (18) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V>>NIL_WBBA_KGBE | 120.1667 | 131.75 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
V_BANNERTSF_FLT_45 | 120 | 30.9167 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
SV_470_DYN | 118.8333 | 132.6667 | SA to Victoria on Heywood upper transfer limit of 470 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 50 MW | Outage | Discretionary | SA
V_WEMENSF_FLT_45 | 115.5833 | 19.0833 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_MARYRSF1_RB | 112.9167 | 160.3333 | Maryrorough Run Back limit | NIL | Discretionary | Qld
V_CWWF_ISL_0 | 112.9167 | 0 | Crowlands Wind Farm total upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V>>NIL_BABE_HOMRKM | 112.1667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
Q>NIL_EMBW_EMLV_DS | 110.75 | 141.1667 | Out= Nil, limit Emerald SF to 40MW to avoid overload on Emerald - Lilyvale 66kV line on trip of Emerald - Comet - Blackwater 66kV line (6056 or 6011), swamp if Emerald CBs S612,S610 and Blackwater CB S605 are closed (DS only) | NIL | Thermal | Qld
N>NIL_MBDU | 108.5833 | 48.75 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
V_MURRAWRWF_FLT_90 | 105.4167 | 72.3333 | Limit Murra Warra Wind Farm 1+2 upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
S_ISLE_LKB1+2+3_60 | 104 | 167.1667 | Discretionary upper limit on Lake Bonney (1+2+3) windfarms<=60 MW & No. in-service wind turbines for LKB at 41 Turbines.(Note otherwise, LKB 2+3 +1 will be constrained to 0 MW) | Outage | Discretionary | SA
Q_STR_7C8C_KBWF | 101.8333 | 0 | Limit Kaban Wind Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
V>>NIL_ARWB_RCWEKG | 100.0833 | 84 | Out = Nil, avoid O/L Ararat to Waubra 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
V_MURRAWRWF_FLT_100 | 98.1667 | 0 | Limit Murra Warra Wind Farm 1+2 upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N::N_NIL_63 | 95.4167 | 72.3333 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
N_LIMOSF2_FLT_15 | 95.4167 | 5.6667 | Limit Limondale 2 solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_LIMOSF1_FLT_50 | 93 | 1.9167 | Limit Limondale 1 solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_KARADSF_FLT_25 | 92.75 | 49.6667 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_SUNRSF_FLT_60 | 89.5833 | 7.1667 | Limit Sunraysia solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
#BLUEGSF1_E | 89.0833 | 4535.0833 | QCBS1B.ENERGY * 1 <= 148 (Wt = 360) | Other | DEFAULT | Quick
SVML_ROC_80 | 87.9167 | 79.0833 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | SA
#DEVILS_G_E | 87.8333 | 50.6667 | TDG11.ENERGY * 1 <= 64 (Wt = 360) | Other | DEFAULT | Quick
Q>>BCRG_CLWU_BCCP | 87.75 | 35 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
S:V_550_HY_TEST | 87.6667 | 5.6667 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
N_BROKENHSF_FLT_25 | 86.5833 | 3.75 | Limit Broken Hill Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S^^V_SETB_1 | 85.3333 | 8.75 | Out= one South East to Tailem Bend 275kV line, voltage collapse equation Tailem Bend-Keith #2 132kV Line <=135 MW on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage | Thermal | SA
Q_STR_7C2K_KBWF_5 | 84.8333 | 0 | Limit to Kaban Wind Farm 1% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>250&270(AVG),Ross_FN>100&120(AVG), 80% limit if NQLD>350&370(AVG),Ross_FN>150&170(AVG)and Haughton syncon ON or at night, Zero otherwise. | Outage | System Strength | Qld
V_GANWRSF_FLT_30 | 83.5833 | 31.9167 | Limit Gannawarra solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N::N_DTKV_2 | 83.5 | 0 | Out = Dapto - Kangaroo Valley (18) 330kV line, transient stability limit (Snowy-NSW) for loss of one 330kV line between Yass and Bannaby/Marulan with summated flow on 4+5+61 <=1500 | Outage | Transient Stability | NSW
N>>964_86_85_S | 82.6667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Armidale to Tamworth (86) on trip of Uralla to Tamworth (85) line, Feedback | Outage | Thermal | NSW
V_SHWF_FLT_286 | 82.5 | 97.25 | Limit Stockyard Hill wind farm to 286 MW if Heywood flow is above 470 MW (SA to VIC direction). Swamp otherwise. This is to manage voltage oscillation. | NIL | System Strength | Vic
N_SUNRSF_FLT_80 | 82.0833 | 0 | Limit Sunraysia solar farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S>>PARB_RBTU_WTTP | 81.9167 | 19.6667 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N_LIMOSF1_FLT_85 | 79.75 | 0 | Limit Limondale 1 solar farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>NIL_WETX_NIL | 79.5833 | 226.3333 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback | NIL | Thermal | Vic
VSML_ROC_80 | 79.5 | 73.1667 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | Vic
N_DARLSF_FLT_110 | 79.4167 | 0 | Limit Darlington Pt Solar Farm upper limit to 110 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_BANNERTSF_FLT_20 | 77.75 | 0 | Limit Bannerton Solar Farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>NIL_9ML | 77.6667 | 77.75 | Out= Nil, avoid O/L Crudine Ridge to Ilford Tee (9ML) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
N>X-968+96M_969_NIL | 77.3333 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line and 96M(Narrabri to Moree), avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | Outage | Thermal | NSW
N>N-NIL_JUTX_LV | 77.1667 | 80.25 | Out= Nil, avoid O/L Junee#3 132/66kV transformer on trip of Nil, Feedback. 90% of Rating is used as operating margin. | NIL | Thermal | NSW
S>>PARB_RBTU_WEWT | 76.9167 | 31.5 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V_KARADSF_FLT_20 | 76.75 | 8.0833 | Limit Karadoc solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_YATPSF_FLT_20 | 75.8333 | 7.6667 | Limit Yatpool solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>>NIL_33_34 | 75.4167 | 0 | Out= Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL | Thermal | NSW
V_WEMENSF_FLT_20 | 75.4167 | 0 | Limit Wemen Solar Farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>>NIL_84_88_S | 74.9167 | 42.3333 | Out= NIL, avoid O/L Tamworth to Liddell (84) using 15 min rating on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL | Thermal | NSW
N>>NIL_86_85_S | 71.5833 | 0 | Out= NIL, avoid O/L Armidale to Tamworth (86) on trip of Uralla to Tamworth (85) line, Feedback | NIL | Thermal | NSW
#PPCCGT_D_E | 69.8333 | 19 | SPPT.ENERGY * 1 = 165 (Wt = 755) | Other | DEFAULT | Direction
Q_STR_KBWF_N-2 | 69.8333 | 30.5 | Out = Nil, Loss of 858 and 857 declared credible. No limit to Kaban WF if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7, Kar>= 2,NQLD>350&370(AVG),Ross_FN>150&170(AVG) and Feeder 8905 IS, Zero otherwise. | Outage | System Strength | Qld
N>>YSTX_TX_051 | 69.1667 | 0 | Out= One Yass 330/132kV TX, avoid O/L of other Yass 132/330kV TX on trip of Wagga to Lower Tumut (051) line, Feedback | Outage | Thermal | NSW
N_LIMOSF2_FLT_10 | 69 | 0 | Limit Limondale 2 solar farm upper limit to 10 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_FINLYSF_FLT_40 | 68.9167 | 0 | Limit Finley solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_BROKENHSF_FLT_30 | 68.1667 | 6.6667 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_KEP-HYB_38MW | 68 | 0 | Kennedy Energy Park upper limit of 38MW | Outage | Discretionary | Qld
S>>RBTU_RBPA_WTTP | 67.3333 | 2.3333 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
N_FINLYSF_FLT_55 | 65.75 | 0 | Limit Finley solar farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
T::T_NIL_3 | 65.6667 | 120.8333 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Transient Stability | Tas
N^^V_NIL_1 | 65.5 | 17.75 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | Voltage Stability | NSW
#WANDSF1_E | 64.9167 | 0 | QWSR1W.ENERGY * 1 <= 125 (Wt = 360) | Other | DEFAULT | Quick
S>>NIL_TWPA_TPRS | 64.25 | 48.8333 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
VS_050_DYN | 63.6667 | 27.9167 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
T_ROCOF_3 | 60.75 | 8.5833 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | ROC Frequency | Tas
S_DVRB2_270 | 60.5833 | 8.9167 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
Q_STR_7C2K_HASF_5 | 60.25 | 231.8333 | No limit to Haughton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N^^V_SM_SCAP_R & N^^V_SM_SCAP_P | 59.9167 | 159.25 | Out = both South Morang 330 kV series capacitor banks, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_7C8C_MEWF | 59.6667 | 0 | Limit Mt Emerald Wind Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
N_NIL_TE_B | 59.5 | 93 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | Other | NSW
V_MURRAWRWF_FLT_60 | 59.25 | 0 | Limit Murra Warra Wind Farm 1+2 upper limit to 60 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
NSA_Q_BARCALDN | 59.0833 | 25 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Network Support | Qld
T_MRWF_QLIM_xx | 58.75 | 54.6667 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Transient Stability | Tas
N::Q_8C8J_KC_N-2 | 58 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | NSW
V_MURRAWRWF_FLT_15 | 57.25 | 3.6667 | Limit Murra Warra Wind Farm 1+2 upper limit to 15 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N_DARLSF_FLT_65 | 56.25 | 0 | Limit Darlington Pt Solar Farm upper limit to 65 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S>SE6161_SETX2_SGBL | 55.5833 | 0 | Out= South East 132kV CB6161, avoid O/L Snuggery-Blanche 132kV line on trip of South East 132/275 TX2 ( this offloads Mayura-South East T 132kV line), Feedback | Outage | Thermal | SA
V::N_HYSE_xxx | 55.4167 | 12.1667 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_GANWRSF_FLT_15 | 55.4167 | 0 | Limit Gannawarra solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>Q-NIL_757_758 | 54.6667 | 58.9167 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL | Thermal | NSW
N>NIL_901 | 53.3333 | 0 | Out= Nil, avoid O/L West Wyalong to Temora 132kV (901) line on trip of Nil, Feedback | NIL | Thermal | NSW
V::N_DDSM_xxx | 52.9167 | 318.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_X_SMSC_O1 | 51.1667 | 99.3333 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
S>>RBTU_N-2_WTTP | 50.75 | 0 | Out= Nil, avoid O/L Waterloo to Templers 132kV line on trip of Robertstown - Tungkillo 275kV line 1 and 2, Feedback | Outage | Thermal | SA
N>NIL_9R4_99A | 50.4167 | 0 | Out= Nil, avoid O/L Finley to Mulwala 132kV line (9R4) on trip of Finley to Uranquinty (99A) line, Feedback | NIL | Thermal | NSW
S>>RBTU_N-2_WEWT | 50.4167 | 0 | Out= Nil, avoid O/L Waterloo East to Waterloo #1 132kV line on trip of Robertstown - Tungkillo 275kV line 1 and 2, Feedback | Outage | Thermal | SA
N_X_MBTE2_A & N_X_MBTE2_B | 49.4167 | 0.5 | Out= two Directlink cables, NSW to Qld limit | Outage | Unit Zero | NSW
T::T_HA_GT_PM_4 | 48.3333 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Transient Stability | Tas
V_ARARATWF_FLT_60 | 48.1667 | 0 | Limit Ararat Wind Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#WSTWYSF1_E | 46.9167 | 24.3333 | NWGJ3W.ENERGY * 1 <= 90 (Wt = 360) | Other | DEFAULT | Quick
S>>RBTX_WEWT_RBTX | 45.0833 | 90.6667 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage | Thermal | SA
S>>RBTU_TWPA_TPRS | 45 | 0.5 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
N>94K2_94T_998 | 44.4167 | 0 | Out= Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only), avoid O/L Molong to Orange North (94T) on trip of Forbes to Cowra (998) line, Feedback | Outage | Thermal | NSW
QNTE_ROC | 44.3333 | 34.5 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | Qld
#NEWENSF2_E | 43.3333 | 0.41667 | NURR2N.ENERGY * 1 <= 200 (Wt = 360) | Other | DEFAULT | Quick
V^^SML_NIL_3 | 42.9167 | 0.083333 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Voltage Stability | Vic
N::N_UTRV_2 | 42.75 | 288.8333 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
V>>NIL_MBDD_MBDD | 41.3333 | 19.3333 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Thermal | Vic
#BW02_D_E | 40.5 | 0 | NBAY2.ENERGY * 1 = 330 (Wt = 755) | Other | DEFAULT | Direction
N_BOMENSF1_ZERO | 39.8333 | 0 | Bomen SF upper limit of 0 MW | Outage | Unit Zero | NSW
N^^Q_DM_TW_SVC_B1 | 39.8333 | 0 | Out = Dumaresq or Tamworth SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
V_BANSF_BBD_S3 | 39.75 | 0 | Out = Nil, Bannerton SF limitation segment 3 if Boundary Bend (BBD) loading is between 10 and 20 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
S>>BWMP_TWPA_TPRS | 39.4167 | 80.75 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
NQTE_ROC | 38.6667 | 32.4167 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | NSW
N>>NIL_85_86_S | 38.0833 | 0 | Out= NIL, avoid O/L Uralla to Tamworth (85) on trip of Armidale to Tamworth (86) line, Feedback | NIL | Thermal | NSW
N^^V_NIL_ARWBBA | 38 | 31.3333 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL | Voltage Stability | NSW
N_LIMOSF21_ZERO | 37.9167 | 0 | Limondale 2 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_LIMOSF11_ZERO | 37.75 | 0.083333 | Limondale 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
S_ISLE_CANUNDA_35 | 37.6667 | 81.9167 | Discretionary upper limit on Canunda windfarm<=35MW & No. in-service wind turbines for canunda at 23 Turbines.(Note otherwise,Canunda will be constrained to 0 MW) | Outage | Discretionary | SA
V>>N_NIL_65_66 | 37.5833 | 133 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Thermal | Vic
V>>N-62_66_65_RADIAL | 36.5833 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | Vic
Q_OKYTX4 | 36.4167 | 5.75 | Out = Oakey 4T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 71MW | Outage | Thermal | Qld
S^NIL_CRK+MTM_95 | 35.8333 | 347.5 | Out= Nil, upper limit for Cathedral Rocks WF + Mt Millar WF <= 95 MW to maintain voltage stability limits | NIL | Voltage Stability | SA
#MAPS2PV1_E | 35.5 | 34.9167 | SMA21M.ENERGY * 1 <= 10.5 (Wt = 360) | Other | DEFAULT | Quick
#DULAWF1_E | 35.25 | 0 | QCBF1D.ENERGY * 1 <= 173 (Wt = 360) | Other | DEFAULT | Quick
N^^V_CNCW_1 | 35.1667 | 40.0833 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W) or Dapto-Kangaroo Valley (18), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
T>T_NIL_110_1 | 35 | 49.75 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Thermal | Tas
S-CRK_0 | 34.75 | 5.0833 | Discretionary upper limit for Cathedral Rocks windfarm generation of 0 MW | Outage | Unit Zero | SA
T>>T_NIL_BL_EXP_7C | 34.75 | 9.8333 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
V::S_NIL_MAXG_xxx | 34.75 | 56.6667 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Transient Stability | SA
#BARKIPS1_D_E | 33.6667 | 5.3333 | SBPS1B.ENERGY * 1 = 72 (Wt = 755) | Other | DEFAULT | Direction
S>>X_RBTU+RBTX_13 | 33.4167 | 25 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Waterloo-Templers 132kV line on trip of remaining Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N_SILVERTWF_FLT_80 | 33 | 0 | Limit Silverton Wind Farm upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
#DRYCGT1_D_E | 32.8333 | 3.5833 | SDCA1.ENERGY * 1 = 35 (Wt = 755) | Other | DEFAULT | Direction
#DRYCGT3_D_E | 32.8333 | 20.6667 | SDCA3.ENERGY * 1 = 35 (Wt = 755) | Other | DEFAULT | Direction
V_KIAMAL_ISL_0 | 32.6667 | 0 | Kiamal Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
N>NIL_997/2_99A | 32.0833 | 0 | Out= NIL, avoid O/L Mulwala to Corowa (996/2) 132kV line on trip of Finley to Uranquinty (99A) 132kV line, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_MEWF_5 | 31.9167 | 56.4167 | Limit Mt Emerald Windfarm to 80% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),(100% at night),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise Zero otherwise. | Outage | System Strength | Qld
S>>TBTU_TUTB_MOTB | 31.5833 | 0 | Out= One Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of remaining Tungkillo-Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
V_BANSF_BBD_S2 | 31.4167 | 0 | Out = Nil, Bannerton SF limitation segment 2 if Boundary Bend (BBD) loading is between 5 and 10 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
N>NIL_99U | 31.3333 | 3.0833 | Out= Nil avoid O/L Sebastopol to Wagga North (99U) 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
V_YATPSF_FLT_40 | 31.25 | 0 | Limit Yatpool solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>>964_85_86_S | 30.8333 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Uralla to Tamworth (85) on trip of Armidale to Tamworth (86) line, Feedback | Outage | Thermal | NSW
N>NIL_COTX_LV | 30.5 | 20.25 | Out= Nil, avoid O/L either Corowa 22kV/132kV Transformer on NIL trip, Feedback. NOTE: System normal is only one transformer in service. 90% of Rating and no operating margin is used as per Essential Energy advice. | NIL | Thermal | NSW
T_BLINK_TV_NGZ | 30.25 | 40.5 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | NIL | Other | Tas
N^^V_MLNK_1 | 30.1667 | 1.9167 | Out = Murraylink, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N^N-X_LS_SVC+96R | 29.8333 | 0 | Out= Lismore SVC + 96R/96L O/S, avoid Voltage collapse on TL (87) trip; [Swamped for 3 DLK cables are O/S Or when ECS is enabled with DLK is exporting to QLD,sets DLK to -29 MW for -29< DLK FLOW<0, checks ETS status & unswamps if O/S) | Outage | Voltage Stability | NSW
N>9U2_969_NIL | 29.6667 | 0 | Out= 9U2 (Moree to Inverell ) 132kV line, avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | Outage | Thermal | NSW
V_S_NIL_ROCOF | 29.5 | 20.75 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | Vic
Q_STR_7C2K_RRSF_5 | 28.8333 | 0.25 | No limit to Ross River Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
Q_STR_7C2K_DAYSF_5 | 28.75 | 0.25 | No limit to Daydream Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
Q_STR_7C2K_HASF_8 | 28.5833 | 0 | No limit to Haughton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_COLSF_5 | 28.5 | 1 | No limit to Collinsville Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG) (80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise. | Outage | System Strength | Qld
S>X_CNRB+RBTX1_23 | 28.25 | 0 | Out= Robertstown TX1 + Canowie-Robertstown 275kV line O/S, avoid O/L Robertstown 275/132kV TX2 on trip of Robertstown-Waterloo East 132kV line (This trip MWP4 SF) line, Feedback | Outage | Thermal | SA
N>94K2_94K1_NIL | 28.0833 | 0 | Out= Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only), avoid O/L on Suntop to Wellington (94K/1) on trip of Nil, Feedback | Outage | Thermal | NSW
S>>NIL_RBTU_RBTU | 27.6667 | 0 | Out= NIL, avoid O/L Robertstown-Tungkillo 275kV line 1 or 2 on trip of parallel Robertstown-Tungkillo 275kV line 2 or 1, Feedback | NIL | Thermal | SA
V>>NIL_WBBA_RCBSS | 27.6667 | 0 | Out= NIL, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Buronga (0X1) 220kV line, Feedback | NIL | Thermal | Vic
Q_STR_7C2K_KIDSF_5 | 26.8333 | 0.25 | No limit to Kidston Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
Q_STR_7C2K_HAYSF_5 | 26.75 | 0.25 | No limit to Hayman Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
SVML_FLT_125 | 26.75 | 0.16667 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
Q:N_1078 | 26.75 | 11.9167 | QNI oscillatory stability limit of 1078 MW | Outage | Oscillatory Stability | Qld
V>NIL_WBBA_KMRC | 26.6667 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
VS_050 | 26.6667 | 0.33333 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Discretionary | Vic
Q_STR_7C2K_KEP_5 | 26.6667 | 0.25 | No limit to Kennedy Energy Park if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
Q_STR_7C2K_SMSF_5 | 26.5833 | 0.5 | No limit to Sun Metals Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
Q_STR_7C2K_HAMSF_5 | 26.4167 | 0.25 | No limit to Hamilton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
Q_STR_7C2K_RUGSF_5 | 26.3333 | 0.58333 | No limit to Rugby Run Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
N>NIL_94T_947 | 26.1667 | 94.5833 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947) line, Feedback | NIL | Thermal | NSW
N_SILVERTWF_FLT_50 | 26.1667 | 0 | Limit Silverton Wind Farm upper limit to 50 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
T>T_HA_TX_2 | 26.0833 | 7.4167 | Out = Hadspen 220/110 kV txfmr, avoid O/L Palmerston 220/110 kV txfmr (flow from 110 kV to 220 kV) on trip of remaining Hadspen 220/110 kV txfmr, feedback | Outage | Thermal | Tas
Q_STR_7C0K_MEWF_2 | 26 | 0 | Limit 70% to Mt Emerald WF if Stan>=2+Stan+Cal>=3+Glad>=2+(Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% Haughton Syncon ON,100% night), 40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG)(25% if Syncon OFF),Zero otherwise. | Outage | System Strength | Qld
N>>NIL_88_84_S | 25.9167 | 11 | Out= NIL, avoid O/L Tamworth to Muswellbrook (88) using 15 min rating on trip of Tamworth to Liddell (84) line, Feedback | NIL | Thermal | NSW
Q>>LCCP_CLWU_BCCP | 25.9167 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
V_MURRAWRWF_FLT_80 | 25.9167 | 8.75 | Limit Murra Warra Wind Farm 1+2 upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N::Q_NIL_KC | 25.4167 | 0.66667 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | Transient Stability | NSW
Q_STR_8C_7C2K_RGUSF | 25.4167 | 88.0833 | No limit to Rugby Run SF to if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad)>=8+ one SVC(Dysart/ Nebo/Strathmore)OS OR Stan>=2+Cal>=1+Glad>=2+(Stan+Cal+Glad)>=7+Kar>=2+Dysart SVC OS/Haughton Syncon ON,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
I_CTRL_ISSUE_ML | 25.3333 | 7.25 | DC Link Control Issue Constraint for Murraylink | Outage | Other | Other
N_WRWSF_055 | 25.25 | 27.0833 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | System Strength | NSW
Q_KEP-HYB_ZERO | 25.25 | 234.75 | Kennedy Energy Park upper limit of 0MW | Outage | Unit Zero | Qld
V_ARARATWF_ISL_0 | 25.25 | 0 | Limit Ararat Wind Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
Q_STR_7C2K_CLRSF_5 | 25 | 0.25 | No limit to Clare Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_WHTSF_5 | 25 | 0.25 | No limit to Whitsunday Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
N>>NIL_86_8U_S | 24.6667 | 73.0833 | Out= NIL, avoid O/L Armidale to Tamworth (86) using 15 min rating on trip of the other Armidale to Uralla line (8U), Feedback | NIL | Thermal | NSW
V::N_HWSM_xxx | 24.6667 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
T^V_NIL_9 | 24.5833 | 33.4167 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Voltage Stability | Tas
N::X_2+3J_2 | 24.5 | 0 | Out = Upper Tumut-Ravine (6X) 330kV line/Ravine-Yass (2) 330kV line + Yass-Gullen Range (3J) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
S>>X_RBTU+RBTX_15 | 24.4167 | 61.25 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>MKRB_BWMP_HUWT | 24.0833 | 18.25 | Out= Mokota-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>NIL_BWMP_RHBR-T | 22.8333 | 10.5833 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
V_S_HEYWOOD_UFLS | 22.75 | 23.25 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC. Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL | Other | Vic
N>>NIL_998 | 22.6667 | 0.83333 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL | Thermal | NSW
N>94K2_94T_947 | 22.6667 | 0 | Out= Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only), avoid O/L on Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | Outage | Thermal | NSW
S>>RBTU_RBPA_WEWT | 22.4167 | 16.25 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
SVML_FLT_150 | 21.75 | 2.0833 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | SA
N>>DP_TIETX_D | 21.75 | 0 | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (220 KV to 330 kV) on Kerang-Bendigo trip; Feedback | Outage | Thermal | NSW
V_KARADSF_FLT_45 | 21.5 | 0 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V::N_X_SMSC_xxx | 21.4167 | 191.75 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
N_WRWSF_066 | 21.1667 | 0 | White Rock wind farm and White Rock solar farm upper limit of 66 MW | Outage | System Strength | NSW
N_SUNRSF_FLT_50 | 21 | 1.1667 | Limit Sunraysia solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_FINLYSF_FLT_30 | 20.5833 | 0.66667 | Limit Finley solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_BANNERTSF_FLT_25 | 20.4167 | 6.0833 | Limit Bannerton Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>>NIL_RBTU_WTTP | 20.3333 | 32.3333 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of one Robertstown - Tungkillo 275kV line, Feedback | NIL | Thermal | SA
V^SML_HORC_3 | 20.25 | 0 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
V::N_JNWG_xxx | 20.1667 | 1.5833 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>>NIL_WEKG_HOBUCW | 20.0833 | 24.8333 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
N>79_998_72 | 19.9167 | 0 | Out= Wollar West to Wellington (79) 330kV line or Wollar 500/330kV TX or Wollar to Wollar West (75) 330kV line, avoid O/L on Cowra to Forbes North (998) on trip of Mt Piper to Wellington line (72), Feedback | Outage | Thermal | NSW
V_WEMENSF_FLT_25 | 19.8333 | 3.0833 | Limit Wemen Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_DARLSF_FLT_85 | 19.75 | 7.5833 | Limit Darlington Pt Solar Farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_LIMOSF1_FLT_60 | 19.6667 | 8.0833 | Limit Limondale 1 solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_WAGGNSF1_ZERO | 19.5833 | 0.25 | Wagga North solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
S>NIL_SGBN_SGSE-T2 | 19.5833 | 0 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | Thermal | SA
#NEWENSF1_E | 19.3333 | 0 | NURR1N.ENERGY * 1 <= 200 (Wt = 360) | Other | DEFAULT | Quick
SVML_FLT_130 | 18.8333 | 26.5 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
V_KIATAWF_FLT_15 | 18.6667 | 8.5833 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V^^N_DTMN_1 | 18.3333 | 52.3333 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S_DVRB_270 | 18.25 | 98.8333 | Out = DV-BL 275kV line Or MK-RB 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF + Hallet Hill WF (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
I_CTRL_ISSUE_TE | 18.1667 | 6.9167 | DC Link Control Issue Constraint for Terranora | Outage | Other | Other
V_GANWRSF_FLT_25 | 18.1667 | 2.25 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>RBTX1_RBTX2_WEMWP4 | 18.1667 | 76.3333 | Out= one Robertstown 275/132kV TX, avoid O/L MWP4-Robertstown 132kV line on trip of remaining Robertstown 275/132kV TX | Outage | Thermal | SA
Q::N_8C8J_AR_2LG_N-2 | 18.0833 | 3 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | Qld
Q_MARYRSF1_10 | 18.0833 | 32.5833 | Maryrorough Solar Farm upper limit of 10 MW | Outage | Discretionary | Qld
S>>X_CNRB+RBTX_22 | 18 | 0 | Out= One Robertstown TX + Canowie-Robertstown 275kV line O/S, avoid O/L Templers-Roseworthy 275kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
V>>NIL_BEKG_HOMRKM | 17.8333 | 134.6667 | Out= Nil, avoid O/L Bendigo to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
V^^SML_ARWBBA_1 | 17.75 | 0 | Out = Ballarat to Waubra to Ararat 220kV line (or any line section between Ballarat and Ararat), avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
S>>PA6509_BWPA_WTTP | 17.6667 | 0 | Out= Para 275kV CB6509, avoid O/L Waterloo-Templers 132kV line on trip of Munno Para-Para 275kV line (this offloads Tungkillo-Para 275kV line 2 & Blyth West-Munno Para 275kV line & Munno Para TX), Feedback | Outage | Thermal | SA
S_WP_ISL | 17.5 | 8.4167 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Wattle Pt WF islanded | Outage | Islanding - Unit | SA
V_BANSF_BBD_60 | 17.4167 | 384.1667 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Discretionary | Vic
VSML_030 | 17.3333 | 0 | Vic to SA on ML upper transfer limit of 30 MW | Outage | Discretionary | Vic
S>>MKRB_TWPA_TPRS | 17.25 | 50.5 | Out= Mokota-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
V^^SML_NSWRB_2 | 17.25 | 81.75 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Voltage Stability | Vic
S_DLBAT-L_ISL | 17.0833 | 8.3333 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Dalrymple Battery (Load Mode) islanded | Outage | Islanding - Unit | SA
N>NIL_9GL | 16.5833 | 1.0833 | Out= Nil, avoid O/L Bango973 to Yass (9GL) on trip of Nil, (Note: Swamped when 999 is O/S) | NIL | Thermal | NSW
Q_NIL_STRGTH_HAUSF | 16.5833 | 2.25 | Out = Nil, limit Haughton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
VTBL_ROC | 16.5833 | 12.3333 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Vic
V>>ARCW_DPTX_KGBE | 16.1667 | 0 | Out= Ararat to Crowlands 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
N^N_KKLS_1 | 16 | 1.4167 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
N_FINLYSF_FLT_50 | 15.75 | 10.25 | Limit Finley solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
#MOORAWF1_E | 15.6667 | 25.75 | VELT2M.ENERGY * 1 <= 305 (Wt = 360) | Other | DEFAULT | Quick
N>>V_NIL_0X1_60 | 15.6667 | 4.1667 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL | Thermal | NSW
N_FINLYSF_FLT_45 | 15.5833 | 7.4167 | Limit Finley solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S>>RBTX1_RBTX2_WEWT | 15.4167 | 0 | Out= one Robertstown 275/132kV TX, avoid O/L Waterloo East-Waterloo 132kV line on trip of remaining Robertstown 132/275kV TX, Feedback | Outage | Thermal | SA
N>NIL_99F | 15.3333 | 0 | Out= Nil, avoid O/L Narrandera to Uranquinty (99F) 132 kV line on trip of Nil, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_RUGSF_7 | 15.3333 | 18.5 | Limit to Rugby Run Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_KBWF_1 | 14.9167 | 0 | Limit 40% to Kaban WF if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar>=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Syncon ON, 1% if Kar<0,100% at night),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
N^^V_DDSM1 | 14.75 | 22.6667 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | Voltage Stability | NSW
T>T_NIL_BL_IMP_7CC | 14.6667 | 12.9167 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
N>NIL_9GM | 14.3333 | 0 | Out= Nil, avoid O/L Bango999 to Yass (9GM) on trip of Nil, Feedback | NIL | Thermal | NSW
V>>NIL_RCWE_HOBUCW | 14.3333 | 23.4167 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
N::N_SDUT_2 | 14.25 | 21.1667 | Out = Upper Tumut-Stockdill (1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
V^^N_DPWG_X5_1 | 14.25 | 7.6667 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N-DBWL_94J | 14.1667 | 0 | Out = Dubbo132 to Wellington (94J) 132 kV line, Upper limit of 80 on Nevertire SF, EE advice on 13/02/2020 | Outage | Other | NSW
N>>964_8U_86_S | 14.1667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Armidale to Uralla (8U) on trip of Armidale to Tamworth (86) line, Feedback | Outage | Thermal | NSW
#MTGELWF1_E | 14.0833 | 4.4167 | VGTW1M.ENERGY * 1 <= 100 (Wt = 360) | Other | DEFAULT | Quick
Q-LILYSF_MVAR | 14.0833 | 0 | Constraint to violate if Reactive power output of Lilyvale Solar farm is greater than +/- 10Mvar at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
V>NIL_GNTX_GNTX_TEMP | 14 | 0 | Out= Nil, maintain post-contingent loading (from 66 to 220kV) on either Glenrowan B txfmr less than 187.5 MVA for loss of one Glenrowan B txfmr, Feedback | NIL | Thermal | Vic
#WARWSF2_E | 13.9167 | 506.75 | QMRY4W.ENERGY * 1 <= 32 (Wt = 360) | Other | DEFAULT | Quick
N_LIMOSF2_FLT_25 | 13.9167 | 0 | Limit Limondale 2 solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_KEP-HYB_20MW | 13.6667 | 257.0833 | Kennedy Energy Park upper limit of 20MW | Outage | Discretionary | Qld
S>DVTX_NIL_DVTX | 13.6667 | 74.0833 | Out= One Davenport 275/132kV TX O/S, avoid O/L of remaining Davenport 132/275kV TX on NIL trip. | Outage | Thermal | SA
N>>17_39_11 | 13.5833 | 0 | Out = Avon-Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage | Thermal | NSW
N::N_CNSD_2 | 13.5 | 2.25 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
S>S_WERB_TWPA_TPRS | 13.4167 | 0 | Out= Robertstown - MWP4 - Waterloo East O/S(offloads MWP4 SF), avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
#KEPWF1_E | 13.3333 | 123.75 | QROW1K.ENERGY * 1 <= 25 (Wt = 360) | Other | DEFAULT | Quick
QN_1200_DYN_TEST | 13.3333 | 3.1667 | QLD to NSW on QNI upper transfer limit of 1200 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | Qld
T_V_NIL_BL1 | 13.3333 | 13.0833 | Out=Nil, Basslink no go zone limits Tas to Vic. Limit Basslink upper limit to 125 MW on 1st DI out of no go zone. i.e. BL <= 125 MW | NIL | Other | Tas
S_DLBAT-G_ISL | 13.25 | 6.75 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Dalrymple Battery (Gen Mode) islanded | Outage | Islanding - Unit | SA
#EDENVSF1_E | 13.1667 | 0 | QORS1E.ENERGY * 1 <= 146 (Wt = 360) | Other | DEFAULT | Quick
S>NIL_BWMP_HUWT | 13.0833 | 9.9167 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
NQ_750_DYN_TEST | 12.8333 | 0 | NSW to QLD on QNI upper transfer limit of 750 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | NSW
V_VS_MLMO_NETT | 12.8333 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage | FCAS | Vic
#MOUSF1_E | 12.75 | 80.5 | QMRR1M.ENERGY * 1 <= 82 (Wt = 360) | Other | DEFAULT | Quick
Q_STR_7C2K_RRSF_7 | 12.5 | 19 | Limit to Ross River Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_SMSF_7 | 12.5 | 13.5 | Limit to Sun Metals Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N>>LDTM_964_81_OPEN | 12.4167 | 5.25 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage | Thermal | NSW
V>>NIL_SMTX_SMTX_R5 | 12.3333 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 500kV mode, Feedback | NIL | Thermal | Vic
V^^N_DTSS_1 | 12.3333 | 0 | Out = Dapto-Sydney South(11), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^N_UTRV_1 | 12.3333 | 21.5833 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_CWWF_FLT_55 | 12.25 | 8.0833 | Limit Crowlands Wind Farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
NRM_QLD1_NSW1 | 12.0833 | 34 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue | Negative Residue
V_BULGANAWF_FLT_40 | 12.0833 | 0.41667 | Limit Bulgana Wind Farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#YABULU_D_E | 12 | 0 | QTYP.ENERGY * 1 = 83 (Wt = 755) | Other | DEFAULT | Direction
#LYA1_E | 11.8333 | 9.25 | VLYP1.ENERGY * 1 <= 530 (Wt = 360) | Other | DEFAULT | Quick
NC_Q_LILYSF1 | 11.8333 | 0 | Non Conformance Constraint for LILYVALE SOLAR FARM | Other | Non-Conformance | Non-Conformance
Q_NIL_STRGTH_KBWF | 11.6667 | 5.0833 | Out = Nil, limit Kaban Wind farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
V^^N_BURC_1 | 11.5 | 0 | Out = Buronga to Red Cliffs (0X1) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^S_TBCB94_35_SETB | 11.5 | 0 | Out= Tailem Bend 275kV CB6594 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Voltage Stability | SA
S>>RBTU_RBTU_WTTP | 11.4167 | 0 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Waterloo to Templers 132kV line on trip of Robertstown to Tungkillo 275kV line 1 or 2, Feedback | Outage | Thermal | SA
V^^S_PAVC1_SETB | 11.4167 | 1.9167 | Out= Para one SVC(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
Q_HAYMSF1_ZERO | 11.25 | 0 | Hayman solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
V_T_NIL_BL1 | 11.25 | 9.5833 | Out=Nil, Basslink no go zone limits Vic to Tas. Limit Basslink lower limit to -125 MW on 1st DI out of no go zone. i.e. BL >= -125 MW | NIL | Other | Vic
N>>81_964_82 | 11.1667 | 3.25 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, (Note: Swamps if 964 O/S) | Outage | Thermal | NSW
Q_CS_1100 | 11.1667 | 70.6667 | Qld Central to Qld South upper transfer limit of 1100MW (discretionary) | Outage | Discretionary | Qld
N_COLEASF1_FLT_30 | 11.0833 | 0.25 | Limit Coleambally solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_KEP-HYB_29MW | 10.9167 | 0 | Kennedy Energy Park upper limit of 29MW | Outage | Discretionary | Qld
Q_OKYTX3 | 10.9167 | 1.8333 | Out = Oakey 3T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 67.3MW | Outage | Thermal | Qld
S>>X_RBTU+RBTX_10 | 10.9167 | 20.6667 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Templers- Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
N>>NIL_8U_86_S | 10.8333 | 0 | Out= NIL, avoid O/L Armidale to Uralla (8U) on trip of Armidale to Tamworth (86) line, Feedback | NIL | Thermal | NSW
N>NIL_999 | 10.8333 | 0 | Out= Nil, avoid O/L Bango999 to Cowra (999) on trip of Nil, Feedback | NIL | Thermal | NSW
N^^V_2_6X_3J_1 | 10.8333 | 0 | Out = Ravine-Yass or Upper Tumut to Ravine (2 or 6X) 330kV line and Gullen Range to Yass (3J), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_COLEASF1_FLT_45 | 10.8333 | 5.3333 | Limit Coleambally solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C2K_KIDSF_7 | 10.8333 | 19.5 | Limit to Kidston Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>BWMP_BRTW_WTTP | 10.75 | 9 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
VSML_110 | 10.75 | 1.6667 | Vic to SA on ML upper transfer limit of 110 MW | Outage | Discretionary | Vic
V_MC_SH_WF_600 | 10.75 | 13 | Limit the total MW from Macarthur and Stockyard Hill WF <= 600 MW to maintain generation contingency size in Victoria. | Outage | Discretionary | Vic
S>>X_RBTU+RBTX_14 | 10.6667 | 32.75 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of remaining Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
Q_STR_7C8C_KIDSF | 10.6667 | 5.5833 | Limit Kidston Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
S-MAPS3-PV_0 | 10.6667 | 0 | Discretionary upper limit for SA WATER Mannum Adelaide Pumping Station No 3 PV (Kanmantoo) generation of 0 MW | Outage | Unit Zero | SA
T>T_NIL_BL_IMP_7C | 10.5 | 13.4167 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
Q>NIL_DRLCLB_NIL | 10.4167 | 0 | Out= Nil, avoid OL on 7490 or 7491 (T280 Drillham to T194 Columboola) 132kV feeder, NIL trip. Feedback | NIL | Thermal | Qld
T_T_FASH_HM_OPEN_1 | 10.4167 | 0 | Out = one Farrell to Sheffield 220kV line, West Coast 220/110 kV parallel open, Farrell 220 kV bus not split, limit West Coast gen <= 110% of West Coast load | Outage | Other | Tas
Q^^N_TW+LS_SVC_SRAR | 10.3333 | 0 | Out = Tamworth SVC and Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
S>>X_RBPA+RBTX2_16 | 10.25 | 28 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo East-Waterloo 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
N>>994_99F_63 | 10.0833 | 22.5833 | Out= Narrandera to Wagga (994) 132kV line, avoid O/L Yanco to Uranquinty (99F) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,(Note: Option C on OM521) | Outage | Thermal | NSW
V_BANSF_BBD_80 | 10.0833 | 30.3333 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
T_GRANVH_ZERO | 10 | 0 | Granville Harbour wind farm upper limit of 0 MW | Outage | Unit Zero | Tas
Q_STR_7C2K_HAMSF_7 | 9.9167 | 15.1667 | Limit to Hamilton Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S_BRBG_CMWF_0 | 9.9167 | 0 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | Unit Zero | SA
Q_STR_7C2K_DAYSF_7 | 9.9167 | 16.6667 | Limit to Daydream Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N_DARLSF_FLT_80 | 9.8333 | 0 | Limit Darlington Pt Solar Farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_TARALGAWF_005 | 9.75 | 359.9167 | Taralga WF upper limit of 5 MW | Outage | Discretionary | NSW
TVBL_ROC | 9.75 | 6.4167 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Tas
Q_WARMR_736_SF2 | 9.6667 | 0 | Out= Warwick to Middle Ridge 110kV feeder (736), limit Warwick SF2 to 20MW as per Ergon ramp down scheme | Outage | Thermal | Qld
S>>X_RBTX+MNWT_24 | 9.6667 | 0 | Out= One Robertstown 275/132 kV TX + Mintaro-Waterloo 132 kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX2 on trip of Waterloo East-Waterloo 132 kV line, Feedback | Outage | Thermal | SA
V>SMLMHNW1 | 9.6667 | 0 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | Vic
NC_Q_MPP_2 | 9.5833 | 47.3333 | Non Conformance Constraint for Millmerran 2 Power Station | Other | Non-Conformance | Non-Conformance
Q_STR_7C0K_HASF_1 | 9.5833 | 0 | No limit to Haughton Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>2_NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N_SILVERTWF_FLT_100 | 9.5 | 1.25 | Limit Silverton Wind Farm upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
S>NIL_RBMWP3_RBNW1 | 9.5 | 15.1667 | Out= Nil, avoid O/L Robertstown-North West Bend #1 132kV line on trip of Robertstown-Morgan Pipeline 3-Morgan Pipeline 2-Morgan Pipeline 1-North West Bend 132kV #2 line, Feedback | NIL | Thermal | SA
N::Q_DM_TW_SVC_KC | 9.3333 | 0 | Out = Dumaresq or Tamworth SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
N>>NIL_84_83_OPEN | 9.3333 | 6 | Out = Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | Thermal | NSW
N>N-BEBO-94B-1 | 9.3333 | 0 | Out= Beryl to Bodangora WF 132kV line (94B/2), avoid O/L Crudine Ridge WF to Ilford Tee (9ML/1) on trip of Nil, Feedback | Outage | Thermal | NSW
S>>BWMP_DVBR_RHBG-T | 9.3333 | 17.5 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill- Brinkworth 132kV T line on trip of Davenport-Brinkworth 275kV line, Feedback | Outage | Thermal | SA
N>MPWW_94T_71 | 9.25 | 0 | Out = Mt. Piper to Wallerawang (70 or 71), avoid O/L Molong to Orange North (94T) on trip of the remaining Mt Piper to Wallerawang (71 or 70), [Note: Line 94E O/S as per OM521] | Outage | Thermal | NSW
S>V_460_DYN | 9.1667 | 2.6667 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | SA
Q_STR_7C2K_COLSF_7 | 9.0833 | 15.9167 | Limit to Collinsville Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S:V_XPAVC_310 | 9.0833 | 26.4167 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
S>>X_RBPA+RBTX2_22 | 8.9167 | 38.1667 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo-Templers 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
Q_WARMR_736_SF1 | 8.6667 | 0 | Out= Warwick to Middle Ridge 110kV feeder (736), limit Warwick SF1 to 20MW as per Ergon ramp down scheme | Outage | Thermal | Qld
N_DARLSF1_ZERO | 8.5 | 0 | Darlington Point solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q_YARANSF1_37 | 8.5 | 17.8333 | Yarranlea Solar Farm upper limit of 37 MW | Outage | Discretionary | Qld
T_GRANVH_060 | 8.5 | 0 | Discretionary 60 MW upper limit on Granville Harbour Wind Farm | Outage | Discretionary | Tas
V_MACARTHUR_ZERO | 8.5 | 0 | Macarthur upper limit of 0 MW | Outage | Unit Zero | Vic
V::S_PAVC1_SETB | 8.4167 | 3.0833 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
T>NIL_SH_IMPORT | 8.3333 | 0 | Credible risk of losing entire Sheffield 220kV network, Limit importing flow into Sheffield on Sheffield to Palmerston and Sheffield to George Town 220kV lines to <= 10 MVA. Feedback | Outage | Other | Tas
CA_SYDS_5494AABA_1 | 8.25 | 0 | Constraint Automation, O/L 99F:L99F:Z:132@NARRAND@NSW for Nil Trip Base Case. Generated by STNET[NORCR1] Host NORREGEEMP7(EMPSYD) | Outage | Thermal | Constraint Automation
Q_STR_7C2K_HAYSF_7 | 8 | 20.5833 | Limit to Hayman Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_RUGSF | 8 | 3.6667 | Limit Rugby Run Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
V::N_SETB_O1 | 8 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V^^N_HWSM_1 | 8 | 0 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V::N_X_SMSC_O2 | 7.9167 | 94.9167 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
N>966+KK_966/1_NIL | 7.8333 | 0 | Out= 966 (Armidale to Koolkhan) 132kV line [NOTE: Open at Koolkan end ONLY, Armidale end remains closed] O/S , avoid O/L Metz Tee to Armidale (966/1) kV line on trip of Nil, Feedback | Outage | Thermal | NSW
V::N_MLTX_xxx | 7.75 | 0 | Out = Moorabool Transformer 500/220kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::N_X_ARWBBA_xxx | 7.6667 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
N>947_94T | 7.5833 | 0 | Out= Wellington to Orange North (947) 132kV line, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
N>>NIL_4 | 7.5833 | 0.5 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL | Thermal | NSW
Q^^N_LS_SVC_SRAR | 7.5833 | 0 | Out = Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
T_WCOAST_220G_144 | 7.5 | 0 | Total generation of Bastyan, Granville Harbour, John Butters, Tribute, Reece 1 and 2 limited to <= 144 MW | Outage | Discretionary | Tas
VSML_165 | 7.5 | 6.9167 | Vic to SA on ML upper transfer limit of 165 MW | Outage | Discretionary | Vic
N>NIL_94B | 7.4167 | 12.5 | Out= Nil, avoid O/L Beryl to Wellington 132 kV (94B/1) on nil trip, Feedback. Metering at Wellington is used | NIL | Thermal | NSW
Q_STR_7C8C_COLSF | 7.4167 | 1.1667 | Limit Collinsville Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
S_LB2WF_CONF | 7.3333 | 2.9167 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | Voltage Stability | SA
Q_STR_7C8C_DAYSF | 7.25 | 1.0833 | Limit Daydream Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
#METZSF1_E | 7.0833 | 3.5 | NMTZ1M.ENERGY * 1 <= 115 (Wt = 360) | Other | DEFAULT | Quick
N_NYNGANSF_010 | 7.0833 | 0 | Nyngan Solar Farm upper limit of 10 MW | Outage | Discretionary | NSW
N>GITN-96R_967_89 | 7 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89),(Noted: Swamped out when 967 O/S) | Outage | Thermal | NSW
V^^N_CRGR_1 | 6.9167 | 0 | Out = Crookwell to Gullen Range (3H), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N>72_94T_79 | 6.75 | 0 | Out = Mt Piper to Wellington line (72), avoid O/L on Molong to Orange North (94T) on trip of Wellington to Wollar West (79), Feedback | Outage | Thermal | NSW
T::T_GTHA_2 | 6.75 | 0 | Out = George Town to Hadspen 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage | Transient Stability | Tas
V::N_SETB_O2 | 6.75 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
VSML_020 | 6.6667 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage | Discretionary | Vic
#DPNTBL1_E | 6.5833 | 0 | NRDP2D.ENERGY * 1 <= 25 (Wt = 360) | Other | DEFAULT | Quick
N>96L/96R_967_89_S | 6.5833 | 0 | Out= Lismore to Tenterfield (96L) or Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Lismore to Koolkhan (967) 132kV line on trip of Lismore to Coffs Harbour (89) 330kV line, Feedback | Outage | Thermal | NSW
T>T_NIL_BL_110_4 | 6.5833 | 8.75 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Thermal | Tas
V^^N_LTMS_1 | 6.5833 | 0 | Out = Murray to Lower Tumut 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q>NIL_757_758_ECS | 6.4167 | 40.5 | Out= Nil, ECS for managing Mudgeeraba to Terranora (757 or 758) 110kV lines, Summer and Winter ECS ratings selected by SCADA status | NIL | Thermal | Qld
V^^N_SDUT_1 | 6.4167 | 2.0833 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N_SUNRSF_FLT_120 | 6.3333 | 5.9167 | Limit Sunraysia solar farm upper limit to 120 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
VT_250 | 6.3333 | 0 | Vic to Tas on Basslink upper limit of 250 MW | Outage | Discretionary | Vic
V^T_NIL_9 | 6.3333 | 24.4167 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL | Voltage Stability | Vic
N::Q_ARSR_1 | 6.25 | 0 | Out= Armidale - Saphhire (8E) 330kV line, NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | Transient Stability | NSW
N>999_9GL_NIL | 6.25 | 1 | Out= Bango999 WF to Cowra 132kV line(999), avoid O/L Bango973 to Yass (9GL) on trip of Nil, Feedback | Outage | Thermal | NSW
N>>3H_998_4 | 6.25 | 0 | Out = Crookwell to Gullen Range(3H) 330kV line, avoid O/L Cowra to Forbes (998) 132kV line on trip of Collector to Marulan (4) 330kV line, Feedback | Outage | Thermal | NSW
Q_KEP-HYB_50MW | 6.25 | 0 | Kennedy Energy Park upper limit of 50MW | Outage | Discretionary | Qld
S::V_TBSE_TBSE_2 | 6.25 | 1.0833 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
S:VS_PA_SVC_620 | 6.25 | 9.9167 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murraylink upper transfer limit of 620 MW | Outage | Oscillatory Stability | SA
V^^S_PAVC1_MAXG | 6.25 | 2 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
S>>WEWT_BWPA_WTTP | 6.1667 | 0 | Out= Waterloo East-Waterloo 132kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V>>NIL_RCWE_HOMRKM | 6.1667 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
S>V_460 | 6.0833 | 2 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage | Thermal | SA
NC_N_RESS2_ADG1 | 6 | 0 | Non Conformance Constraint for RESS2_ADG1 | Other | Non-Conformance | Non-Conformance
Q>>BCRG_BCCP_CLWU | 6 | 2.3333 | Out= Bouldercombe to Raglan (811), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
S_ISLE_CRK_60 | 6 | 0 | Discretionary upper limit on Cathedral Rocks windfarm <=60 MW when 4 syn cons I/S for SA is at risk of islanding - otherwise limited to 10 MW | Outage | Discretionary | SA
V_KARADSF_FLT_54 | 6 | 9.5 | Limit Karadoc solar Farm upper limit to 54 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>947+949_94T | 5.9167 | 0 | Out= Wellington to Orange North (947) 132kV line + Orange North to Mt Piper (949) 132kV line, avoid O/L Molong to Orange North (94T) 132kV line, Feedback | Outage | Thermal | NSW
N_STWF1_ZERO | 5.9167 | 21.1667 | Silverton wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_WEMENSF_FLT_53 | 5.9167 | 4.0833 | Limit Wemen Solar Farm upper limit to 53 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>NIL_997/2_62 | 5.75 | 0 | Out= NIL, avoid O/L Mulwala to Corowa (997/2) 132kV line on trip of Wagga to Jindera (62) 330kV line, Feedback | NIL | Thermal | NSW
Q_STR_7C8C_HAMSF | 5.75 | 0.5 | Limit Hamilton Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
Q_STR_7C8C_RRSF | 5.75 | 5.8333 | Limit Ross River Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
Q_STR_SMSF_ZERO | 5.75 | 0 | Limit 0MW to Sun Metals Solar farm for system strength requirement | Outage | System Strength | Qld
Q_YARANSF1_ZERO | 5.75 | 6.1667 | Yarranlea Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V_YATPSF_FLT_49 | 5.75 | 9.6667 | Limit Yatpool solar Farm upper limit to 49 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N^^V_JNWG_63_X5_1 | 5.6667 | 0.75 | Out = Jindera to Wagga(62) 330kV line, 63 + X5 open, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>>RBTX_TWPA_TPRS | 5.6667 | 24.0833 | Out= one Robertstown 275/132kV transformed, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
Q_DAYDSF1_ZERO | 5.5833 | 0 | Daydream solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
V>>NIL_SMTX_SMTX_R2 | 5.5833 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 220kV mode, Feedback | NIL | Thermal | Vic
N>>NIL_996_62 | 5.5 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback (Note: constraint swamped when 996 is O/S) | NIL | Thermal | NSW
Q_STR_7C8C_SMSF | 5.5 | 0 | Limit Sun Metals Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
V_BANNERTSF_FLT_53 | 5.5 | 9.1667 | Limit Bannerton Solar Farm upper limit to 53 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
QN_1200_TEST | 5.4167 | 0.83333 | Qld to NSW on QNI upper transfer limit of 1200 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | Qld
Q_STR_7C2K_WHTSF_7 | 5.4167 | 13.3333 | Limit to Whitsunday Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_HAYSF | 5.4167 | 1.0833 | Limit Hayman Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
V>>V_DDSM_1 | 5.4167 | 136.9167 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Thermal | Vic
Q_MARYRSF1_ZERO | 5.3333 | 0 | Maryrorough Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>>PA6509_BWPA_RBTU | 5.3333 | 0 | Out= Para 275kV CB6509, avoid O/L Robertstown-Tungkillo 275kV line 1 or 2 on trip of Munno Para-Para 275kV line (this offloads Tungkillo-Para 275kV line 2 & Blyth West-Munno Para 275kV line & Munno Para TX), Feedback | Outage | Thermal | SA
S>V_RBNW_RBMWP3 | 5.3333 | 0.33333 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage | Thermal | SA
V>DDMB_MBDD_EPTT | 5.3333 | 0 | Out= one Dederang to Mount Beauty 220 kV line, avoid O/L the remaining Mount Beauty to Dederang 220kV line on trip of the Eildon to Thomastown 220 kV line, feedback | Outage | Thermal | Vic
N::N_CRGR_2 | 5.25 | 0 | Out = Crookwell to Gullen Range (3H), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | Transient Stability | NSW
S>VMLMHNW1 | 5.25 | 0 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | SA
V_COHUNASF_FLT_17 | 5.0833 | 3.1667 | Limit Cohuna Solar Farm upper limit to 17 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_BROKENHSF_FLT_32 | 5 | 5.4167 | Limit Broken Hill Solar Farm upper limit to 32 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_DARLSF_FLT_100 | 5 | 8.4167 | Limit Darlington Pt Solar Farm upper limit to 100 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_WRWF1_ZERO | 5 | 10.1667 | White Rock WF upper limit of 0 MW and all turbines disconnected | Outage | Unit Zero | NSW
Q_STR_7C2K_KBWF_12 | 5 | 0 | No limit to Kaban if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton syncon ON(Haughton syncon OFF 50% daytime,100% at night) ,1% if Kar < 2 or Kareeya >=2, NQLD>250&Ross_FN>100, Zero otherwise. | Outage | System Strength | Qld
T>T_NWSD_110_1 | 5 | 0.66667 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752, avoid O/L Scottsdale Tee to Norwood 110kV line on Nil trip, Feedback | Outage | Thermal | Tas
N_LIMOSF1_FLT_132 | 4.9167 | 3.9167 | Limit Limondale 1 solar farm upper limit to 132 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>N-MUTE_758 | 4.9167 | 6.0833 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
#HILLSTN1_E | 4.8333 | 2.4167 | NDNH1H.ENERGY * 1 <= 85 (Wt = 360) | Other | DEFAULT | Quick
N::N_CNCW_2 | 4.8333 | 7.75 | Out = Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line | Outage | Transient Stability | NSW
VSML_100 | 4.8333 | 0 | Vic to SA on ML upper transfer limit of 100 MW | Outage | Discretionary | Vic
#NSW1-QLD1_RAMP_I_F | 4.75 | 4 | NSW1-QLD1 >= MIN(-122, InitialFlow + 200) (Wt=35) | Other | Ramping | Quick
S>>NIL_RBTU_RBPA | 4.75 | 1.5833 | Out= Nil, avoid O/L Robertstown-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
V>>RCWE_DPTX_ARWB | 4.75 | 0 | Out= Any 220kV line section between Red Cliffs and Wemen, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Ararat to Waubra to Ballarat 220kV line, Feedback | Outage | Thermal | Vic
N>9R6_9R5_901 | 4.6667 | 0 | Out= 9R6 (Wagga North to Wagga 132) 132kV line, avoid O/L Wagga North to Wagga (9R5) on trip of Temora to Wyalong 132kV (901) line, Feedback | Outage | Thermal | NSW
N>N-BAMB_132_OPEN_B | 4.6667 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage | Thermal | NSW
NC_V_YENDWF1 | 4.6667 | 0 | Non Conformance Constraint for YENDON WIND FARM 1 | Other | Non-Conformance | Non-Conformance
N_FINLYSF_FLT_93 | 4.6667 | 7.5 | Limit Finley solar farm upper limit to 93 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S>RBTX2_RBTX1_WEMWP4 | 4.6667 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage | Thermal | SA
V::S_TBCP1_MAXG | 4.6667 | 0.083333 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage | Transient Stability | SA
V_MTMERCER_ZERO | 4.6667 | 2.0833 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Unit Zero | Vic
N>945_94T | 4.5833 | 0 | Out= Wellington to Molong (945) 132kV line, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
N>9U6/9U7_8507_9U7 | 4.5833 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L Balina to Astonville (8507) 66kV line on trip of other 9U7 or 9U6 132kV line, Feedback | Outage | Thermal | NSW
N>>NIL_5_61_N | 4.5833 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) 330kV line on trip of Crookwell to Bannaby (61) 330kV line, Feedback | NIL | Thermal | NSW
N_LIMOSF2_FLT_18 | 4.5833 | 3.75 | Limit Limondale 2 solar farm upper limit to 18 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S>>TBTU_TBTU_TBMO | 4.5833 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of remaining Tailem Bend-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>V_MWP3RB_RBNW1 | 4.5833 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L Roberstown-North West Bend 132kV line on trip of Nil trip, Feedback | Outage | Thermal | SA
V^^S_TBEBUS_MAXG | 4.5833 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA | Outage | Voltage Stability | SA
V_OAKHILL_TFB_42 | 4.5833 | 0 | Out = Nil, Oaklands Hill Windfarm upper limit of 42.7 MW due to Oaklands Hill windfarm TFB mode operation, DS only. Swamp out if TFB mode is OFF | NIL | Discretionary | Vic
N>NIL_9R6 | 4.5 | 0 | Out= NIL, avoid O/L Wagga North - Wagga (9R6) 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
N_WRWSF_ZERO | 4.5 | 12.4167 | White Rock wind farm and White Rock solar farm upper limit of zero MW | Outage | Discretionary | NSW
Q_STR_7C2K_KBWF_13 | 4.5 | 0 | Limit 40% to Kaban WF if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG) (100% if Haughton Syncon ON or at night, 1% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_KEP | 4.5 | 0 | Limit Kennedy Energy Park output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
Q_CHILDSF1_ZERO | 4.4167 | 1.0833 | Childers Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
V_MACWF_FLT_0 | 4.4167 | 24.1667 | Limit Macarthur Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>>RBTU_RBTU_WEWT | 4.3333 | 0 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Waterloo East to Waterloo #1 132kV line on trip of Robertstown to Tungkillo 275kV line 1 or 2, Feedback | Outage | Thermal | SA
V::S_SEVC1_MAXG | 4.3333 | 1 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V>>NIL_ARTSTL_ARCW | 4.3333 | 0 | Out = Nil, avoid O/L Ararat to Stawell 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service, Feedback | NIL | Thermal | Vic
V>>NIL_MLGT_MLGT_A | 4.3333 | 0 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | NIL | Thermal | Vic
CA_SYDS_52C88A79_1 | 4.25 | 0 | Constraint Automation, O/L 65:LSM1:I:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
QNI_SOUTH_1000_DYN | 4.25 | 0 | QLD to NSW on QNI upper transfer limit of 1000 MW, dynamic headroom with Max calc on the QNI, DS formulation only. | Outage | Transient Stability | Qld
V_ARARATWF_FLT_160 | 4.25 | 0 | Limit Ararat Wind Farm upper limit to 160 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
NQ_750_TEST | 4.1667 | 0 | NSW to Qld on QNI upper transfer limit of 750 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | NSW
S>NIL_PL_GENMAX_YDMD | 4.1667 | 2.5833 | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating. | NIL | Thermal | SA
NC_V_MUWAWF2 | 4.0833 | 1.9167 | Non Conformance Constraint for MUWAWF2 | Other | Non-Conformance | Non-Conformance
Q_STR_7C0K_SMSF_1 | 4.0833 | 0 | No limit to Sun metals Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
N^^V_BADP_1 | 4 | 4.75 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_COLEASF1_FLT_105 | 4 | 1.0833 | Limit Coleambally solar farm upper limit to 105 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>NIL_TV66 | 4 | 10.6667 | Out=Nil, limit Sun metals SF and Mt Stuart GTs to avoid over load on 66kV feeders on trip of one of the 66kV feeders in the Townsville area | NIL | Thermal | Qld
Q_STR_7C0K_COLSF_1 | 4 | 0 | No limit to Collinsville Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_DAYSF_1 | 4 | 0 | No limit to Daydream Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_HAMSF_1 | 4 | 0 | No limit to Hamilton Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_RRSF_1 | 4 | 0 | No limit to Ross River Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
N>79_94T_72 | 3.9167 | 0 | Out= Wollar West to Wellington (79) 330kV line or Wollar 500/330kV TX or Wollar to Wollar West (75) 330kV line, avoid O/L on Molong to Orange North (94T) on trip of Wellington to Mt Piper line (72), Feedback | Outage | Thermal | NSW
V>>N_NIL_65 | 3.9167 | 10.3333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Thermal | Vic
CA_BRIS_542A136B_1 | 3.8333 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage | Thermal | Constraint Automation
NC_S_STARHLWF | 3.8333 | 2.8333 | Non Conformance Constraint for Starfish Hill Wind Farm | Other | Non-Conformance | Non-Conformance
S>>RBTX1_RBTX2_WTTP | 3.8333 | 0 | Out= one Robertstown 275/132kV TX, avoid O/L Waterloo-Templers 132kV line on trip of remaining Robertstown 132/275kV TX, Feedback | Outage | Thermal | SA
S^NIL_PL_MAX | 3.8333 | 41.9167 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | Voltage Stability | SA
Q_KEP-HYB_35MW | 3.75 | 0 | Kennedy Energy Park upper limit of 35MW | Outage | Discretionary | Qld
S>>X_CR+RBTX+TPRS_13 | 3.75 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
S>>X_RBPA+RBTX_06 | 3.75 | 0 | Out=Robertstown-Para 275 kV line + one Robertstown TX 275/132 kV, avoid O/L remaining Robertstown 275/132kV TX on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
T:T_LIPM_1 | 3.75 | 0.5 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South). Swamp if no Gordon units online. | Outage | Transient Stability | Tas
N>945_94K1 | 3.6667 | 0 | Out= Wellington to Molong 132kV line (945), avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | Outage | Thermal | NSW
NC_V_GLRWNSF1 | 3.6667 | 0 | Non Conformance Constraint for GLENROWAN WEST SF1 | Other | Non-Conformance | Non-Conformance
Q_STR_7C2K_KBWF_10 | 3.6667 | 0 | Limit to Kaban Solar Farm 60% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Haughton Syncon ON, Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_MEWF_13 | 3.6667 | 0 | Limit Mt Emerald Windfarm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),(100% at night),Zero otherwise. | Outage | System Strength | Qld
V::N_HYTR_O1 | 3.6667 | 1.6667 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V>>SML_NIL_7B | 3.6667 | 0.16667 | Out = Nil, avoid O/L Buangor to Ararat 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL | Thermal | Vic
Q^^N_AR+LS_SVC_SRAR | 3.5833 | 0 | Out = Lismore SVC + Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
N_METZSF_106 | 3.5833 | 0 | Metz Solar farm upper limit of 106 MW | Outage | System Strength | NSW
S>>PARB_RBTU_RBMWP4 | 3.5833 | 1.25 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N>NIL_997/1_62 | 3.5 | 0 | Out= NIL, avoid O/L Corowa to Albury (997/1) 132kV line on trip of Wagga to Jindera (62) 330kV line, Feedback | NIL | Thermal | NSW
NC_N_DPNTBESS_ADG1 | 3.5 | 0 | Non Conformance Constraint for DPNTBESS_ADG1 | Other | Non-Conformance | Non-Conformance
NC_Q_MPP_1 | 3.5 | 34.75 | Non Conformance Constraint for Millmerran 1 Power Station | Other | Non-Conformance | Non-Conformance
Q_STR_7C2K_KBWF_17 | 3.5 | 0 | Limit Kaban Solar Farm to 40% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
T^V_NIL_8 | 3.5 | 5.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Voltage Stability | Tas
V>>X5_WBBA_KGBE | 3.5 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
V^^S_MLSY_3 | 3.5 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage | Voltage Stability | Vic
V_KIAMSF_FLT_120 | 3.4167 | 4.5833 | Limit Kiamal Solar Farm upper limit to 120 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_STR_7C0K_CLRSF_1 | 3.4167 | 0 | No limit to Clare Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_HAYSF_1 | 3.4167 | 0 | No limit to Hayman Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_KEP_1 | 3.4167 | 0 | No limit to Kennedy Energy Park if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_KIDSF_1 | 3.4167 | 0 | No limit to Kidston Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_MEWF_1 | 3.4167 | 0 | No limit to Mt Emerald Wind Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_RUGSF_1 | 3.4167 | 0 | No limit to Rugby Run Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_WHTSF_1 | 3.4167 | 0 | No limit to Whitsunday Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
N>>3H_5_4_N | 3.3333 | 0 | Out = Crookwell to Gullen Range (3H), avoid O/L Yass to Marulan (5) 330kV line on trip of Collector to Marulan (4) 330kV line, Feedback | Outage | Thermal | NSW
Q^^N_NIL_SRAR | 3.3333 | 279.25 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Voltage Stability | Qld
Q_STR_7C0K_COLSF_2 | 3.3333 | 0 | Limit Collinsville SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_KBWF_18 | 3.3333 | 0 | Limit to Kaban Wind Farm 40% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), 80% at night, Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_KBWF_7 | 3.3333 | 0 | Limit to Kaban Solar Farm 25% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG),1% if NQLD>250&270(AVG),Ross_FN>100&120(AVG), Zero otherwise. | Outage | System Strength | Qld
V>>ARWB_X3_BEKG | 3.3333 | 0 | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage | Thermal | Vic
N>N_LSDU_9U6_2 | 3.25 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage | Thermal | NSW
#DPNTBG1_E | 3.1667 | 0 | NRDP1D.ENERGY * 1 <= 25 (Wt = 360) | Other | DEFAULT | Quick
N::Q_BWTX_KC | 3.1667 | 0 | Out= Bayswater 500/330kV tie Tx, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
N>N-BAMB_132_OPEN_A | 3.1667 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | Thermal | NSW
NC_Q_HAUGHT11 | 3.1667 | 0 | Non Conformance Constraint for HAUGHTON SOLAR FARM | Other | Non-Conformance | Non-Conformance
V>>BUCW_DPTX_KGBE | 3.0833 | 0 | Out= Bulgana to Crowlands 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
V^SML_KGRC_4 | 3.0833 | 0 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Voltage Stability | Vic
Q_STR_7C0K_SMSF_2 | 3 | 0 | Limit Sun Metals SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_WHTSF | 3 | 1 | Limit Whitsunday Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
T>T_NIL_BL_220_6B | 3 | 0 | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Thermal | Tas
V>>XGTML2_KTTX2_1_R2 | 3 | 0 | Out= Geelong to Moorabool No.2 220kV line and Keilor A2 500/220kV transformer, avoid O/L Moorabool to Geelong No.1 220kV line on trip of Sydenham to Keilor 500kV line (offloading Keilor A4 500/220kV transformer), radial mode, YWPS1 on 220kV mode, Feedback | Outage | Thermal | Vic
VSML_ZERO | 3 | 2.5833 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | Vic
T^V_HAPM_220_1 | 2.9167 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage | Voltage Stability | Tas
N>>NIL_39_17 | 2.8333 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL | Thermal | NSW
NC_V_GANNSF1 | 2.8333 | 0.16667 | Non Conformance Constraint for GANNAWARRA SOLAR | Other | Non-Conformance | Non-Conformance
N^^V_DTSS_1 | 2.8333 | 0 | Out = Dapto-Sydney South(11), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_7C0K_RRSF_2 | 2.8333 | 0 | Limit Ross River SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_CLRSF_7 | 2.8333 | 16 | Limit to Clare Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>MKRB_CNRB_WEMWP4 | 2.8333 | 4.25 | Out= Mokota-Robertstown 275kV line, avoid O/L Morgan Whyalla 4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage | Thermal | SA
VS_250 | 2.8333 | 4 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Discretionary | Vic
V_OWF_TGTSNRBHTN_30 | 2.8333 | 11.3333 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Discretionary | Vic
N::Q_MUTW_1 | 2.75 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | Transient Stability | NSW
N>N-X_9U6_9G2_2 | 2.75 | 0 | Out = one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 132kV line between Mullumbimby and Ballina (9G2, 9G3, 9G4 or 9G5), avoid O/L remaining 132kV line, Qld to NSW limit | Outage | Thermal | NSW
Q_STR_7C0K_DAYSF_2 | 2.75 | 0 | Limit Daydream SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_MEWF | 2.75 | 0 | No limit to Mt Emerald Wind farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_MEWF_12 | 2.75 | 0 | Limit Mt Emerald Wind Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
T>T_GTSH_IMP_4K | 2.75 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
VSML_060 | 2.75 | 0 | Vic to SA on ML upper transfer limit of 60 MW | Outage | Discretionary | Vic
Q_STR_7C8C_CLRSF | 2.6667 | 2.6667 | Limit Clare Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
S:VS_700_HY_TEST_DYN | 2.6667 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
T_T_FASH_HM_OPEN_2 | 2.6667 | 0 | Out = one Farrell to Sheffield 220kV line, West Coast 220/110 kV parallel open, Farrell 220 kV bus not split, limit West Coast gen >= 90% of West Coast load | Outage | Other | Tas
V>>BAML1_ELML_BAML2 | 2.6667 | 0 | Out= Ballarat to Moorabool No.1 220kV line, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | Outage | Thermal | Vic
CA_SYDS_544A2F7F_2 | 2.5833 | 0 | Constraint Automation, O/L 998:L998:I:132@COWRA@NSW for CTG LNQT on trip of COLLECWF-MARULAN 4 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP7(EMPSYD) | Outage | Thermal | Constraint Automation
N>96M_969_NIL | 2.5833 | 0 | Out= Any one 132kV feeder between Moree to Boggabri East (96M,9UH,9UJ),avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | Outage | Thermal | NSW
NC_N_NEWENSF1 | 2.5833 | 0 | Non Conformance Constraint for NEW ENGLAND GS1 | Other | Non-Conformance | Non-Conformance
NSA_T_DVGATE_10 | 2.5833 | 0 | Devils Gate >= 10 MW for Network Support Agreement | Outage | Network Support | Tas
S>>NIL_RBTU_WEWT | 2.5833 | 20.1667 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of one Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
Q_MIDDLSF1_ZERO | 2.5 | 0.16667 | Middlemount Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V^^N_CNCW_1 | 2.5 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^S_NIL_MAXG_xxx | 2.5 | 1.4167 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Voltage Stability | SA
#HEZ1_E | 2.4167 | 0 | NNEE1H.ENERGY * 1 <= 18 (Wt = 360) | Other | DEFAULT | Quick
NC_N_NEWENSF2 | 2.4167 | 0 | Non Conformance Constraint for NEW ENGLAND GS2 | Other | Non-Conformance | Non-Conformance
N^^Q_ARTW_B1 | 2.4167 | 17 | Out = Armidale to Tamworth (85 or 86 or 8U), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | Voltage Stability | NSW
S::V_TBSE_TBSE | 2.4167 | 107 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
T>T_FASH_3_N-2 | 2.4167 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV line (flow to Burnie) for loss of both Farrell to Sheffield 220 kV lines | Outage | Thermal | Tas
T_FARC2_2 | 2.4167 | 0 | Out=Farrell - Reece 2 220KV line. Discretionary 144 MW limit on Reece 1 + Granville Harbour WF | Outage | Discretionary | Tas
V::S_TBEBUS_SETB | 2.4167 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage | Transient Stability | SA
T_T_FASH2_1 | 2.3333 | 0 | Out = Farrell 220 kV bus split, limit John Butters, Bastyan and Mackintosh to less than 110% West Coast load | Outage | Other | Tas
V^^S_SETB_TBSE_2 | 2.3333 | 5 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Voltage Stability | SA
CA_SYDS_53C9C000_1 | 2.25 | 0 | Constraint Automation, O/L XFMR 4H@DARL_PT@NSW for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP7(EMPSYD) | Outage | Thermal | Constraint Automation
Q_STR_7C0K_HAMSF_2 | 2.25 | 0 | Limit Hamilton SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
S>>NIL_RBTX_RBTX_1 | 2.25 | 0 | Out= Nil, avoid O/L of one Robertstown 275/132kV TX on trip of other Robertstown 275/132kV TX, Feedback | NIL | Thermal | SA
V:T_HAPM_BL_1 | 2.25 | 0 | Out = Hadspen to Palmerston 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to Palmerston 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
V>>ARWB_DPTX_KGBE | 2.25 | 0 | Out= Any 220kV line section between Ararat and Ballarat, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
V>>NIL_BABE_KMRC | 2.25 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
V_MTGELIBRAND_66 | 2.25 | 0 | Mt Gelibrand wind farm upper limit of 66 MW | Outage | Discretionary | Vic
N_MOREESF1_055 | 2.1667 | 0 | Moree Solar Farm upper limit of 55 MW | Outage | System Strength | NSW
Q:N_1150 | 2.1667 | 0 | QNI oscillatory stability limit of 1150 MW | Outage | Oscillatory Stability | Qld
Q_STR_7C0K_MEWF_6 | 2.1667 | 0 | Limit 80% to Mt Emerald WF if Stan>=2+Stan+Cal>=3+Glad>=2+(Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% at night), 40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG)(25% if Syncon OFF),Zero otherwise. | Outage | System Strength | Qld
S>>X_CNRB+RBTX1_07 | 2.1667 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
N>94T_947_72 | 2.0833 | 0 | Out= Molong to Orange North (94T) 132kV line, avoid O/L Wellington to Orange North (947) 132kV line on trip of Wellington to Mt Piper (72) 330kV line, Feedback | Outage | Thermal | NSW
NC_N_VP6 | 2.0833 | 1 | Non Conformance Constraint for Vales Point VP6 Power Station | Other | Non-Conformance | Non-Conformance
N^^V_LTWG_1 | 2.0833 | 2.25 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S-OUT_WTPT_SC+INV_1 | 2.0833 | 2.3333 | Out=HUBG Or HUWT line Or one CB(HU 6135/6060,BG 6246,WT 7022/7021), limit output of Wattle Pt WF based on Wattle Pt statcom status & the number of Dalrymble battery inverters I/S (Note:swamped for No. of Dalrymple bat. inverters < 10 && 1or2 SC O/S) | Outage | Other | SA
T>T_PMSH_IMP_4F | 2.0833 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
CA_BRIS_5347C6C8_1 | 2 | 0 | Constraint Automation, O/L SNWHUM_T:LHS:I:132@BUNGAM@SA for CTG LS6X on trip of CLAR_N - MINTAR 132KV LINE. Generated by STNET[BNECR3] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
N>>NIL_39_11 | 2 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | Thermal | NSW
NC_Q_HAYMSF1 | 2 | 10.25 | Non Conformance Constraint for HAYMAN SOLAR FARM | Other | Non-Conformance | Non-Conformance
Q>NIL_SRMB_M020/1 | 2 | 0.75 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Thermal | Qld
S-MAPS2-PV_0 | 2 | 0.33333 | Discretionary upper limit for SA WATER Mannum Adelaide Pumping Station No 2 PV (Palmer) generation of 0 MW | Outage | Unit Zero | SA
V:T_HAGT_BL_1 | 2 | 0 | Out = Hadspen to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to George Town 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
#BHBG1_E | 1.9167 | 0 | NBKB1B.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
#BHBL1_E | 1.9167 | 0 | NBKB2B.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
NC_Q_KSP1 | 1.9167 | 0 | Non Conformance Constraint for Kidston solar farm | Other | Non-Conformance | Non-Conformance
S>>NIL_BWMP_WTTP | 1.9167 | 0.25 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
T>T_GTHA_IMP_4N | 1.9167 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V>>N-62_65_66_RADIAL | 1.9167 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | Vic
V>>NIL_EPTT_DDSM_SIP | 1.9167 | 0 | Out= Nil, avoid O/L Eildon to Thomastown 220kV line on trip of one Dederang to South Morang 330kV line, 5 min line rating, Feedback. Swamp if SIPS not available | NIL | Thermal | Vic
V_BULGANAWF_FLT_60 | 1.9167 | 0 | Limit Bulgana Wind Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_T_FCSPS_RAMP | 1.9167 | 0 | Ramp down (200 MW per DI) Basslink (Vic to Tas) to 144 MW for outage of FCSPS | Outage | Ramping | Vic
N>968_969_NIL | 1.8333 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line, avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | Outage | Thermal | NSW
S^NIL_CRK_VCS_STATUS | 1.8333 | 35.25 | Out= Nil, upper limit for Cathedral Rocks WF based on Mt Millar Voltage Control System (VCS) availability, (Note: CRK <=55 MW when VCS OFF; CRK<= 60 MW when VCS ON) | NIL | Voltage Stability | SA
V::S_RBTU_SETB | 1.8333 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Transient Stability | SA
V^^S_SEVC1_MAXG | 1.8333 | 0.75 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
#MIDDLSF1_E | 1.75 | 2.4167 | QLIS2M.ENERGY * 1 <= 26 (Wt = 360) | Other | DEFAULT | Quick
NC_N_VP5 | 1.75 | 1 | Non Conformance Constraint for Vales Point VP5 Power Station | Other | Non-Conformance | Non-Conformance
N^^V_2+3J+DDSM_1 | 1.75 | 0 | Out = Ravine-Yass (2)/Upper Tumut-Ravine (6X) + Yass-Gullen Range (3J) + one Dederang-South Morang line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_FINLYSF1_ZERO | 1.75 | 0.16667 | Finley solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
S>>CGTB1_TUTB_MOTB | 1.75 | 0.91667 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
T>T_HA_TX | 1.75 | 0 | Out = Hadspen 220/110 kV txfmr, avoid O/L Palmerston 220/110 kV txfmr (flow from 220 kV to 110 kV) on trip of remaining Hadspen 220/110 kV txfmr, feedback | Outage | Thermal | Tas
#V-SA_RAMP_I_F | 1.6667 | 8.5 | V-SA >= MIN(-119, InitialFlow + 50) (Wt=35) | Other | Ramping | Quick
N^^V_MLNK_ARWBBA | 1.6667 | 1.3333 | Out = Murraylink, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | Outage | Voltage Stability | NSW
Q>NIL_MRTX_MRTX_N-2 | 1.6667 | 0 | Out= Nil, avoid O/L Middle Ridge 275/110kV (1T) transformer on trip of remaining Middle Ridge 275/110kV (2T and 3T) transformers, Feedback | Outage | Thermal | Qld
Q_COLUMSF1_ZERO | 1.6667 | 0 | Columboola Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_STR_7C0K_RUGSF_2 | 1.6667 | 0 | Limit Rugby Run SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_SMSF_10 | 1.6667 | 0 | Limit Sun Metals Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
S:V_PASVC_420OSC_AT | 1.6667 | 0 | Out = one Para SVC, Upper transfer limit of 420 MW on SA to VIC on Heywood, Active only when I25 mode cannot be monitored. | Outage | Oscillatory Stability | SA
V::S_PAVC1_MAXG | 1.6667 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | Transient Stability | SA
V::S_RBTU_MAXG_2 | 1.6667 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V_KIAMSF_40INV_DYN | 1.6667 | 1.5833 | Limit Kiamal Solar Farm upper limit to 0 MW if number of inverter available exceeds 40 and Murra Warra 2 WF Syncon O/S. Constraint swamps out otherwise. DS only | Outage | System Strength | Vic
N>>14_39_12 | 1.5833 | 0 | Out = Kemps Creek to Sydney North (14), avoid O/L Bannaby to Sydney West (39) on trip of Sydney South to Liverpool (12) line, Feedback | Outage | Thermal | NSW
NC_Q_DAYDSF1 | 1.5833 | 0 | Non Conformance Constraint for DAYDREAM SOLAR FARM | Other | Non-Conformance | Non-Conformance
QN_1000 | 1.5833 | 0 | Qld to NSW on QNI upper transfer limit of 1000 MW | Outage | Discretionary | Qld
Q_STR_7C2K_HAMSF_10 | 1.5833 | 0 | Limit Hamilton Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_KIDSF_10 | 1.5833 | 0 | Limit Kidston Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
V^^N_2_6X_3J_1 | 1.5833 | 0 | Out = Ravine-Yass or Upper Tumut to Ravine (2 or 6X) 330kV line and Gullen Range to Yass (3J), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N::Q_AR_VC_KC | 1.5 | 0 | Out= Armidale SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
NC_N_SUNTPSF1 | 1.5 | 28.9167 | Non Conformance Constraint for SUNTOP SOLAR FARM | Other | Non-Conformance | Non-Conformance
N_BROKENH1_0INV | 1.5 | 0.83333 | Broken Hill Solar Farm inverter limit of zero. Constraint to violate if Broken Hill Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q-X>RS2TX_TX_TX_O | 1.5 | 0 | Out= Two Ross 275/132 KV transformers, avoid O/L on the remaining Ross 275/132 KV transformer on trip of another Ross 275/132 KV transformer with 132 KV network between Ross and Woree Opened, Feedback | Outage | Thermal | Qld
Q_STR_7C2K_HAYSF_10 | 1.5 | 0 | Limit Hayman Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_WARTX_SF2 | 1.5 | 0 | Out= Warwick 110/33kV Transformer T1 or T2 O/S, limit Warwick SF 2 to 16.7MW as per Ergon ramp down scheme | Outage | Thermal | Qld
S>>NIL_RBTX_RBTX_2 | 1.5 | 0.91667 | Out= Nil, avoid O/L of one Robertstown 132/275kV TX on trip of other Robertstown 132/275kV TX, Feedback | NIL | Thermal | SA
V_BANNERTON_ZERO | 1.5 | 8.9167 | Bannerton Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V_KIATAWF_FLT_18 | 1.5 | 3.0833 | Limit Kiata Wind Farm upper limit to 18 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V_SV_MLMO_NETT | 1.5 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW | Outage | FCAS | Vic
N>>964_88_84_S | 1.4167 | 0.5 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | Outage | Thermal | NSW
N>>NIL_YSTX_LV | 1.4167 | 0 | Out= Nil, avoid O/L Either of Yass 132/330 Transformers on trip of Nil, Feedback | NIL | Thermal | NSW
N^^N_NIL_1 | 1.4167 | 1.9167 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | Voltage Stability | NSW
Q_STR_7C2K_COLSF_10 | 1.4167 | 0 | Limit Collinsville Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_DAYSF_10 | 1.4167 | 0 | Limit Daydream Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_MEWF_9 | 1.4167 | 0 | Limit to Mt Emerald Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_GANWR_SF_BAT_50 | 1.4167 | 3.25 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Discretionary | Vic
#WALGRVG1_E | 1.3333 | 0.83333 | NSWB1W.ENERGY * 1 <= 50 (Wt = 360) | Other | DEFAULT | Quick
NC_N_PARSF1 | 1.3333 | 0 | Non Conformance Constraint for Parkes Solar Farm | Other | Non-Conformance | Non-Conformance
NC_Q_OAKEY1SF | 1.3333 | 2.1667 | Non Conformance Constraint for OAKEY 1 SOLAR FARM | Other | Non-Conformance | Non-Conformance
N_NEWENSF1+2_100-INV | 1.3333 | 0 | New England Solar inverter limit of 100. Constraint to violate if New England Solar inverter availability greater than 100. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q>>LCCP_BCCP_CLWU | 1.3333 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
Q_STR_7C2K_RRSF_10 | 1.3333 | 0 | Limit Ross River Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_RUGSF_10 | 1.3333 | 0 | Limit Rugby Run Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_WARTX_SF1 | 1.3333 | 0 | Out= Warwick 110/33kV Transformer T1 or T2 O/S, limit Warwick SF 1 to 16.7MW as per Ergon ramp down scheme | Outage | Thermal | Qld
S>>BRTW_BWPA_WTTP | 1.3333 | 1.3333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V::S_NIL_TBSE_1 | 1.3333 | 3.1667 | Out = Nil(Both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (Both South East Capacitors (61 and 62) Available). | NIL | Transient Stability | SA
CA_SYDS_52C76ACC_1 | 1.25 | 0 | Constraint Automation, O/L 65:LSM1:I:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR2] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
N>>NIL_5_3L_N | 1.25 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) using 15 mins rating on trip of Yass to Collector (3L) line, Feedback | NIL | Thermal | NSW
NC_N_DARLSF1 | 1.25 | 0.58333 | Non Conformance Constraint for DARLINGTON POINT SF | Other | Non-Conformance | Non-Conformance
N_MOREESF1_21INV | 1.25 | 0 | Moree Solar Farm inverter limit of 21. Constraint to violate if Moree Solar Farm inverter availability greater than 21. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_WSTWYSF1_0INV | 1.25 | 0 | West Wyalong Solar Farm inverter limit of zero. Constraint to violate if West Wyalong Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q>>NIL_BCCP_RGLC | 1.25 | 25.8333 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
Q_STR_7C2K_KBWF_15 | 1.25 | 0 | Limit to Kaban Wind Farm 50% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar>=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), no limit if Haughton syncon ON or at night,1% if Kar < 2 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>V_NIL_NIL_RBMW3 | 1.25 | 0.5 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL | Thermal | SA
SVML_000 | 1.25 | 0 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Discretionary | SA
S_CMWF_0 | 1.25 | 0 | Discretionary upper limit for Clements Gap WF generation of 0 MW | Outage | Unit Zero | SA
V>>DDTX2_DDTX3_DDTX1 | 1.25 | 0 | Out= Dederang H2 txfmr, avoid O/L Dederang H3 330/220kV txfmr on trip of Dederang H1 330/220kV txfmr, Feedback | Outage | Thermal | Vic
V_MWWF_0_WT12 | 1.25 | 0 | Limit Murra Warra Wind Farm upper limit to 0 MW if Murra Warra wind farm turbine collector group 1 and/or 2 generating. Constraint swamp out if only turbine collector group 3 and/or 4 generating. DS only | Outage | System Strength | Vic
N::Q_8C8J_TNT_N-2 | 1.1667 | 0 | Out = Nil, NSW to Qld Transient Stability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | NSW
N>>NIL_DPTX_HV | 1.1667 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL | Thermal | NSW
Q_STR_7C2K_MEWF_14 | 1.1667 | 0 | Limit Mt Emerald WF to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),(80% if Haughton Syncon ON,100% at night),25%(40% if Haughton Syncon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise. | Outage | System Strength | Qld
S>>BWMP_BGBR_HUWT | 1.1667 | 0.16667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap WF), Feedback | Outage | Thermal | SA
S>>NIL_TWPA_BWMP | 1.1667 | 0 | Out= Nil, avoid O/L Blyth West-Munno Para 275kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
S>>X_RBTX+MNWT_18 | 1.1667 | 0 | Out= One Robertstown 275/132 kV TX + Mintaro-Waterloo 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage | Thermal | SA
N::N_CNLT_2 | 1.0833 | 0 | Out = Lower Tumut-Canberra (07), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
N>9R6_9R5_NIL | 1.0833 | 0 | Out= 9R6 (Wagga North to Wagga 132) 132kV line, avoid O/L Wagga North to Wagga (9R5) on trip of Nil, Feedback | Outage | Thermal | NSW
N_COLEASF1_FLT_40 | 1.0833 | 0 | Limit Coleambally solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>COLTX | 1.0833 | 0.58333 | Out = Collinsville North T1 or T2 132/33 kV transformer, limit Collinsville Solar Farm to 33.9MW to prevent overload on RMU of the remaining transformer | Outage | Thermal | Qld
QNTE_OSCILLATE | 1.0833 | 2.8333 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Discretionary | Qld
S>>PARB_TWPA_TPRS | 1.0833 | 0.33333 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S_PPT+SNPT+BLVR_220 | 1.0833 | 0 | SA Pelican Point + Snapper Point generation +Bolivar PS<= 220 MW | Outage | Discretionary | SA
V::N_ROSM_O1 | 1.0833 | 1.25 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V>>NIL_WEKG_HOMRKM | 1.0833 | 0.25 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
NRM_VIC1_NSW1 | 1 | 3.4167 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue | Negative Residue
N_TARALGA1_2WT | 1 | 0 | Constraint to violate if Taralga WF wind turbines ONLINE greater than 2. Dispatch only. swamped out otherwise. DS only. | Outage | System Strength | NSW
Q-CLRSF_MVAR | 1 | 44.1667 | Constraint to violate if Reactive power output of Clare Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q:N_1110 | 1 | 0 | QNI oscillatory stability limit of 1110 MW | Outage | Oscillatory Stability | Qld
Q_NQ_SEMI_RAMP_ZERO | 1 | 37.4167 | Ramp North Qld semi-scheduled generators to zero and hold at zero | Outage | Unit Zero | Qld
Q_YARANSF1_37MW_N-1 | 1 | 12.75 | Limit Yarrenlea Solar Farm to 37 MW when feeder 733/1 or 733/3 or 734/1 or 734/3 (T10 Yarranlea to H14 Middle Ridge) trip, Swamp when the feeders are in service. DS formulation only | NIL | Unit Zero | Qld
V:T_SHGT_BL_1 | 1 | 0 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
V>>N-BUDP_2N | 1 | 0 | Out= Buronga-(X5), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, (Note: assumed Darlington-Wagga 132kV mesh operated CLOSED) | Outage | Thermal | Vic
VS_250_DYN | 1 | 4.6667 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
V^S_HYCP | 1 | 14.5833 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL | Voltage Stability | Vic
CA_SYDS_549FBEF5_1 | 0.91667 | 0 | Constraint Automation, O/L XFMR 1_H4@H4_MUGBA@QLD for CTG TQHQ on trip of H4_MUGBA #5 TRANS. Generated by STNET[BNECR3] Host NORREGEEMP7(EMPSYD) | Outage | Thermal | Constraint Automation
N>>81_964_84 | 0.91667 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tamworth (84) line,(Note: Swamps if 964 O/S) | Outage | Thermal | NSW
N>>NIL_9_18_N | 0.91667 | 0 | Out= Nil, avoid O/L Canberra to Yass (9) using 15 mins rating on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | Thermal | NSW
N>NIL_9R5 | 0.91667 | 0 | Out= NIL, avoid O/L Wagga North-Wagga (9R5) 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
NC_Q_STAN-1 | 0.91667 | 0.083333 | Non Conformance Constraint for Stanwell STAN-1 Power Station | Other | Non-Conformance | Non-Conformance
N^^Q_MIMR_TWO_B1 | 0.91667 | 0 | Out = Two parallel feeders between R4 Millmerran to H14 Middle Ridge (9914+9915 or 9908+9907), avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
N_COLMBSF_60_INV | 0.91667 | 0.75 | Coleambally Solar Farm inverter limit of 60. Constraint to violate if Coleambally Solar Farm inverter availability greater than 60. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_FINLYSF1_0INV | 0.91667 | 3 | Finley Solar Farm inverter limit of zero. Constraint to violate if Finley Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q-RRSF_MVAR | 0.91667 | 44.4167 | Constraint to violate if Reactive power output of Ross River Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-WHTSF_MVAR | 0.91667 | 44.25 | Constraint to violate if Reactive power output of Whitsundays Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q_CLERMSF1_ZERO | 0.91667 | 0.083333 | Clermont Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>>WERB_BWPA_WTTP | 0.91667 | 0 | Out= Robertstown - MWP4 - Waterloo East O/S(offloads MWP4 SF), avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>X_RBTU+RBTX_16 | 0.91667 | 4.25 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage | Thermal | SA
S>WT-BUS_MNWT_SNBG-T | 0.91667 | 0 | Out= Waterloo 132kV South bus outage (this offloads TX 5), avoid O/L Snowtown-Bungama 132kV line on trip of Mintaro-Waterloo 132kV line (this offloads Hummocks-Waterloo 132kV line), Feedback | Outage | Thermal | SA
T^^V_GTHA_1 | 0.91667 | 0 | Out = George Town to Hadspen 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining George Town to Hadspen 220 kV line. | Outage | Voltage Stability | Tas
V::S_NIL_SETB_SECP_1 | 0.91667 | 5.1667 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | Transient Stability | SA
VSML_085 | 0.91667 | 0 | Vic to SA on ML upper transfer limit of 85 MW | Outage | Discretionary | Vic
VSML_FLT_150 | 0.91667 | 0 | Vic to SA on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
V>S_460 | 0.83333 | 14.4167 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage | Thermal | Vic
CA_BRIS_540A554F_1 | 0.83333 | 0 | Constraint Automation, O/L 9R6:L9R6:Z:132@WAGGANTH@NSW for CTG LN7V on trip of YASS-MURRUMBR 99M 132KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP5(EMPBRI) | Outage | Thermal | Constraint Automation
N>>NIL_61_4 | 0.83333 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) on trip of Collector to Marulan (4) line, Feedback | NIL | Thermal | NSW
NC_N_HUMENSW | 0.83333 | 0 | Non Conformance Constraint for Hume Hydro Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_OAKEY2SF | 0.83333 | 0 | Non Conformance Constraint for OAKEY 2 SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_Q_SWAN_E | 0.83333 | 1.1667 | Non Conformance Constraint for Swanbank E Power Station | Other | Non-Conformance | Non-Conformance
NC_S_TIBESS_ADG1 | 0.83333 | 0 | Non Conformance Constraint for TIBESS_ADG1 | Other | Non-Conformance | Non-Conformance
NC_V_YWPS2 | 0.83333 | 0.5 | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Other | Non-Conformance | Non-Conformance
N_MBTE1_A | 0.83333 | 0.66667 | Out= one Directlink cable, NSW to Qld limit | Outage | Unit Zero | NSW
N_NYNGANSF_ZERO | 0.83333 | 0 | Nyngan Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q-MEWF_MVAR | 0.83333 | 56.25 | Constraint to violate if Reactive power output of Mt Emerald Wind farm Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q_STR_32282_CLRSF | 0.83333 | 3.75 | Limit 50% to Clare SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_HASF | 0.83333 | 3.8333 | Limit 50% to Haughton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_KEP | 0.83333 | 2.5 | Limit 50% to kennedy Energy Park if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_WHTSF | 0.83333 | 3.6667 | Limit 50% to Whitsunday SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_KIDSF_2 | 0.83333 | 0 | Limit Kidston SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
S-MBPS2-PV_0 | 0.83333 | 0 | Discretionary upper limit for SA WATER Murray Bridge (Hahndorf ) - Onkaparinga Pipeline Pumping Station 2 PV of 0 MW | Outage | Unit Zero | SA
S>>X_CR+RBTX+TPRS_04 | 0.83333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
T>T_HAPM_IMP_4N | 0.83333 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V::N_MLMO_xxx | 0.83333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>>EPTT_DDSM_DDSM | 0.83333 | 0 | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to South) for loss of the parallel line, 15 min rating, feedback. Swamp if VBB/SIPS available | Outage | Thermal | Vic
V_STOCKYH_ZERO | 0.83333 | 0.66667 | Stockyard Hill wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
#GANGARR1_E | 0.75 | 99 | QWSS1G.ENERGY * 1 <= 95 (Wt = 360) | Other | DEFAULT | Quick
N>991_9R6_9R5 | 0.75 | 0 | Out= Wagga North to Murrumburrah 132kV line (991), avoid O/L Wagga North to Wagga132 (9R6) on trip of Wagga North to Wagga330 (9R5) line, Feedback | Outage | Thermal | NSW
N>>NIL_7_3 | 0.75 | 1.3333 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, [Note: unswamped when both 1 & 2 LSC disabled] | NIL | Thermal | NSW
N>>NIL_964_88_S | 0.75 | 0 | Out= NIL, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL | Thermal | NSW
N>>NIL_DPTX_LV | 0.75 | 0.33333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | Thermal | NSW
NC_N_WYASF1 | 0.75 | 0 | Non Conformance Constraint for WYALONG SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_S_CNUNDAWF | 0.75 | 0 | Non Conformance Constraint for Canunda Wind Farm | Other | Non-Conformance | Non-Conformance
NRM_NSW1_QLD1 | 0.75 | 2.4167 | Negative Residue Management constraint for NSW to QLD flow. | NIL | Negative Residue | Negative Residue
N_NEWENSF1+2_201-INV | 0.75 | 0 | New England Solar inverter limit of 201. Constraint to violate if New England Solar inverter availability greater than 201. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q-DAYSF_MVAR | 0.75 | 31.5 | Constraint to violate if Reactive power output of Daydream Solar farm is greater than +/- 10Mvar at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-HAMSF_MVAR | 0.75 | 44.25 | Constraint to violate if Reactive power output of Hamilton Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-HAUSF_MVAR | 0.75 | 56.5833 | Constraint to violate if Reactive power output of Haughton Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-HAYSF_MVAR | 0.75 | 44.5 | Constraint to violate if Reactive power output of Hayman Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-SMSF_MVAR | 0.75 | 56.6667 | Constraint to violate if Reactive power output of Sun Metals Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q_STR_32282_MEWF | 0.75 | 3.6667 | Limit 50% to Mt Emerald WF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_CLRSF_10 | 0.75 | 0 | Limit Clare Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
S>>BWMP_RBTU_RBPA | 0.75 | 1.6667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Robertstown-Para 275kV line on trip of Robertstown -Tungkillo 275kV line, Feedback | Outage | Thermal | SA
T>T_SH_TX | 0.75 | 0 | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Thermal | Tas
T_ROCOF_2 | 0.75 | 0 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of TAS largest unit with Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | ROC Frequency | Tas
V::N_KMRC_O2 | 0.75 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
N>PKTX_TX_NIL | 0.66667 | 0 | Out= One Parkes 132/66kV transformer , avoid O/L the remaining Parkes 66/132kV transformer on trip of Nil, Feedback | Outage | Thermal | NSW
NC_Q_YABULU2 | 0.66667 | 0.41667 | Non Conformance Constraint for Yabulu 2 Power Station | Other | Non-Conformance | Non-Conformance
N^^V_LTUT_1 | 0.66667 | 0 | Out = Lower to Upper Tumut (64) 330kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_MOREESF1_20INV | 0.66667 | 0 | Moree Solar Farm inverter limit of 20. Constraint to violate if Moree Solar Farm inverter availability greater than 20. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_SUNRSF1_0INV | 0.66667 | 0 | Sunraysia Solar Farm inverter limit of zero. Constraint to violate if Sunraysia Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_WR_30_WT-INV | 0.66667 | 0.33333 | White Rock Wind & Solar Farm inverter limit of 30. Constraint to violate if White Rock Wind & Solar Farm inverter availability greater than 30. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q-RGBSF_MVAR | 0.66667 | 41.25 | Constraint to violate if Reactive power output of Rugby Run Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q_STR_32282_DAYSF | 0.66667 | 3.6667 | Limit 50% to Daydream SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_HAYSF | 0.66667 | 3.5833 | Limit 50% to Hayman SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_KIDSF | 0.66667 | 3.5833 | Limit 50% to Kidston SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
S:V_460 | 0.66667 | 0 | Maintain maximum transfer limit of 460 MW on Heywood IC from SA to VIC to avoid oscillatory instability | Outage | Oscillatory Stability | SA
S>>BWMP_HUWT_RHBG-T | 0.66667 | 1.3333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill-Brinkworth 132kV T line on trip of Hummocks-Waterloo 132kV line, Feedback | Outage | Thermal | SA
T>T_NIL_BL_3C | 0.66667 | 2.1667 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
T^^V_GTSH_1 | 0.66667 | 0 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Voltage Stability | Tas
V::N_HYTR_xxx | 0.66667 | 1.25 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V^^N_JNWG_1 | 0.66667 | 0 | Out = Jindera to Wagga (62) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_KIAMAL_SC_DYN | 0.66667 | 0 | Out = Kiamal Syncon, Limit Kiamal solar farm to 135 MW when Murra Warra 2 WF syncon I/S. Limit Kiamal solar farm to 100 MW when Murra Warra 2 WF syncon O/S. DS only. Swamp out if Kiamal Syncon is in service | NIL | Discretionary | Vic
V_ELAINEWF_ZERO | 0.66667 | 13.4167 | Elaine Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
#BRAEMAR2_E | 0.58333 | 55.6667 | QBRA2.ENERGY * 1 <= 188 (Wt = 360) | Other | DEFAULT | Quick
#BRYB2WF2_E | 0.58333 | 484.5833 | VBBT2B.ENERGY * 1 <= 75.6 (Wt = 360) | Other | DEFAULT | Quick
#SITHE01_E | 0.58333 | 0 | NSYW1.ENERGY * 1 <= 36 (Wt = 29) | Other | DEFAULT | Quick
N>>99D_99K_63 | 0.58333 | 0 | Out= Darlington Point to Yanco (99D) 132kV line, avoid O/L Darlington Point to Griffith (99K) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, [Note:Wagga to Darlington Point network solid, X5 trip scheme disarmed, option C OM521] | Outage | Thermal | NSW
N>>99J_99D_63 | 0.58333 | 0 | Out= Griffith to Yanco (99J) 132kV line, avoid O/L Darlington Point to Yanco (99D) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, (Note:X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521) | Outage | Thermal | NSW
N>>9R3_99D_63 | 0.58333 | 0 | Out= Finley to Deniliquin (9R3), avoid O/L Darlington Point to Yanco (99D) 132kV line on trip of Darling Point to Wagga (63) 330kV line, X5 trip scheme disarmed, Feedback | Outage | Thermal | NSW
N>NIL_947_94T | 0.58333 | 5.0833 | Out= Nil, avoid O/L Wellington to Orange North (947) on trip of Molong to Orange North (94T), Feedback | NIL | Thermal | NSW
N_GOONSF1_0INV | 0.58333 | 1.5 | Goonumbla Solar Farm inverter limit of zero. Constraint to violate if Goonumbla Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_GOONSF_11_INV | 0.58333 | 0.66667 | Goonumbla Solar Farm inverter limit of 11. Constraint to violate if Goonumbla Solar Farm inverter availability greater than 11. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q>N-MUTE_757 | 0.58333 | 9.1667 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
Q_STR_32282_COLSF | 0.58333 | 3 | Limit 50% to Collinsville SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_HAMSF | 0.58333 | 3.5833 | Limit 50% to Hamilton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_RGBSF | 0.58333 | 3.75 | Limit 50% to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_RRSF | 0.58333 | 3.4167 | Limit 50% to Ross River SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_SMSF | 0.58333 | 2.9167 | Limit 50% to Sun Metals SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_WHTSF_10 | 0.58333 | 0 | Limit Whitsunday Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_WDGPH1_ZERO | 0.58333 | 0 | Western Downs Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S-MWPS3-PV_0 | 0.58333 | 2 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 3 PV generation of 0 MW | Outage | Unit Zero | SA
S-WP_0 | 0.58333 | 0.083333 | Discretionary upper limit for Wattle Point windfarm generation of 0 MW | Outage | Unit Zero | SA
S:VS_700_HY_TEST | 0.58333 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
SVML_030 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 30 MW | Outage | Discretionary | SA
T>T_PMSH_IMP_4E | 0.58333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V::N_KMRC_O1 | 0.58333 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V^^N_BADP_1 | 0.58333 | 4.8333 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
#QBYNBL1_E | 0.5 | 9 | NQBB2Q.ENERGY * 1 <= 10 (Wt = 360) | Other | DEFAULT | Quick
N::Q_MIMR_TWO_KC | 0.5 | 0 | Out = Two parallel feeders between R4 Millmerran to H14 Middle Ridge (9914+9915 or 9908+9907), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
N>>V_NIL_65_66 | 0.5 | 0.16667 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; (Note: constraint is swamped out if TL 64 is O/S) | NIL | Thermal | NSW
N>BWLD33_BWLD34 | 0.5 | 0 | Constraint Automation, O/L 34:LN34:Z:330@BAYSWATR@NSW for CTG LNPI on trip of BAYSWATR-LIDDELL 33 330KV LINE. Generated by RTCA[EMS] | Outage | Thermal | Constraint Automation - RT
NC_N_BW02 | 0.5 | 0.25 | Non Conformance Constraint for Bayswater 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_LD02 | 0.5 | 0.41667 | Non Conformance Constraint for Liddell LD02 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_TALWA1 | 0.5 | 2 | Non Conformance Constraint for Tallawarra Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_MOUSF1 | 0.5 | 0 | Non Conformance Constraint for MOURA SOLAR FARM | Other | Non-Conformance | Non-Conformance
Q::N_30+38_AR_2L-G | 0.5 | 0 | Out = Liverpool to Sydney West (30) + Regentville to Sydney West (38) 330 kV lines, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
Q>NIL_DRLCLB_DRLCLB | 0.5 | 0 | Out= Nil, avoid OL on 7490 or 7491 (T280 Drillham to T194 Columboola) 132kV feeder on trip of 7491 or 7490 (T280 Drillham to T194 Columboola) 132kV feeder, Feedback | NIL | Thermal | Qld
Q_STR_7C0K_KEP_2 | 0.5 | 0 | Limit Kennedy Energy park to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
S:V_PA_SVC_420 | 0.5 | 93.5833 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
S>>X_RBPA+RBTX2_06 | 0.5 | 50.5 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
T>T_PMSH_IMP_4D | 0.5 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
T^T_LIPM_1 | 0.5 | 6.3333 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line | Outage | Voltage Stability | Tas
T_FISH | 0.5 | 0 | Out=Sheffield-Fisher 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
T_T_FASH2_2 | 0.5 | 0 | Out = Farrell 220 kV bus split, limit John Butters, Bastyan and Mackintosh to greater than 90% West Coast load | Outage | Other | Tas
V::N_KGRC_O2 | 0.5 | 0 | Out = Kerang to Red Cliffs 220kV line (or any section in between), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
V>>MLSY_KTDPT_SYML | 0.5 | 0 | Out = Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid O/L Keilor to Deer Park 220 kV line on trip of remaining Moorabool to Sydenham 500 kV line, feedback | Outage | Thermal | Vic
V>>S_MWP3RB_NWRB1 | 0.5 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L North West Bend-Roberstown #1 132kV line on Nil trip, Feedback | Outage | Thermal | SA
V>S_460_DYN | 0.5 | 11.75 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | Vic
VSML_010 | 0.5 | 0 | Vic to SA on ML upper transfer limit of 10 MW | Outage | Discretionary | Vic
VSML_025 | 0.5 | 0 | Vic to SA on ML upper transfer limit of 25 MW | Outage | Discretionary | Vic
#BBATTERY_E | 0.41667 | 0 | QBCB1B.ENERGY * 1 <= 50 (Wt = 360) | Other | DEFAULT | Quick
#MRTLSWF1_E | 0.41667 | 861.5833 | VTG21M.ENERGY * 1 <= 102 (Wt = 360) | Other | DEFAULT | Quick
N>9GM_999_NIL | 0.41667 | 0 | Out= Bango999 WF to Yass 132kV line(9GM), avoid O/L Bango999 to Cowra (999) on trip of Nil, Feedback | Outage | Thermal | NSW
NC_N_BW03 | 0.41667 | 0.33333 | Non Conformance Constraint for Bayswater 3 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_BW04 | 0.41667 | 0.25 | Non Conformance Constraint for Bayswater 4 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_ER01 | 0.41667 | 0.83333 | Non Conformance Constraint for Eraring ER01 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_MP2 | 0.41667 | 1.0833 | Non Conformance Constraint for Mt Piper 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE5 | 0.41667 | 0.41667 | Non Conformance Constraint for Gladstone 5 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_TARONG#1 | 0.41667 | 0 | Non Conformance Constraint for Tarong 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_WDGPH1 | 0.41667 | 0 | Non Conformance Constraint for WESTERN DOWNS GPH | Other | Non-Conformance | Non-Conformance
NC_Q_YABULU | 0.41667 | 21.25 | Non Conformance Constraint for Yabulu Power Station | Other | Non-Conformance | Non-Conformance
NC_S_NBHWF1 | 0.41667 | 0 | Non Conformance Constraint for North Brown Hill Windfarm | Other | Non-Conformance | Non-Conformance
NC_V_YWPS4 | 0.41667 | 0.66667 | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Other | Non-Conformance | Non-Conformance
N_AVLSF1_0INV | 0.41667 | 0 | Avonlie Solar Farm inverter limit of zero. Constraint to violate if Avonlie Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_AVLSF1_47INV | 0.41667 | 0 | Avonlie Solar Farm inverter limit of 47. Constraint to violate if Avonlie Solar Farm inverter availability greater than 47. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_BDKV | 0.41667 | 0 | Out= Bendeela - Kangaroo Valley (19) line | Outage | Unit Zero | NSW
N_METZSF_0INV | 0.41667 | 0.33333 | Metz Solar Farm inverter limit of zero. Constraint to violate if Metz Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_METZSF_20INV | 0.41667 | 0 | Metz Solar Farm inverter limit of 20. Constraint to violate if Metz Solar Farm inverter availability greater than 20. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_MOREESF1_35INV | 0.41667 | 0 | Moree Solar Farm inverter limit of 35. Constraint to violate if Moree Solar Farm inverter availability greater than 35. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_WALGR_BAT_G_ZERO | 0.41667 | 0 | Wallgrove Battery (Generation Component) upper limit of 0 MW | Outage | Unit Zero | NSW
Q^^N_DM+LS_SVC_SRAR | 0.41667 | 0 | Out = Dumaresq SVC + Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
S-MWPS2-PV_0 | 0.41667 | 9.3333 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 2 PV generation of 0 MW | Outage | Unit Zero | SA
V::S_RBPA_SETB | 0.41667 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Transient Stability | SA
V::S_TBEBUS_MAXG | 0.41667 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage | Transient Stability | SA
V::V_1900 | 0.41667 | 0.25 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Oscillatory Stability | Vic
V>>CWHO_X3_BEKG | 0.41667 | 0 | Out = Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage | Thermal | Vic
V>>DBT_DDTX3_DDTX | 0.41667 | 0 | Out = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage Schemes), avoid O/L Dederang H3 330/220kV transformer for loss of Dederang H1 or H2 330/220kV transformer, feedback | Outage | Thermal | Vic
V>>KMCB_BABE_KMRC | 0.41667 | 0 | Out= Kiamal 220kV CB (one or more MR2B or 7422A or 7422B), avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | Outage | Thermal | Vic
V^^S_RBPA_SETB | 0.41667 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Voltage Stability | SA
V_COHUNASF_0INV | 0.41667 | 1.0833 | Cohuna Solar Farm inverter limit of zero. Constraint to violate if Cohuna Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | Vic
V_MOORBWF_ZERO | 0.41667 | 0 | Moorabool Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V_MURRAWRWF_FLT_135 | 0.41667 | 7.25 | Limit Murra Warra Wind Farm 1+2 upper limit to 135 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N_FINLEYSF_49_INV | 0.41667 | 1.5 | Finley Solar Farm inverter limit of 49. Constraint to violate if Finley Solar Farm inverter availability greater than 49. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_METZSF_43 | 0.41667 | 0 | Metz Solar farm upper limit of 43 MW | Outage | System Strength | NSW
N_MOREESF1_40INV | 0.41667 | 0.33333 | Moree Solar Farm inverter limit of 40. Constraint to violate if Moree Solar Farm inverter availability greater than 40. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_NEWENSF1+2_110-INV | 0.41667 | 0 | New England Solar inverter limit of 110. Constraint to violate if New England Solar inverter availability greater than 110. Swamp out otherwise. DS only | Outage | System Strength | NSW
S_PPT+SNPT_270 | 0.41667 | 3.9167 | SA Pelican Point + Snapper Point generation <= 270 MW | Outage | Discretionary | SA
#KABANWF1_E | 0.33333 | 79.8333 | QTMW1K.ENERGY * 1 <= 152 (Wt = 360) | Other | DEFAULT | Quick
#LIMOSF11_E | 0.33333 | 0.75 | NBSF1L.ENERGY * 1 <= 220 (Wt = 360) | Other | DEFAULT | Quick
N>947+94P_94T | 0.33333 | 0 | Out= Wellington to Orange North (947) 132kV line + Manildra to Molong (94P) 132kV, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
N>96L_967_89 | 0.33333 | 0 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), TG formulation in PD/ST(Noted: Swamped out when 967 O/S) | Outage | Thermal | NSW
N>>99K_99D_63 | 0.33333 | 0 | Out= Darlington Point to Griffith (99K) 132kV line, avoid O/L Darlington Pt to Yanco (99D) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,(Note: assumed X5 trip scheme disarmed & Wagga to Darlington Point network solid, option C on OM521) | Outage | Thermal | NSW
N>>NIL_5_3J_N | 0.33333 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) using 15 mins rating on trip of Yass to Gullen Range (3J) line, Feedback | NIL | Thermal | NSW
N>>NIL_966/1_87_S | 0.33333 | 0 | Out=Nil, avoid O/L Metz Tee to Armidale (966/1) kV line on trip of Coffs Harbour to Armidale (87) 330kV line, Feedback | NIL | Thermal | NSW
NC_N_MP1 | 0.33333 | 0.16667 | Non Conformance Constraint for Mt Piper 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_SEBSF1 | 0.33333 | 0 | Non Conformance Constraint for SEBASTOPOL SF | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE3 | 0.33333 | 0.33333 | Non Conformance Constraint for Gladstone 3 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_STAN-2 | 0.33333 | 0.083333 | Non Conformance Constraint for Stanwell STAN-2 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_ADP_ADG1 | 0.33333 | 0 | Non Conformance Constraint for ADP_ADG1 | Other | Non-Conformance | Non-Conformance
NQTE_090 | 0.33333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of 90 MW | Outage | Discretionary | NSW
NQ_700_DYN_TEST | 0.33333 | 15.5833 | NSW to QLD on QNI upper transfer limit of 700 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | NSW
N_GNNDHSF1_0INV | 0.33333 | 0 | Gunnedah Solar Farm inverter limit of zero. Constraint to violate if Gunnedah Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_HILLSTSF1_0INV | 0.33333 | 0.16667 | Hillston Solar Farm inverter limit of zero. Constraint to violate if Hillston Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_WR_0WT-0INV | 0.33333 | 0.083333 | White Rock Wind & Solar Farm inverter limit of zero. Constraint to violate if White Rock Wind & Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q-KBWF_MVAR | 0.33333 | 0 | Constraint to violate if Reactive power output of Kaban Wind farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q>GBMO_BLYTA_GBMO | 0.33333 | 0 | Out= 8824 or 8825 (S3 Greenbank to H4 Molendinar) 275kV line, avoid OL on 704 (T108 Beenleigh to Yatala) 132kV line on trip of remaining feeder 8824 or 8825, feedback | Outage | Thermal | Qld
Q>NIL_BI_xxx | 0.33333 | 0 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines | NIL | Thermal | Qld
Q_STR_7C2K_KEP_7 | 0.33333 | 0 | Limit to Kennedy Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STSTN_864 | 0.33333 | 0 | Out= 864 Stanwell Power Station 275kV line | Outage | Unit Zero | Qld
S-BUPV1_0 | 0.33333 | 0.5 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | Unit Zero | SA
S>>WEWT_TWPA_TPRS | 0.33333 | 0 | Out= Waterloo East-Waterloo 132kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S>>X_CR+RBTX+TPRS_12 | 0.33333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
S>LFPP_PGPA_PGPE | 0.33333 | 0 | Out= Lefevre-Pelican Point 275kV line, avoid O/L Parafield Gardens West-Paralowie 66kV line on trip of Parafield Gardens West-Para 275kV line, Feedback | Outage | Thermal | SA
SV_420_DYN | 0.33333 | 168.25 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 50 MW | Outage | Discretionary | SA
S_BIPS_ZERO | 0.33333 | 0 | Barker Inlet upper limit of 0 MW | Outage | Unit Zero | SA
T_FASH_MAXG_SB3 | 0.33333 | 0 | Upper limit on West Coast Gens with both Farrell to Sheffield 220 kV lines declared credible, West Coast 220/110 kV parallel closed. Constraint active if MORE THAN TWO West Coast Hydro machines online. CP-04, Scenario B | Outage | Other | Tas
V::S_SEVC1_SETB | 0.33333 | 1.25 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
V>>NIL_BANBGR_ARCW | 0.33333 | 0 | Out = Nil, avoid O/L Ballarat North to Buangor 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service, Feedback | NIL | Thermal | Vic
V>>N_051_66_65_R | 0.33333 | 1.5 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line,(Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | Vic
VSML_195 | 0.33333 | 1.0833 | Vic to SA on ML upper transfer limit of 195 MW | Outage | Discretionary | Vic
V_KIAMAL_0INV | 0.33333 | 0 | Kiamal Solar Farm inverter limit of zero. Constraint to violate if Kiamal Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | Vic
#BBATRYL1_E | 0.25 | 0 | QBCB2B.ENERGY * 1 <= 50 (Wt = 360) | Other | DEFAULT | Quick
#DARLSF1_E | 0.25 | 0.16667 | NDNS1D.ENERGY * 1 <= 275 (Wt = 360) | Other | DEFAULT | Quick
#QBYNBG1_E | 0.25 | 9.75 | NQBB1Q.ENERGY * 1 <= 10 (Wt = 360) | Other | DEFAULT | Quick
#SEBSF1_E | 0.25 | 3.3333 | NWGJ2S.ENERGY * 1 <= 90 (Wt = 360) | Other | DEFAULT | Quick
#T-V-MNSP1_RAMP_I_F | 0.25 | 0 | T-V-MNSP1 >= MIN(-250, InitialFlow + 100) (Wt=35) | Other | Ramping | Quick
#WALGRVL1_E | 0.25 | 0 | NSWB2W.ENERGY * 1 <= 47 (Wt = 360) | Other | DEFAULT | Quick
#WARWSF1_E | 0.25 | 142.9167 | QMRY3W.ENERGY * 1 <= 32 (Wt = 360) | Other | DEFAULT | Quick
N::Q_TW_SVC_TNT | 0.25 | 0 | Out = Tamworth SVC, NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage | Transient Stability | NSW
N::V_DDSM_UTMS | 0.25 | 0.41667 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit for trip of Upper Tumut - Murray (65) line | Outage | Transient Stability | NSW
N>947+94P_94K_1 | 0.25 | 0 | Out= Wellington to Orange North (947) 132kV line + Manildra to Molong (94P) 132kV, avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | Outage | Thermal | NSW
N>>24_93_90 | 0.25 | 0 | Out = Eraring to Vales Point (24), avoid O/L Eraring to Newcastle (93) on trip of Eraring to Newcastle (90) line, Feedback | Outage | Thermal | NSW
N>>NIL_4_61_N | 0.25 | 0 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Crookwell to Bannaby (61) line, Feedback | NIL | Thermal | NSW
N>>NIL_8E_8C_S | 0.25 | 0 | Out = Nil, avoid O/L Sapphire to Armidale (8E) using 15 min rating on trip of Dumaresq to Armidale (8C) line, Feedback | NIL | Thermal | NSW
N>NIL_9R5_9R6_N | 0.25 | 0 | Out= NIL, avoid O/L Wagga330 to Wagga North (9R5) 132kV line on trip of Wagga132 to Wagga North (9R6) 132kV line, Feedback | NIL | Thermal | NSW
NC_N_ER03 | 0.25 | 0 | Non Conformance Constraint for Eraring ER03 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_CALL_B_1 | 0.25 | 0.083333 | Non Conformance Constraint for Callide B_1 | Other | Non-Conformance | Non-Conformance
NC_S_SNAPPER1 | 0.25 | 0.58333 | Non Conformance Constraint for SNAPPER POINT POWER | Other | Non-Conformance | Non-Conformance
NC_V_NPS | 0.25 | 17.4167 | Non Conformance Constraint for Newport Power Station | Other | Non-Conformance | Non-Conformance
N_BROKENH1_ZERO | 0.25 | 91.8333 | Broken Hill Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_FINLEYSF_80INV | 0.25 | 0 | Finley Solar Farm inverter limit of 80. Constraint to violate if Finley Solar Farm inverter availability greater than 80. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_GNNDHSF1_82INV | 0.25 | 0 | Gunnedah Solar Farm inverter limit of 82. Constraint to violate if Gunnedah Solar Farm inverter availability greater than 82. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_NEWENSF1+2_260-INV | 0.25 | 0 | New England Solar inverter limit of 260. Constraint to violate if New England Solar inverter availability greater than 260. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_SAPHWF1_28WT | 0.25 | 0 | Constraint to violate if Sapphire WF turbines On greater than 28. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
Q>>BCCP_CLWU_RGLC | 0.25 | 0 | Out= Bouldercombe to Calliope River (812), avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
Q_HAMISF1_ZERO | 0.25 | 6.6667 | Hamilton solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_KEP-HYB_21MW | 0.25 | 0 | Kennedy Energy Park upper limit of 21MW | Outage | Discretionary | Qld
Q_WANDBL1_ZERO | 0.25 | 0 | Wandoan South BESS (load component) upper limit of 0 MW | Outage | Unit Zero | Qld
S>>MKRB_BWMP_WTTP | 0.25 | 1.4167 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_CGTB_TUTB_1 | 0.25 | 0 | Out= Nil, avoid O/L Tungkillo - Tailem Bend 275kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | NIL | Thermal | SA
S>>NIL_TBCG_TBTU_1 | 0.25 | 0.58333 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | Thermal | SA
S>>RBTX_BWPA_WTTP | 0.25 | 1.3333 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>V_NIL_NIL_RBNW1 | 0.25 | 0.083333 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL | Thermal | SA
S>LFPP_PGPA_PGPS | 0.25 | 0 | Out= Lefevre-Pelican Point 275kV line, avoid O/L Parafield Gardens West-Parafield Gardens 66kV line on trip of Parafield Gardens West-Para 275kV line, Feedback | Outage | Thermal | SA
S>NIL_NIL_NWMH2 | 0.25 | 0.16667 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
S^DVPL_CRK_VCS | 0.25 | 0 | Out= Any line between Davenport, Cultana and Port Lincoln, Upper limit for Cathedral Rocks WF based on Mt Millar Voltage Control System (VCS) availability, (Note: CRK <=45 MW when VCS OFF; CRK<= 53 MW when VCS ON) | Outage | Voltage Stability | SA
T^T_NIL_BL_6 | 0.25 | 0 | Outage = Nil, avoid voltage instability or violations for loss of a Liapootah-Waddamana-Palmerston 220 kV line | NIL | Voltage Stability | Tas
T^V_HA_GT_220_1 | 0.25 | 0 | Out= one George Town to Hadspen 220kV line, limit post-contingency loading on Palmerston to Sheffield 220kV line (flow to north) to avoid voltage collapse on trip of the remaining Hadspen to George Town 220kV line. | Outage | Voltage Stability | Tas
T_BLINK_VT_NGZ | 0.25 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow < 0, Basslink Target MW <= 0, swamped if Basslink Metered Flow > -0.1 DS only. | NIL | Other | Tas
T_FAJB | 0.25 | 0 | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
T_PMPO_220 | 0.25 | 0 | Out=A single Palmerston-Poatina 220KV line. One line out of service only | Outage | Unit Zero | Tas
V::N_ROSM_O2 | 0.25 | 1.5833 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
V::N_SMTT_O2 | 0.25 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
V::S_NIL_MG_PS_N-2_1 | 0.25 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA with loss of Pelican Point + Snapper Point PS declared as credible.( Note: South East Capacitor Available) | Outage | Transient Stability | SA
V>>ARWB_X5DP_KGBE | 0.25 | 0 | Out= Any 220kV line section between Ararat and Ballarat, avoid O/L Balranald to Darlington Point (X5) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
V>>NIL_MLGT_MLGT_B | 0.25 | 0 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 220 kV mode, Feedback | NIL | Thermal | Vic
VT_350 | 0.25 | 0 | Vic to Tas on Basslink upper limit of 350 MW | Outage | Discretionary | Vic
V_GANNSF_12INV | 0.25 | 0 | Gannawarra Solar Farm inverter limit of 12. Constraint to violate if Gannawarra Solar Farm inverter availability greater than 12. Swamp out otherwise. DS only | Outage | System Strength | Vic
V_GANWR_BAT_L_FLT_0 | 0.25 | 0 | Limit Gannawarra Battery (Load Component) upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_GANWR_BAT_L_ISL_0 | 0.25 | 3.4167 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
CA_BRIS_542A0DC2_1 | 0.16667 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage | Thermal | Constraint Automation
CA_BRIS_542A114F_1 | 0.16667 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage | Thermal | Constraint Automation
CA_SYDS_52F01146_1 | 0.16667 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
N::Q_8C8J_LDTW_N-2 | 0.16667 | 0 | Out = Nil, NSW to Qld Transient Stability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | NSW
N>947_94K1 | 0.16667 | 0 | Out= Wellington to Orange North (947) 132kV line, avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | Outage | Thermal | NSW
N>>LDTM_964_84_OPEN | 0.16667 | 0 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Liddell (84) line, Feedback | Outage | Thermal | NSW
N>>NIL_5_3P_N | 0.16667 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) using 15 mins rating on trip of Rye Park to Gullen Range (3P) line, Feedback | NIL | Thermal | NSW
N>>V_051_65_66_R | 0.16667 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Upper Tumut to Murray (65) on trip of Lower Tumut to Murray (66) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | NSW
N>>V_NIL_66_65 | 0.16667 | 0.33333 | Out = Nil, avoid Lower Tumut to Murray(66) using 15 mins rating O/L on Upper Tumut to Murray(65) trip; (Note: Swamped when TL 64 is O/S) | NIL | Thermal | NSW
N>NIL-BHTX_BHTX_NIL | 0.16667 | 0 | Out= NIL with one Broken Hill 22/220kV TX switched O/S (Note: only one TX can be I/S for system normal), avoid O/L remaining Broken Hill 22/220kV TX on trip of Nil, (Note: Swamped when both TX1&2 are I/S, otherwise unswamped; Assumed 22kV CB 2112 I/S) | NIL | Thermal | NSW
N>NIL_973 | 0.16667 | 0 | Out= Nil, avoid O/L Bango973 to Cowra (973) on trip of Nil, Feedback | NIL | Thermal | NSW
NC_N_BANGOWF1 | 0.16667 | 0 | Non Conformance Constraint for BANGO WIND FARM 973 | Other | Non-Conformance | Non-Conformance
NC_N_SITHE01 | 0.16667 | 17.6667 | Non Conformance Constraint for Smithfield Energy Facility | Other | Non-Conformance | Non-Conformance
NC_Q_CLARESF1 | 0.16667 | 0 | Non Conformance Constraint for CLARE SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_Q_PUMP2 | 0.16667 | 0 | Non Conformance Constraint for Wivenhoe No.2 Pump | Other | Non-Conformance | Non-Conformance
NC_Q_SMCSF1 | 0.16667 | 0 | Non Conformance Constraint for Sun Metals solar farm | Other | Non-Conformance | Non-Conformance
NC_S_BARKIPS1 | 0.16667 | 1.5833 | Non Conformance Constraint for BARKER INLET PS | Other | Non-Conformance | Non-Conformance
NC_S_BOLIVPS1 | 0.16667 | 0.25 | Non Conformance Constraint for BOLIVARPOWERSTATION1 | Other | Non-Conformance | Non-Conformance
NC_S_LGAPWF1 | 0.16667 | 0 | Non Conformance Constraint for Lincoln Gap Wind Farm | Other | Non-Conformance | Non-Conformance
NC_S_LGAPWF2 | 0.16667 | 0 | Non Conformance Constraint for LINCOLN GAP WF 2 | Other | Non-Conformance | Non-Conformance
NC_V_BRYB2WF2 | 0.16667 | 0 | Non Conformance Constraint for BERRYBANK 2 WF | Other | Non-Conformance | Non-Conformance
NC_V_JLA04 | 0.16667 | 14.8333 | Non Conformance Constraint for Jeeralang A - 04 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_KIAMSF1 | 0.16667 | 0 | Non Conformance Constraint for KIAMAL SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_V_VBB_ADG1 | 0.16667 | 0 | Non Conformance Constraint for VBB_ADG1 | Other | Non-Conformance | Non-Conformance
NC_V_YWPS3 | 0.16667 | 0.16667 | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Other | Non-Conformance | Non-Conformance
NQTE_-090 | 0.16667 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -90 MW | Outage | Discretionary | NSW
N^^V_MSUT_1 | 0.16667 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_GOONSF_9_INV | 0.16667 | 0 | Goonumbla Solar Farm inverter limit of 9. Constraint to violate if Goonumbla Solar Farm inverter availability greater than 9. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_METZSF_25INV | 0.16667 | 0 | Metz Solar Farm inverter limit of 25. Constraint to violate if Metz Solar Farm inverter availability greater than 25. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_METZSF_34INV | 0.16667 | 0 | Metz Solar Farm inverter limit of 34. Constraint to violate if Metz Solar Farm inverter availability greater than 34. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_NEWENSF1+2_279 | 0.16667 | 0 | New England Solar farms 1 + 2 upper limit of 279 MW | Outage | System Strength | NSW
N_WAGGNSF1_0INV | 0.16667 | 0 | Wagga North Solar Farm inverter limit of zero. Constraint to violate if Wagga North Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_WALGR_BAT_L_ZERO | 0.16667 | 0.25 | Wallgrove Battery (Load Component) upper limit of 0 MW | Outage | Unit Zero | NSW
Q>>BCCP_BCRG_CLWU | 0.16667 | 0 | Out= Bouldercombe to Calliope River (812), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
Q>STBS_STBS_BCBS | 0.16667 | 0 | Out= Stanwell to Broadsound (856 or 8831), avoid O/L Bouldercombe to Broadsound (820) on trip of remaining Stanwell to Broadsound (856 or 8831), Feedback | Outage | Thermal | Qld
QNTE_090 | 0.16667 | 0 | Qld to NSW on Terranora Interconnector upper transfer limit of 90 MW | Outage | Discretionary | Qld
QNTE_ZERO | 0.16667 | 0 | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW | Outage | Interconnector Zero | Qld
Q_EMERASF1_ZERO | 0.16667 | 10.75 | Emerald Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_RGBYRSF1_ZERO | 0.16667 | 0.66667 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_WARWSF1_ZERO | 0.16667 | 7.6667 | Warwick Solar Farm 1 upper limit of 0 MW | Outage | Unit Zero | Qld
Q_WHITSF1_ZERO | 0.16667 | 5.8333 | Whitsunday solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S-MWPS1-PV_0 | 0.16667 | 9.0833 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 1 PV generation of 0 MW | Outage | Unit Zero | SA
S-MWPS4-PV_0 | 0.16667 | 7.0833 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 4 PV generation of 0 MW | Outage | Unit Zero | SA
S:VS_XPAVC_460 | 0.16667 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood and Murraylink combined upper transfer limit of 460 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
S>>MKRB_BRTW_WTTP | 0.16667 | 1.5833 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
S>>RBTU_RBPA_BWMP | 0.16667 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Blyth West-Munno Para 275kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
S>>X_RBTU+RBTX_01 | 0.16667 | 0 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown-Tungkillo 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>X_RBTU+RBTX_12 | 0.16667 | 0 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Blyth West-Munno Para275kV line on trip of remaining Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>WERB_WTTP_CLNBR | 0.16667 | 0 | Out= Robertstown -MWP4 -Waterloo East O/S(offloads MWPF SF), avoid O/L Claire North-Brinkworth 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | Thermal | SA
S>X-WTTP+CB_1 | 0.16667 | 0 | Out= Waterloo-Templers 132kV line + associated line CBs O/S, avoid O/L Snowtown-Bungama T 132kV line on trip of Mintaro-Waterloo 132kV line(this offloads Hummocks-Waterloo 132kV line), Feedback | Outage | Thermal | SA
T>T_TUNN3_110_2 | 0.16667 | 0 | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
V::S_SETB_MG_PPGT1 | 0.16667 | 0 | Out= one South East -Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT1 + DPV trip) in SA (SE Cap Available). (NOTE: with one Black Range series capacitors I/S. Co-optimised eq PPGT1 LHS | Outage | Transient Stability | SA
V>>051_68_67_R | 0.16667 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, (Note: Assumed Wagga-Yass 132kV network Split, X5, 63 & 9R4 opened, & with 2 Yass Transformer I/S; Swamped if SIPS ENABLED) | Outage | Thermal | Vic
V>>KMRC_DPTX_KGBE | 0.16667 | 0 | Out= Kiamal to Red Cliffs 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
V>>MLSY_KTTX_SYML_5R | 0.16667 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage | Thermal | Vic
V>>N-DPWG_X5_A | 0.16667 | 0 | Out = to Wagga (63) and Darlington Point to Balranald (X5), avoid Murray to Upper Tumut (65) O/L on Murray to Lower Tumut (66) trip; Feedback | Outage | Thermal | Vic
V>>NIL_SMDD_SMDD | 0.16667 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL | Thermal | Vic
V^^S_RBPA_MAXG | 0.16667 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA | Outage | Voltage Stability | SA
V_GANWRSF_0INV | 0.16667 | 0.75 | Gannawarra Solar Farm inverter limit of zero. Constraint to violate if Gannawarra Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | Vic
V_T_FCSPS_DS | 0.16667 | 0 | Basslink limit from Vic to Tas for FCSPS scheme outage, DS only. Swamped when FCSPS scheme in service and load available for arming | NIL | Other | Vic
V_WEMENSF_21INV | 0.16667 | 0 | Wemen Solar Farm inverter limit of 21. Constraint to violate if Wemen Solar Farm inverter availability greater than 21. Swamp out otherwise. DS only | Outage | System Strength | Vic
N_BOMENSF1_0INV | 0.16667 | 0 | Bomen Solar Farm inverter limit of zero. Constraint to violate if Bomen Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
#BRAEMAR1_E | 0.083333 | 1.75 | QBRA1.ENERGY * 1 <= 188 (Wt = 360) | Other | DEFAULT | Quick
#CHBESSL1_E | 0.083333 | 0 | QWDB2C.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
#MANNSF2_E | 0.083333 | 0 | SMAE1M.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
#OAKEY2SF_E | 0.083333 | 0 | QTKS2O.ENERGY * 1 <= 55 (Wt = 360) | Other | DEFAULT | Quick
#WELLSF1_E | 0.083333 | 0 | NWLS4W.ENERGY * 1 <= 170 (Wt = 360) | Other | DEFAULT | Quick
N::Q_LDTM_KC | 0.083333 | 0 | Out= Liddell-Tomago (82), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
N>>11_39_17 | 0.083333 | 0 | Out = Dapto-Sydney South (11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage | Thermal | NSW
N>>64_07_03 | 0.083333 | 0 | Out = LowerTumut-UpperTumut (64), avoid O/L Lower Tumut to Canberra (07) on trip of Lower Tumut to Yass (03) line, Feedback | Outage | Thermal | NSW
N>>LDTM_964_81_CL | 0.083333 | 0 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV closed, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage | Thermal | NSW
N>>NIL_64_65 | 0.083333 | 0 | Out = Nil, avoid Lower Tumut to Upper Tumut(64) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL | Thermal | NSW
N>>NIL_X3_060 | 0.083333 | 0 | Out= Nil, avoid O/L Balranald to Buronga (X3) on trip of Jindera to Wodonga (060) line, Feedback | NIL | Thermal | NSW
N>>V_SMDD6 | 0.083333 | 1.4167 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
N>NIL_9R5_9R6 | 0.083333 | 0 | Out= Nil, avoid O/L Wagga North to Wagga330 (9R5) on trip of Wagga North to Wagga 132 (9R6) line, Feedback | NIL | Thermal | NSW
N>WLTX_94T_WLTX | 0.083333 | 0.25 | Out= one of the Wellington 132/330kV Transformers, avoid O/L on Molong to Orange North (94T) on trip of remaining Wellington 132/330kV transformer, Feedback | Outage | Thermal | NSW
NC_N_COLWF01 | 0.083333 | 0 | Non Conformance Constraint for COLLECTOR WIND FARM | Other | Non-Conformance | Non-Conformance
NC_N_GULLRWF1 | 0.083333 | 0 | Non Conformance Constraint for Gullen Range Wind Farm | Other | Non-Conformance | Non-Conformance
NC_N_GULLRWF2 | 0.083333 | 0 | Non Conformance Constraint for GULLEN RANGE WF2 | Other | Non-Conformance | Non-Conformance
NC_N_LD01 | 0.083333 | 0.5 | Non Conformance Constraint for Liddell LD01 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_STWF1 | 0.083333 | 0 | Non Conformance Constraint for SILVERTON WIND FARM | Other | Non-Conformance | Non-Conformance
NC_Q_BARRON-2 | 0.083333 | 0 | Non Conformance Constraint for Barron Gorge 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_CHBESS_ADG1 | 0.083333 | 0 | Non Conformance Constraint for CHBESS_ADG1 | Other | Non-Conformance | Non-Conformance
NC_Q_DDPS1 | 0.083333 | 0.083333 | Non Conformance Constraint for Darling Downs Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_KAREEYA2 | 0.083333 | 0.41667 | Non Conformance Constraint for Kareeya 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_TARONG#2 | 0.083333 | 0.16667 | Non Conformance Constraint for Tarong 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_TARONG#4 | 0.083333 | 0 | Non Conformance Constraint for Tarong 4 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_MTMILLAR | 0.083333 | 1.0833 | Non Conformance Constraint for Mount Millar Wind Farm | Other | Non-Conformance | Non-Conformance
NC_S_PPCCGT | 0.083333 | 0.16667 | Non Conformance Constraint for Pelican Point Power Station | Other | Non-Conformance | Non-Conformance
NC_S_QPS4 | 0.083333 | 20.3333 | Non Conformance Constraint for Quarantine QPS4 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_WPWF | 0.083333 | 0 | Non Conformance Constraint for Wattle Point Wind Farm | Other | Non-Conformance | Non-Conformance
NC_T_CTHLWF1 | 0.083333 | 0 | Non Conformance Constraint for CATTLE HILL WF 1 | Other | Non-Conformance | Non-Conformance
NC_V_HBESSG1 | 0.083333 | 0 | Non Conformance Constraint for HBESS GENERATION 1 | Other | Non-Conformance | Non-Conformance
NC_V_LYA3 | 0.083333 | 0 | Non Conformance Constraint for Loy Yang A3 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_YWPS1 | 0.083333 | 1.1667 | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Other | Non-Conformance | Non-Conformance
N_BODWF1_0WT | 0.083333 | 0 | Constraint to violate if Bodangora WF turbines On greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
N_COLEASF1_FLT_50 | 0.083333 | 4.6667 | Limit Coleambally solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_DARLSF1_0INV | 0.083333 | 0 | Darlington Point Solar Farm inverter limit of zero. Constraint to violate if Darlington Point Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_DARLSF_FLT_193 | 0.083333 | 1.3333 | Limit Darlington Pt Solar Farm upper limit to 193 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_DARL_BAT_L_ZERO | 0.083333 | 0 | Darlington Point Battery (Load Component) upper limit of 0 MW | Outage | Unit Zero | NSW
N_FINLEYSF_81INV | 0.083333 | 0 | Finley Solar Farm inverter limit of 81. Constraint to violate if Finley Solar Farm inverter availability greater than 81. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_GNNDHSF1_63INV | 0.083333 | 0 | Gunnedah Solar Farm inverter limit of 63. Constraint to violate if Gunnedah Solar Farm inverter availability greater than 63. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_LIMOSF1_0INV | 0.083333 | 0 | Limondale 1 Solar Farm inverter limit of zero. Constraint to violate if Limondale 1 Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_METZSF_38 | 0.083333 | 0 | Metz Solar farm upper limit of 38 MW | Outage | System Strength | NSW
N_METZSF_38INV | 0.083333 | 0 | Metz Solar Farm inverter limit of 38. Constraint to violate if Metz Solar Farm inverter availability greater than 38. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_MOREESF1_55INV | 0.083333 | 0 | Moree Solar Farm inverter limit of 55. Constraint to violate if Moree Solar Farm inverter availability greater than 55. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_WELLSF1_ZERO | 0.083333 | 1.5833 | Wellington solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_WRWSF_060 | 0.083333 | 0 | White Rock wind farm and White Rock solar farm upper limit of 60 MW | Outage | System Strength | NSW
N_WR_55_WT-INV | 0.083333 | 0 | White Rock Wind & Solar Farm inverter limit of 55. Constraint to violate if White Rock Wind & Solar Farm inverter availability greater than 55. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q-COLSF_MVAR | 0.083333 | 11.25 | Constraint to violate if Reactive power output of Collinsville Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-KIDSF_MVAR | 0.083333 | 19.5 | Constraint to violate if Reactive power output of Kidston Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q>>WOPW_WOSP_WOGP_2 | 0.083333 | 60.75 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
Q>N_LSLS_9U8 | 0.083333 | 0 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 Directlink cable O/S. | Outage | Thermal | Qld
Q>X_SRMB_PBMB | 0.083333 | 0 | Out = T015 (Susan River to T59 Maryborough) 66kV line and T014 (Pialba to T59 Maryborough) 66kV line, limit Susan River to 60MW | Outage | Thermal | Qld
QNI_SOUTH_1100_DYN | 0.083333 | 0 | QLD to NSW on QNI upper transfer limit of 1100 MW, dynamic headroom with Max calc on the QNI, DS formulation only. | Outage | Transient Stability | Qld
QN_1300_DYN_TEST | 0.083333 | 0 | QLD to NSW on QNI upper transfer limit of 1300 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | Qld
Q^^N_TW_SVC_SRAR | 0.083333 | 0 | Out = Tamworth SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
Q_KEP-HYB_27MW | 0.083333 | 1 | Kennedy Energy Park upper limit of 27MW | Outage | Discretionary | Qld
Q_SRSF1_ZERO | 0.083333 | 0 | Susan River Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
Q_STR_7C2K_KBWF_8 | 0.083333 | 0 | Limit to Kaban Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Haughton Syncon ON, Zero otherwise. | Outage | System Strength | Qld
S:V_PA_SVC_270 | 0.083333 | 40.9167 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage | Oscillatory Stability | SA
S>>BWMP_DVBR_BGTX2 | 0.083333 | 1.1667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Bungama 275/132kV (TX2) on trip of Davenport-Brinkworth 275 kV line, Feedback | Outage | Thermal | SA
S>>NIL_TBTU_TBTU_1 | 0.083333 | 0 | Out= NIL, avoid O/L Tailem Bend-Tungkillo 275kV line 1 or 2 on trip of parallel Tailem Bend-Tungkillo 275 kV line 2 or 1, Feedback | NIL | Thermal | SA
S>>NIL_TUTB_TUTB_1 | 0.083333 | 0 | Out= NIL, avoid O/L Tungkillo-Tailem Bend 275kV line 1 or 2 on trip of parallel Tungkillo-Tailem Bend 275 kV line 2 or 1, Feedback | NIL | Thermal | SA
S>>RBTX_BRTW_WTTP | 0.083333 | 0 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo - Templers 132kV on trip of Brinkworth - Templers West 275kV line, Feedback | Outage | Thermal | SA
S>>TBTX4_TBTU_TBTU | 0.083333 | 0 | Out= Tailem Bend 275/132kV #4 TX (Black Range series caps I/S), avoid O/L of one Tailem Bend-Tungkillo 275 kV line on trip of other Tailem Bend-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
S>>X_CNRB+RBTX_13 | 0.083333 | 0 | Out= One Robertstown TX + Canowie-Robertstown 275kV line O/S, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>X_CR+RBTX+TPRS_15 | 0.083333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L Templers West-Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
S>>X_CR+RBTX+TPRS_21 | 0.083333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of MWP4-Robertstown 132kV line (This trip MWP4 SF) line, Feedback | Outage | Thermal | SA
S>BWMP_MKRB_CNRB | 0.083333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Canowie-Robertstown 275kV on trip of Mokota-Robertstown 275kV line(this offloads Belalie-Mokota 275kV line and trips Hallet 2 Hill WF) , Feedback | Outage | Thermal | SA
S>NIL_NIL_MHNW2 | 0.083333 | 0 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
S>NIL_WERB_WEWT | 0.083333 | 0 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | Thermal | SA
S>RBPA_BWMP_HUWT | 0.083333 | 0 | Out= Robertstown-Para 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>WERB_WTTP_STBG-T | 0.083333 | 0 | Out= Robertstown - MWP4 - Waterloo East O/S(offloads MWP4 SF), avoid O/L Snowtown-Bungama T 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | Thermal | SA
S>X-MNWT+CB_01 | 0.083333 | 0 | Out= Mintaro-Waterloo 132kV line + associated line CBs O/S, avoid O/L Snowtown-Bungama T 132kV line on trip of Waterloo -Templers 132kV line (this offloads Hummocks-Waterloo 132 kV line), Feedback | Outage | Thermal | SA
SVML_060 | 0.083333 | 0 | SA to Vic on ML upper transfer limit of 60 MW | Outage | Discretionary | SA
S^DVPPL_CRK+MTM_109 | 0.083333 | 0 | Out= Any line between Davenport, Cultana and Port Lincoln, Upper limit for Cathedral Rocks WF + Mt Millar WF <= 109 MW to maintain voltage stability limits | Outage | Voltage Stability | SA
T::T_HA_GT_PM_6 | 0.083333 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT out of service. | Outage | Transient Stability | Tas
T>T_GTHA_IMP_4L | 0.083333 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
T>T_HAPM_IMP_4C | 0.083333 | 0 | Out = Hadspen to Palmerston No. 1 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
T>T_HAPM_IMP_4D | 0.083333 | 0 | Out = Hadspen to Palmerston No. 1 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow North) for trip of either Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
T>T_NIL_BL_3B | 0.083333 | 0 | Out = Nil, avoid pre-contingent O/L of the Palmerston to Hadspen No. 2 220kV line (flow to North), feedback | NIL | Thermal | Tas
T>T_NIL_BL_IMP_3F | 0.083333 | 0 | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
T>T_NIL_BL_IMP_3FF | 0.083333 | 0 | Out = Nil, avoid O/L Palmerston to Hadspen No. 2 220 kV line (flow to North) for trip of the Palmerston to Hadspen No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
V::N_WBHO_xxx | 0.083333 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V:S_570_OSC_AUTO | 0.083333 | 0.083333 | Out = NIL (Note: with both Black Range series capacitors I/S), Upper transfer limit of 570 MW on VIC to SA on Heywood, Active only when I25 mode cannot be monitored. | NIL | Oscillatory Stability | Vic
V:S_PA_SVC_550 | 0.083333 | 0 | Out= one Para SVC (Note: with both Black Range series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 550 MW | Outage | Oscillatory Stability | Vic
V>>N_64_66_65_N | 0.083333 | 0 | Out = LowerTumut-UpperTumut (64), avoid Murray to Lower Tumut (66) O/L on Murray to Upper Tumut (65) trip; Feedback | Outage | Thermal | Vic
V>>N_NIL_66_65 | 0.083333 | 2.3333 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL | Thermal | Vic
VSML_150 | 0.083333 | 0 | Vic to SA on ML upper transfer limit of 150 MW | Outage | Discretionary | Vic
V^^S_MLSY_2 | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Voltage Stability | Vic
V^^S_PAVC_MAXG | 0.083333 | 0 | Out= Para one SVC (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V^^S_TBEBUS_SETB | 0.083333 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line | Outage | Voltage Stability | SA
V^^S_XPAVC_SETB | 0.083333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
V_ARWF_FSTTRP_5 | 0.083333 | 0 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Discretionary | Vic
V_BANSF_0INV | 0.083333 | 0 | Bannerton Solar Farm inverter limit of zero. Constraint to violate if Bannerton Solar Farm inverter availability greater than zero. Swamp out otherwise. DS only | Outage | System Strength | Vic
V_BRYBWF_ZERO | 0.083333 | 0.5 | Berrybank Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V_BULGWF_ISL_0 | 0.083333 | 0 | Bulgana Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V_MURRAWR2_ZERO | 0.083333 | 0 | Murra Warra 2 wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
V_SALTCREEK_ZERO | 0.083333 | 0 | Salt Creek wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
V_SH_DD_MAC_FLT_965 | 0.083333 | 0 | Limit Stockyard Hill, Dundonnell and Macarthur wind farm total output to 965 MW if Heywood flow is above 500 MW (SA to VIC direction). Swamp otherwise. This is to manage voltage oscillation. | NIL | System Strength | Vic

## Binding FCAS
Constraint Equation ID | 2023 Hours | 2022 Hours | Description | Type
F_I+NIL_APD_TL_L60 | 7510.9167 | 5574.5 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R6 | 6739.0833 | 5453.1667 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL
F_T+RREG_0050 | 6452.1667 | 1129 | Tasmania Raise Regulation Requirement greater than 50 MW | NIL
F_T+LREG_0050 | 6309.9167 | 1158.4167 | Tasmania Lower Regulation Requirement greater than 50 MW | NIL
F_I+BIP_ML_L6 | 6008.75 | 34.3333 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL
F_I+NIL_MG_R60 | 5798.25 | 4710.6667 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL
F_I+NIL_APD_TL_L5 | 5761.9167 | 5726.75 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R5 | 5124.5833 | 5231.6667 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL
F_TASCAP_RREG_0220 | 4829.5 | 1139.1667 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_TASCAP_LREG_0210 | 3704.3333 | 1167.9167 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_T_AUFLS2_R6 | 3635.25 | 4340.4167 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL
F_MAIN++APD_TL_L5 | 3083.8333 | 1846.9167 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 2410.4167 | 947.9167 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_I+LREG_0210 | 2330.5 | 6886.4167 | NEM Lower Regulation Requirement greater than 210 MW | NIL
F_MAIN++LREG_0210 | 2172.3333 | 642.5 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R60 | 2054.0833 | 1727.75 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_I+NIL_MG_R1 | 1963.9167 | 0 | Out = Nil, Raise 1 sec requirement for a NEM Generation Event. Requirement capped at 225 MW | NIL
F_I+RREG_0220 | 1949.5 | 6654.25 | NEM Raise Regulation Requirement greater than 200 MW | NIL
F_MAIN++NIL_MG_R6 | 1811.9167 | 1515.0833 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_I+NIL_APD_TL_L6 | 1687.5 | 3593.5833 | Lower 6 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_MAIN++RREG_0220 | 1672.9167 | 416 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
F_T++NIL_ML_L6 | 1312.8333 | 51 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
F_MAIN++APD_TL_L60 | 1303.9167 | 1628.25 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_I+BIP_ML_L1 | 1182.9167 | 0 | Out = Nil, Lower 1 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. Requirement capped at 125 MW | Outage
F_T+NIL_ML_L60 | 1105.1667 | 4258.5 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L6 | 1071.9167 | 4546.0833 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T++NIL_ML_L60 | 940.0833 | 33.6667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
F_T+NIL_ML_L5 | 844.25 | 2206.8333 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_I+GFT_TG_R60 | 711.25 | 478.8333 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_T++RREG_0050 | 689.5 | 529.25 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_I+GFT_TG_R5 | 684.8333 | 558.8333 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_I+TTS_TG_R60 | 670.4167 | 696.3333 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_I+TTS_TG_R5 | 659.25 | 720.5 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_MAIN++APD_TL_L6 | 594.25 | 1042.4167 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_MAIN++BIP_ML_L1 | 576.9167 | 0 | Out = Nil, Lower 1 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS. Requirement capped at 125 MW | Outage
F_MAIN+NIL_DYN_RREG | 558.8333 | 598.25 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL
F_T+NIL_BL_R60_1 & F_T++NIL_BL_R60_x | 443.5 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 400ms | NIL
F_MAIN+NIL_MG_R6 | 421.9167 | 1115 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN++BIP_ML_L6 | 418.0833 | 1.5833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
F_MAIN+RREG_0220 | 416.0833 | 1089.9167 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 407.75 | 1118.0833 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L5 | 406.8333 | 959.9167 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R60 | 391 | 1958.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink unable to transfer FCAS | NIL
F_MAIN+LREG_0210 | 388.3333 | 1061.0833 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 380.6667 | 1020.3333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 378.75 | 1015.6667 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_DYN_LREG | 362.3333 | 263.1667 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL
F_T++NIL_MG_RECL_R6 | 356.3333 | 84.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | NIL
F_T+NIL_BL_R6_1 & F_T++NIL_BL_R6_x | 341.9167 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 400ms | NIL
F_MAIN+BIP_ML_L6 | 314.3333 | 8.5833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL
F_T+NIL_MG_RECL_R6 | 306.1667 | 1779.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_BL_L60 | 288.5 | 876.4167 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_I+GFT_TG_R6 | 253.5833 | 247.8333 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_I+TTS_TG_R6 | 250.0833 | 413.4167 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_T+NIL_MG_RECL_R5 | 247.5 | 1237 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink unable to transfer FCAS | NIL
F_T++NIL_MG_RECL_R60 | 184.3333 | 94.4167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | NIL
F_T++NIL_WF_TG_R6 | 180 | 13.25 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL
F_T++NIL_ML_L5 | 164.75 | 11.5 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 159.4167 | 1143.8333 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_T++NIL_WF_TG_R60 | 153.25 | 30.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL
F_T++NIL_MG_RECL_R5 | 132.6667 | 79.5833 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | NIL
F_T++NIL_WF_TG_R5 | 130.8333 | 41.8333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL
F_MAIN++GFT_TG_R5 | 122 | 96.5 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_T+NIL_WF_TG_R6 | 117.0833 | 1043.5833 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_MAIN++GFT_TG_R60 | 116.9167 | 166.25 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_T+NIL_BL_R5 | 102.3333 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available, LoL = 400ms | NIL
F_T+NIL_MG_R60 | 97.8333 | 1848.6667 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L6 | 94.8333 | 812.1667 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_T++LREG_0050 | 94.1667 | 295.3333 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_T+NIL_WF_TG_R5 | 90.3333 | 1010.25 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_S++HYSE_L60 | 86.25 | 230.8333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
F_S++HYSE_L6_1 | 59.1667 | 191 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
F_T++NIL_MG_R6 | 47.4167 | 13.4167 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL
F_V_APD01_R6 | 47.1667 | 0 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage
F_V_APD01_R5 | 47.0833 | 0 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage
F_V_APD01_R60 | 47.0833 | 0 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage
F_T++NIL_MG_R60 | 45.5833 | 29.6667 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL
F_T+NIL_MG_R6 | 43.75 | 1827.25 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T_NIL_MINP_R6 | 41.9167 | 650.5 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL
F_I+BIP_ML_L60 | 40.5 | 24.9167 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL
F_Q++BCDM_L6 | 40.0833 | 24.4167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
F_MAIN++ML_L6_APD_LD | 38.25 | 32.1667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
F_MAIN+GFT_TG_R60 | 38 | 113.0833 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+GFT_TG_R5 | 37.9167 | 112.8333 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_Q++86_L6 | 36.6667 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 6 sec Requirement | Outage
F_Q++86_L60 | 35.1667 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 60 sec Requirement | Outage
F_I+BIP_ML_L5 | 33.1667 | 2.1667 | Out = Nil, Lower 5 min requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL
F_S++HYSE_L5 | 30.6667 | 30.1667 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
F_MAIN+TTS_TG_R60 | 26.9167 | 26.5 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL
F_MAIN+TTS_TG_R5 | 26.9167 | 26.75 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL
F_Q++BCDM_L60 | 26.1667 | 22.5833 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage
F_MAIN++TTS_TG_R5 | 22.4167 | 29.0833 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
F_MAIN+NIL_MG_R1 | 22.25 | 0 | Out = Nil, Raise 1 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS. Requirement capped at 225 MW | NIL
F_MAIN++TTS_TG_R60 | 22 | 71.8333 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
F_T+NIL_MG_R5 | 21.3333 | 1719.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++GFT_TG_R6 | 20 | 55.8333 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_ESTN++HYTR_L60 | 19.5 | 8.5833 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_MAIN++NIL_MG_R1 | 17.8333 | 0 | Out = Nil, Raise 1 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS. Requirement capped at 225 MW | NIL
F_Q++MUTW_L6 | 16 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
F_Q++MUTW_L60 | 15.5 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
F_ESTN++HYTR_L6 | 14.8333 | 9.1667 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
F_Q++8E_L6 | 14.4167 | 24.75 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
F_S_HPRG1_R1 | 13 | 0 | Out = NIL, Hornsdale BESS R1 Requirement <= 0 MW | Outage
F_V_DRVIOT02_R1 | 13 | 0 | Out = NIL, DR VIOTAS V SL1 R1 Requirement <= 0 MW | Outage
F_Q_ASQENC1_R1 | 13 | 0 | Out = NIL, AGG INTERRUP LOAD Q1 R1 Requirement <= 0 MW | Outage
F_S_ASRMGE01_L1 | 13 | 0 | Out = NIL, AS RMGE S VL1 L1 Requirement <= 0 MW | Outage
F_S_ASRMGE01_R1 | 13 | 0 | Out = NIL, AS RMGE S VL1 R1 Requirement <= 0 MW | Outage
F_S_ASRMGE03_R1 | 13 | 0 | Out = NIL, AS RMGE S VL3 R1 Requirement <= 0 MW | Outage
F_S_HPRL1_L1 | 13 | 0 | Out = NIL, Hornsdale BESS L1 Requirement <= 0 MW | Outage
F_N_QBYNBL1_L1 | 13 | 0 | Out = NIL, Queanbeyan BESS L1 Requirement <= 0 MW | Outage
F_Q_DRVIOT04_R1 | 13 | 0 | Out = NIL, DR VIOTAS Q SL1 R1 Requirement <= 0 MW | Outage
F_V_BULBESL1_L1 | 13 | 0 | Out = NIL, Bulgana BESS L1 Requirement <= 0 MW | Outage
F_N_QBYNBG1_R1 | 13 | 0 | Out = NIL, Queanbeyan BESS R1 Requirement <= 0 MW | Outage
F_N_WALGRVL1_L1 | 13 | 0 | Out = NIL, Wallgrove BESS L1 Requirement <= 0 MW | Outage
F_S_ASRMGE02_R1 | 13 | 0 | Out = NIL, AS RMGE S VL2 R1 Requirement <= 0 MW | Outage
F_S_LBBL1_L1 | 13 | 0 | Out = NIL, Lake Bonney BESS L1 Requirement <= 0 MW | Outage
F_T_DRVIOT05_R1 | 13 | 0 | Out = NIL, DR VIOTAS T SL1 R1 Requirement <= 0 MW | Outage
F_V_VBBL1_L1 | 13 | 0 | Out = NIL, VIC Big Battery L1 Requirement <= 0 MW | Outage
F_N_ASNENC1_R1 | 13 | 0 | Out = NIL, AGG INTERRUP LOAD N1 R1 Requirement <= 0 MW | Outage
F_N_WALGRVG1_R1 | 13 | 0 | Out = NIL, Wallgrove BESS R1 Requirement <= 0 MW | Outage
F_S_ASRMGE02_L1 | 13 | 0 | Out = NIL, AS RMGE S VL2 L1 Requirement <= 0 MW | Outage
F_S_ASRMGE03_L1 | 13 | 0 | Out = NIL, AS RMGE S VL3 L1 Requirement <= 0 MW | Outage
F_S_LBBG1_R1 | 13 | 0 | Out = NIL, Lake Bonney BESS R1 Requirement <= 0 MW | Outage
F_V_VENUS1_R1 | 13 | 0 | Out = NIL, AGG INTERRUP LOAD V1 R1 Requirement <= 0 MW | Outage
F_N_DRVIOT03_R1 | 13 | 0 | Out = NIL, DR VIOTAS N SL1 R1 Requirement <= 0 MW | Outage
F_S_ASSENC1_R1 | 13 | 0 | Out = NIL, AGG INTERRUP LOAD S1 R1 Requirement <= 0 MW | Outage
F_S_DRVIOT01_R1 | 13 | 0 | Out = NIL, DR VIOTAS S SL1 R1 Requirement <= 0 MW | Outage
F_V_BULBESG1_R1 | 13 | 0 | Out = NIL, Bulgana BESS R1 Requirement <= 0 MW | Outage
F_V_VBBG1_R1 | 13 | 0 | Out = NIL, VIC Big Battery R1 Requirement <= 0 MW | Outage
F_I+ML_L6_APD_LD | 12.8333 | 11.5 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage
F_MAIN+BIP_ML_L1 | 12.5833 | 0 | Out = Nil, Lower 1 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS. Requirement capped at 125 MW | Outage
F_MAIN+TTS_TG_R6 | 12.4167 | 6.1667 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL
F_MAIN++BIP_ML_L5 | 12 | 0.41667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
F_Q++MUTW_L5 | 11.6667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
F_MAIN+GFT_TG_R6 | 11.5833 | 40.4167 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_Q++86_L5 | 10.6667 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 5 min Requirement | Outage
F_Q++LDTW_L6 | 9.5 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
F_Q++LDTW_L60 | 9.4167 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
F_T+FA_B_N-2_RREG | 9.4167 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, Bastyan, John Butters, Reece 1 & 2, and Tribute Raise Regulation Requirement = 0 | Outage
F_T++NIL_MG_R5 | 9.1667 | 59.5 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL
F_T++FARE_N-2_TG_R6 | 8.1667 | 0.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
F_Q++85_L6 | 8.0833 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 6 sec Requirement | Outage
F_T++FA_B_N-2_TG_R6 | 8 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
F_Q++LDTW_L5 | 7.6667 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
F_Q++85_L60 | 7.5833 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 60 sec Requirement | Outage
F_ESTN++MLMO_L60 | 6.9167 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_S+MLMO_TL_L60 | 6.25 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
F_T+FARE_N-2_RREG | 6.1667 | 8.1667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_T++FARE_N-2_TG_R60 | 5.5833 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
F_I+ML_ST1_L6 | 5.25 | 4.4167 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_Q++BCDM_L5 | 5.25 | 1.3333 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
F_S+MLMO_TL_L6_1 | 4.6667 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage
F_T_REECE1_R6 | 4.4167 | 0 | Out= NIL, Reece 1 R6 Requirement <= 0MW | Outage
F_T_REECE2_R6 | 4.4167 | 0 | Out= NIL, Reece 2 R6 Requirement <= 0MW | Outage
F_Q++8E_R6 | 4.25 | 1.1667 | Out = Sapphire to Armidale (8E) line, Qld Raise 6 sec Requirement | Outage
F_Q++8C_L6 | 4.1667 | 24.8333 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
F_Q++8E_L60 | 4 | 24.4167 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage
F_T+FARE_N-2_TG_R5 | 3.8333 | 9.6667 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_Q++BCDM_R60 | 3.75 | 1.5 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage
F_Q++BCDM_R6 | 3.6667 | 1 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
F_T++FA_B_N-2_TG_R60 | 3.5833 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
F_ESTN+MCSH_TG_R60 | 3.5 | 1.5 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line | Outage
F_Q++MUTW_R60 | 3.3333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
F_S+MLMO_TL_L5 | 3.25 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 5 min requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
F_S++HYSE_L6_2 | 3.0833 | 0.41667 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage
F_T++FARE_N-2_TG_R5 | 3.0833 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 5 min requirement, Basslink able to transfer FCAS | Outage
F_Q++8C_L60 | 2.9167 | 24.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage
F_Q++NIL_R60 | 2.75 | 0.83333 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL
F_T++FASH_1_TG_R6 | 2.75 | 0 | Out= Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_T+FARE_N-2_TG_R60 | 2.5833 | 3.8333 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_QNV++HYTR_L60 | 2.4167 | 0.33333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++NIL_R5 | 2.4167 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
F_S_DLBAT-G_R6 | 2.3333 | 22.0833 | Out= NIL, Dalrymple Battery (Generation Component) R6 Requirement <= 0MW | Outage
F_S_DLBAT-G_R5 | 2.3333 | 21.9167 | Out= NIL, Dalrymple Battery (Generation Component) R5 Requirement <= 0MW | Outage
F_S+MLMO_TL_L6_2 | 2.3333 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage
F_S_DLBAT-G_R60 | 2.3333 | 22.1667 | Out= NIL, Dalrymple Battery (Generation Component) R60 Requirement <= 0MW | Outage
F_T+FARE_N-2_TG_R6 | 2.25 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage
F_S_DLBAT-L_L60 | 2.25 | 22.25 | Out= NIL, Dalrymple Battery (Load Component) L60 Requirement <= 0MW | Outage
F_S_DLBAT-L_L6 | 2.25 | 18.5 | Out= NIL, Dalrymple Battery (Load Component) L6 Requirement <= 0MW | Outage
F_QNV+HYTR_L60 | 2.25 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_S_DLBAT-L_L5 | 2.1667 | 18.3333 | Out= NIL, Dalrymple Battery (Load Component) L5 Requirement <= 0MW | Outage
F_MAIN++BIP_ML_L60 | 2.0833 | 1.1667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
F_T_JBUTTERS_L60 | 2.0833 | 0 | Out= NIL, John Butters L60 Requirement <= 0MW | Outage
F_ESTN+MCSH_TG_R5 | 2 | 4.75 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line | Outage
F_T_FISHER_L6 | 1.9167 | 0 | Out= NIL, Fisher L6 Requirement <= 0MW | Outage
F_MAIN+BIP_ML_L60 | 1.75 | 5.25 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL
F_MAIN++NIL_BL_L6 | 1.6667 | 31.8333 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_MAIN+BIP_ML_L5 | 1.6667 | 0.16667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL
F_QNV+HYTR_L6 | 1.6667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_ESTN++HYTR_L5 | 1.5833 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
F_T++COGT_TL_L6 | 1.4167 | 0 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
F_Q++MUTW_R6 | 1.4167 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
F_T++FASH_1_TG_R5 | 1.4167 | 0 | Out= Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_T++FASH_1_TG_R60 | 1.4167 | 0 | Out=Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_ESTN++MLMO_L6 | 1.3333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
F_T++COGT_TL_L5 | 1.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
F_MAIN+ML_L6_APD_LD | 1.25 | 1.5 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage
F_Q++85_L5 | 1.25 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 5 min Requirement | Outage
F_T++CO_752_TL_L6 | 1.25 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | Outage
F_T++NIL_TL_L6_DS | 1.1667 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_T++COGT_TL_L60 | 1.1667 | 0 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
F_T_FARC1_R6 | 1.0833 | 0 | Out=Farrell-Reece 1 220KV line. R6 <= 0MW | Outage
F_QNV++HYTR_L5 | 1.0833 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_BLSPS_R6 | 1.0833 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, FCSPS unavailable. DS Only | NIL
F_T++NIL_BLSPS_R60 | 1.0833 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, FCSPS unavailable. DS Only | NIL
F_T++BL_650_R60_3 | 1 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage
F_T++NIL_BLSPS_R5 | 1 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS unavailable. DS Only | NIL
F_T++BL_650_R60_2 | 1 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage
F_T+BL_650_R5 | 1 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available, LoL = 650 ms | Outage
F_Q++8U_L6 | 1 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
F_S_LBBL1_LREG | 0.91667 | 24.9167 | Out= NIL, Lake Bonney Battery (Load Component) LREG Requirement <= 0MW | Outage
F_I+GFT_TG_R1 | 0.83333 | 0 | Out = Nil, Raise 1 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT for a trip of ARTS - WBTS - BATS 220kV line. Requirement capped at 225 MW | Outage
F_MAIN++TTS_TG_R6 | 0.83333 | 18.8333 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
F_Q++8U_L60 | 0.83333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_T+FARE_N-2_TG_R6_2 | 0.83333 | 5.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage
F_Q++NIL_R6 | 0.83333 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 6 sec requirement for loss of a NSW 750 MW unit | NIL
F_N_WALGR_BAT_G_R6 | 0.83333 | 0.25 | Out= Nil, Wallgrove BESS (generation component) Raise 6 sec Requirement <= 0MW | Outage
F_T+BL_650_R60_1 | 0.83333 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage
F_T++BL_650_R6_3 | 0.83333 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage
F_T_FARC1_R60 | 0.83333 | 0 | Out=Farrell-Reece 1 220KV line. R60 <= 0MW | Outage
F_T++BLSPS_IMP_R60_1 | 0.83333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 1 | Outage
F_QNV+HYTR_L5 | 0.75 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_T++CO_752_TL_L60 | 0.75 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | Outage
F_T_CETHANA_L60 | 0.75 | 0 | Out= NIL, Cethana L60 Requirement <= 0MW | Outage
F_T+GTTE_TL_L60 | 0.75 | 88 | Out = one George Town to Temco 110 kV line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_T+GTTE_TL_L6 | 0.75 | 90.5833 | Out = one George Town to Temco 110 kV line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_T_DG_0_L60 | 0.75 | 0 | Devils Gate = 0MW L60 <= 0MW | Outage
F_N_WALGR_BAT_L_L6 | 0.75 | 0 | Out= Nil, Wallgrove BESS (load component) Lower 6 sec Requirement <= 0MW | Outage
F_QNV++HYTR_L6 | 0.66667 | 0.83333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_N_WALGR_BAT_L_L60 | 0.66667 | 0 | Out= Nil, Wallgrove BESS (load component) Lower 60 sec Requirement <= 0MW | Outage
F_T++BLSPS_IMP_R6_1 | 0.66667 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 1 | Outage
F_N_WALGR_BAT_G_RREG | 0.66667 | 0 | Out= Nil, Wallgrove BESS (generation component) Raise Regulation Requirement <= 0MW | Outage
F_N_WALGR_BAT_L_L5 | 0.66667 | 0 | Out= Nil, Wallgrove BESS (load component) Lower 5 min Requirement <= 0MW | Outage
F_Q++8E_L5 | 0.58333 | 1.5833 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
F_Q++MUTW_R5 | 0.58333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
F_N_WALGR_BAT_G_R60 | 0.58333 | 0.25 | Out= Nil, Wallgrove BESS (generation component) Raise 60 sec Requirement <= 0MW | Outage
F_S+NIL_HPR_G+L_LREG | 0.58333 | 0 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS LowerReg ramping constraint | NIL
F_T_JBUTTERS_L5 | 0.58333 | 0 | Out= NIL, John Butters L5 Requirement <= 0MW | Outage
F_Q++8U_R60 | 0.58333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
F_Q++8C_L5 | 0.58333 | 10.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
F_T++CO_752_TL_L5 | 0.58333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | Outage
F_MAIN+APD_TL_L1 | 0.58333 | 0 | Out = Nil, Lower 1 sec requirement for Mainland Network event, simultaneous loss of both APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS. Requirement capped at 125 MW | Outage
F_ESTN+MCSH_TG_R6 | 0.58333 | 0.41667 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line | Outage
F_I+NILL_MG_R1 | 0.58333 | 0 | Out = Nil, Raise 1 sec requirement for a NEM Generation Event. Requirement capped at 225 MW | NIL
F_T++FA_B_N-2_TG_R5 | 0.5 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 5 min requirement, Basslink able to transfer FCAS | Outage
F_Q++8U_L5 | 0.5 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
F_QNV+MLMO_L60 | 0.5 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T+NIL_TL_L60_DS | 0.5 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_MAIN++APD_TL_L1 | 0.5 | 0 | Out = Nil, Lower 1 sec requirement for Mainland Network event, simultaneous loss of both APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS. Requirement capped at 125 MW | Outage
F_T+CO_752_TL_L6 | 0.5 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_T+BL_650_R6_1 | 0.5 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage
F_ESTN++MLMO_L5 | 0.41667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
F_T_CETHANA_R60 | 0.41667 | 0 | Out= NIL, Cethana R60 Requirement <= 0MW | Outage
F_MAIN++GFT_TG_R1 | 0.41667 | 0 | Out= Nil, Raise 1 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT for a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS. Capped at 225 MW | Outage
F_QNV++MLMO_L60 | 0.41667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+CO_752_TL_L5 | 0.41667 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_I+TTS_TG_R1 | 0.41667 | 0 | Out = Nil, Raise 1 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) for contingency trip of line 63. Capped at 225 MW | Outage
F_T++BL_650_R6_2 | 0.41667 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage
F_I+ML_ST1_L60 | 0.33333 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 60 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_I+ML_ST1_L5 | 0.33333 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 5 min Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_T+FARE_N-2_TG_R6_1 | 0.33333 | 3.3333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage
F_T+NIL_TL_L5_DS | 0.33333 | 0.083333 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_N_WALGR_BAT_G_R5 | 0.33333 | 0.25 | Out= Nil, Wallgrove BESS (generation component) Raise 5 min Requirement <= 0MW | Outage
F_T_FARC2_R60 | 0.33333 | 0 | Out=Farrell-Reece 2 220KV line. R60 <= 0MW | Outage
F_QNV++MCSH_TG_R60 | 0.25 | 3.8333 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line, Basslink able to transfer FCAS | Outage
F_T+CO_752_TL_L60 | 0.25 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_T++NIL_TL_L60_DS | 0.25 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_N_WALGR_BAT_L_LREG | 0.25 | 0 | Out= Nil, Wallgrove BESS (load component) Lower Regulation Requirement <= 0MW | Outage
F_MAIN++TTS_TG_R1 | 0.25 | 0 | Out = Nil, Raise 1 sec req. for Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF, DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) for loss of line 63, Basslink able to transfer FCAS. Capped at 225 MW | Outage
F_T+NIL_TL_L6_DS | 0.25 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_I+BIPP_ML_L1 | 0.16667 | 0 | Out = Nil, Lower 1 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. Requirement capped at 125 MW | Outage
F_QNV+MLMO_L6 | 0.16667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_S+NIL_HPR_G+L_RREG | 0.16667 | 0 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS RaiseReg ramping constraint | NIL
F_MAIN++ST1_ML_L6 | 0.16667 | 0.66667 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
F_T_LEM_WIL_R60 | 0.16667 | 0 | Out= NIL, Lemonthyme + Wilmot R60 Requirement <= 0MW | Outage
F_T++NIL_TL_L5_DS | 0.16667 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_T++BLSPS_IMP_R6_2 | 0.083333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 2 | Outage
F_MAIN+ST1_ML_L6 | 0.083333 | 0.33333 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage
F_S_LBBG1_R5 | 0.083333 | 18.6667 | Out= NIL, Lake Bonney Battery (Generation Component) R5 Requirement <= 0MW | Outage
F_S_LBBG1_R60 | 0.083333 | 19.1667 | Out= NIL, Lake Bonney Battery (Generation Component) R60 Requirement <= 0MW | Outage
F_S_LBBL1_L5 | 0.083333 | 15.6667 | Out= NIL, Lake Bonney Battery (Load Component) L5 Requirement <= 0MW | Outage
F_T_FAJB_RREG | 0.083333 | 0 | Out=Farrell-John Butters 220KV line. RREG <= 0MW | Outage
F_T++BLSPS_IMP_R60_2 | 0.083333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 2 | Outage
F_T_FARC2_R6 | 0.083333 | 0.25 | Out=Farrell-Reece 2 220KV line. R6 <= 0MW | Outage
F_T++NIL_BL_R60_4 | 0.083333 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 4, FCSPS available | NIL
F_T+FASH_1_RREG | 0.083333 | 0 | Out = Farrell to Sheffield No.1 line; Bastyan, John Butters, Tribute and Reece 1, 2 and Mackintosh unavailable for raise regulation | Outage
F_Q++86_R60 | 0.083333 | 0 | Out = Armidale to Tamworth (86) line, Qld Raise 60 sec Requirement | Outage
F_T++NIL_BL_R6_4 | 0.083333 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 4, FCSPS available | NIL
F_T_JBUTTERS_RREG | 0.083333 | 0 | Out= NIL, John Butters RREG Requirement <= 0MW | Outage
F_T_REECE2_R60 | 0.083333 | 0 | Out= NIL, Reece 2 R60 Requirement <= 0MW | Outage
F_S_LBBL1_L60 | 0.083333 | 14.6667 | Out= NIL, Lake Bonney Battery (Load Component) L60 Requirement <= 0MW | Outage
F_T++BLSPS_IMP_R5 | 0.083333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 5 min Requirement for loss of Basslink | Outage
F_QNV+MCSH_TG_R60 | 0.083333 | 2.9167 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line, Basslink unable to transfer FCAS | Outage
F_S_LBBG1_R6 | 0.083333 | 15.4167 | Out= NIL, Lake Bonney Battery (Generation Component) R6 Requirement <= 0MW | Outage
F_S_LBBL1_L6 | 0.083333 | 15.6667 | Out= NIL, Lake Bonney Battery (Load Component) L6 Requirement <= 0MW | Outage
F_T_DG_0_RREG | 0.083333 | 0 | Devils Gate = 0MW. RREG <= 0MW | Outage
F_T_CETHANA_RREG | 0.083333 | 0 | Out= NIL, Cethana RREG Requirement <= 0MW | Outage
F_N_WALGR_BAT_L_RREG | 0.083333 | 0 | Out= Nil, Wallgrove BESS (load component) Raise Regulation Requirement <= 0MW | Outage

## Binding Impact
Constraint Equation ID | 2023 Marginal Values | 2022 Marginal Values | 2023 Hours | 2022 Hours | Description | Type | Limit Type | Region
N>NIL_94T | 23990532.1398 | 28433072.4362 | 1703.0833 | 1659.4167 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | NIL | Thermal | NSW
NSA_S_PORxxx | 22135066.9164 | 51310926.4179 | 158.0833 | 315 | Port Lincoln >= 15 MW for Network Support Agreement | Outage | Network Support | SA
N>NIL_969 | 19375989.8117 | 16282082.8499 | 1644.5833 | 1303.8333 | Out= Nil, avoid O/L Gunnedah to Tamworth (969) on trip of Nil, Feedback. Metering is used as specified in OM520 [Note: swamped with 96M or 9UJ or 9UH is O/S] | NIL | Thermal | NSW
N>>NIL_9XX_051 | 12652924.0901 | 0 | 914.1667 | 0 | Out= NIL, avoid O/L Burrinjuck to Yass (970) on trip of Wagga to Lower Tumut (051) line, Feedback | NIL | Thermal | NSW
N>NIL_94K_1 | 12452679.3381 | 9618211.7846 | 1253.5833 | 907.75 | Out= Nil, avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | NIL | Thermal | NSW
V^^V_NIL_KGTS V^^V_NIL_KGTS_2 | 8244169.272 | 5725925.8949 | 1140.5 | 861.6667 | Out= Nil, avoid voltage collapse for loss of Horsham - Murra Warra - Kiamal 220kV line. Murraylink VFRB disabled. Swamp if Murraylink VFRB enabled. | NIL | Voltage Stability | Vic
S>NIL_MHNW1_MHNW2 | 8148303.6665 | 12680695.6875 | 1336.6667 | 1562.75 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL | Thermal | SA
N^^N_NIL_X5_xxx | 7527221.3827 | 15180811.1913 | 1041.25 | 1526.75 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of Bendigo to Shepparton 220kV line in NW Victoria | NIL | Voltage Stability | NSW
Q>NIL_YLMR | 7345087.7412 | 4739618.9279 | 676.9167 | 604.5833 | Out= Nil, avoid overload on 110kV feeders between Yarranlea and Middle Ridge(733/1 and 734/1), Feedback | NIL | Thermal | Qld
N>NIL_9R6_9R5 | 5386845.0919 | 3040478.126 | 605.1667 | 299.25 | Out= Nil, avoid O/L Wagga North to Wagga132 (9R6) on trip of Wagga North to Wagga330 (9R5) line, Feedback | NIL | Thermal | NSW
N>NIL_997_99A | 4496412.2949 | 8702537.855 | 517.0833 | 687.3333 | Out= Nil, avoid O/L Corowa to Albury 132kV line (997/1) on trip of Finley to Uranquinty 132kV line (99A), Feedback | NIL | Thermal | NSW
N>NIL_9R6_991 | 4338900.5669 | 0 | 438.5833 | 0 | Out= Nil, avoid O/L Wagga North to Wagga (9R6) 132kV line on trip of Wagga North to Murrumburrah (991) 132kV line, Feedback | NIL | Thermal | NSW
V^^V_MLNK_KGTS | 3902970.6091 | 1524031.7314 | 319.1667 | 128.0833 | Out= Murraylink, avoid voltage collapse for loss of Horsham - Murra Warra - Kiamal 220kV line | Outage | Voltage Stability | Vic
S>NIL_HUWT_STBG3 | 3234034.9212 | 5291760.1523 | 368.25 | 382.0833 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Constraint Swamped when Wattle PT when generating >=60 MW) | NIL | Thermal | SA
N>94K2_94T_NIL | 3118519.4796 | 0 | 286.4167 | 0 | Out= Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only), avoid O/L on Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
N>NIL_PKTX_LV | 2775237.5035 | 3037072.5149 | 612.6667 | 631.0833 | Out= Nil, avoid O/L either Parkes 132kV/66kV Transformer on NIL trip, Feedback. | NIL | Thermal | NSW
S>NIL_NWRB2_NWRB1 | 2716676.0255 | 1628630.1497 | 376.75 | 223 | Out= NIL, avoid O/L North West Bend-Roberstown #1 132kV line on trip of North West Bend-Robertstown #2 132kV line (this trips MWP1-3 SFs), Feedback | NIL | Thermal | SA
V>>NIL_ARWB_KGBE | 2349117.2202 | 5698616.9732 | 255.25 | 485.5833 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
V_ARARATWF_FLT_0 | 2122957.0709 | 93755.3699 | 175.8333 | 7.5833 | Limit Ararat Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KIAMSF_FLT_50 | 1766375.2635 | 329150.7822 | 144 | 27.25 | Limit Kiamal solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_BANSF_BBD_S1 | 1712969.3585 | 0 | 182.9167 | 0 | Out = Nil, Bannerton SF limitation segment 1 if Boundary Bend (BBD) loading is less than 5 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
N>>DPTX1-2_TX_NIL | 1658533.3385 | 0 | 159.5833 | 0 | Out= one Darlington Pt 132/330kV TX1 or TX2, avoid O/L remaining Darlington Pt 132/330kV TX on trip of Nil, Feedback | Outage | Thermal | NSW
V_BANNERTSF_FLT_45 | 1459398.3428 | 381248.3978 | 119.9167 | 30.75 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>79_998_72 | 1411904.7935 | 0 | 19.9167 | 0 | Out= Wollar West to Wellington (79) 330kV line or Wollar 500/330kV TX or Wollar to Wollar West (75) 330kV line, avoid O/L on Cowra to Forbes North (998) on trip of Mt Piper to Wellington line (72), Feedback | Outage | Thermal | NSW
V_WEMENSF_FLT_45 | 1396645.2593 | 177370.8955 | 115.5833 | 19.5833 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S^NIL_SA_NTH_N-2 | 1364466.491 | 0 | 131.3333 | 0 | Out = NIL, Manage voltage collapse in northern SA for the loss of Robertstown - Tungkillo 275kV line 1 and 2 and the Robertstown No.1 and No.2 synchronous condensers declared credible | Outage | Voltage Stability | SA
F_T+RREG_0050 | 1352684.1044 | 604811.7386 | 6450.6667 | 1186 | Tasmania Raise Regulation Requirement greater than 50 MW | NIL | FCAS | FCAS
V_MURRAWRWF_FLT_90 | 1338245.8483 | 654586.5781 | 105.5 | 72 | Limit Murra Warra Wind Farm 1+2 upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
V_MURRAWRWF_FLT_100 | 1254060.1498 | 0 | 98.3333 | 0 | Limit Murra Warra Wind Farm 1+2 upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
V_KIAMSF_DYN | 1170149.1234 | 1481.5497 | 160.4167 | 0.33333 | Out = Kiamal Syncon, Limit Kiamal solar farm to 135 MW when Murra Warra 2 WF syncon I/S. Limit Kiamal solar farm to 100 MW when Murra Warra 2 WF syncon O/S | Outage | Discretionary | Vic
Q_STR_7C8C_KBWF | 1161749.2725 | 0 | 86.3333 | 0 | Limit Kaban Wind Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
V>>NIL_WBBA_KGBE | 1105218.5892 | 1441551.5253 | 120.1667 | 131.75 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
NRM_NSW1_VIC1 | 1085672.2948 | 1115390.1604 | 229.75 | 80.5833 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue | Negative Residue
Q>NIL_EMCM_6056 | 1023311.3921 | 8000154.5808 | 628.1667 | 969.8333 | Out= NIL, avoid thermal overload on Emerald to Comet (6056) 66 kV Feeder | NIL | Thermal | Qld
V_GANWRSF_FLT_30 | 1020665.3888 | 337001.4263 | 83.5 | 30.9167 | Limit Gannawarra solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_STR_KBWF_N-2 | 988326.1287 | 386661.3347 | 68 | 29.75 | Out = Nil, Loss of 858 and 857 declared credible. No limit to Kaban WF if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7, Kar>= 2,NQLD>350&370(AVG),Ross_FN>150&170(AVG) and Feeder 8905 IS, Zero otherwise. | Outage | System Strength | Qld
N_BROKENHSF_FLT_25 | 984865.9201 | 36690.485 | 86.6667 | 3.75 | Limit Broken Hill Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C2K_KBWF_5 | 964903.1892 | 0 | 76.5833 | 0 | Limit to Kaban Wind Farm 1% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>250&270(AVG),Ross_FN>100&120(AVG), 80% limit if NQLD>350&370(AVG),Ross_FN>150&170(AVG)and Haughton syncon ON or at night, Zero otherwise. | Outage | System Strength | Qld
SVML_ZERO | 939801.8649 | 364932.5374 | 208.4167 | 122.25 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | SA
V_BANNERTSF_FLT_20 | 928050.7773 | 0 | 77.8333 | 0 | Limit Bannerton Solar Farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N^N-LS_SVC | 919614.9049 | 9734872.7814 | 3089.8333 | 4482.1667 | Out= Lismore SVC O/S or reactive power control mode,avoid Voltage collapse on TL 87/89 trip;[Swamped for 3 DLK cables are O/S Or when ECS is enabled with DLK is exporting to QLD,sets DLK to -29 MW for -29< DLK FLOW<0, checks ETS status & unswamps if O/S) | Outage | Voltage Stability | NSW
S_ISLE_CRK_10 | 916203.5378 | 2559038.126 | 188.3333 | 282.6667 | Discretionary upper limit on Cathedral Rocks windfarm<=10 MW when 2-4 syn cons I/S for SA is at risk of islanding or in islanded mode(Note: this equation is swamped when 0-1 sync cons are I/S) | Outage | Discretionary | SA
N>>YSTX_TX_051 | 910845.8983 | 0 | 69.1667 | 0 | Out= One Yass 330/132kV TX, avoid O/L of other Yass 132/330kV TX on trip of Wagga to Lower Tumut (051) line, Feedback | Outage | Thermal | NSW
N_LIMOSF2_FLT_15 | 906222.1046 | 58989.5863 | 95.1667 | 5.6667 | Limit Limondale 2 solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_WEMENSF_FLT_20 | 894535.2351 | 0 | 75.0833 | 0 | Limit Wemen Solar Farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_DARLSF_FLT_110 | 885896.2302 | 0 | 79.25 | 0 | Limit Darlington Pt Solar Farm upper limit to 110 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V::S_SETB_TBSE_2 | 861074.867 | 141628.2613 | 139.8333 | 71 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Transient Stability | SA
S>>PARB_RBTU_WTTP | 854042.1283 | 139135.795 | 81.9167 | 19.6667 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V_KIATA_ISL_0 | 828697.7917 | 2178.7221 | 161.1667 | 1.5833 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
N_BROKENHSF_FLT_30 | 801046.7064 | 75507.2385 | 68.1667 | 6.6667 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_CWWF_ISL_0 | 794703.9524 | 0 | 113.4167 | 0 | Crowlands Wind Farm total upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
N_LIMOSF1_FLT_85 | 786741.6868 | 0 | 79.8333 | 0 | Limit Limondale 1 solar farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>>NIL_964_84_S | 774024.1303 | 0 | 807.1667 | 0 | Out= NIL, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Liddell (84) line, Feedback | NIL | Thermal | NSW
S>>RBTU_TWPA_TPRS | 771095.3039 | 5011.8949 | 45 | 0.5 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
N>NIL_9ML | 756776.9064 | 743027.2661 | 77.6667 | 77.75 | Out= Nil, avoid O/L Crudine Ridge to Ilford Tee (9ML) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
N::N_NIL_63 | 730216.3007 | 813205.1765 | 95.4167 | 72.3333 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
V_MURRAWRWF_FLT_60 | 729136.5273 | 0 | 59.4167 | 0 | Limit Murra Warra Wind Farm 1+2 upper limit to 60 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N_LIMOSF1_FLT_50 | 727059.3079 | 7703.337 | 93.0833 | 1.9167 | Limit Limondale 1 solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>>NIL_998 | 681432.4868 | 19405.0895 | 22.6667 | 0.83333 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL | Thermal | NSW
NSA_Q_BARCALDN | 670073.1765 | 240726.0924 | 53.25 | 21.8333 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Network Support | Qld
S_DVRB2_270 | 661065.7448 | 32619.3256 | 60.6667 | 8.75 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
N_DARLSF_FLT_65 | 654926.0308 | 0 | 56.25 | 0 | Limit Darlington Pt Solar Farm upper limit to 65 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_GANWRSF_FLT_15 | 652269.9284 | 0 | 55.25 | 0 | Limit Gannawarra solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_T+LREG_0050 | 649417.1319 | 371377.5311 | 6307.9167 | 1221.5833 | Tasmania Lower Regulation Requirement greater than 50 MW | NIL | FCAS | FCAS
V_MURRAWRWF_FLT_15 | 647366.7184 | 48616.0861 | 57.5 | 3.6667 | Limit Murra Warra Wind Farm 1+2 upper limit to 15 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
V_CWWF_FLT_0 | 637286.5279 | 51899.265 | 178.9167 | 8.75 | Limit Crowlands Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_FINLYSF_FLT_55 | 627648.9763 | 0 | 65.8333 | 0 | Limit Finley solar farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>>NIL_WBBA_RCWEKG | 598843.2936 | 1733953.7546 | 122.8333 | 116.9167 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
N>X-968+96M_969_NIL | 597739.5517 | 0 | 77.3333 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line and 96M(Narrabri to Moree), avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | Outage | Thermal | NSW
SVML^NIL_MH-CAP_ON | 593332.7074 | 1411370.3552 | 520.6667 | 451.6667 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL | Voltage Stability | SA
N::N_DTKV_2 | 590412.8361 | 0 | 83.5 | 0 | Out = Dapto - Kangaroo Valley (18) 330kV line, transient stability limit (Snowy-NSW) for loss of one 330kV line between Yass and Bannaby/Marulan with summated flow on 4+5+61 <=1500 | Outage | Transient Stability | NSW
V_ARARATWF_FLT_60 | 585899.9183 | 0 | 48.1667 | 0 | Limit Ararat Wind Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_GOONSF1_ZERO | 583349.2727 | 3633.1848 | 144.5 | 0.75 | Goonumbla solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
T::T_NIL_1 | 578313.2849 | 354819.5665 | 1649.9167 | 283.3333 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Swamp if less than 3 synchronous West Coast units generating or Farrell 220kV bus coupler open or Hampshire 110kV line is closed. | NIL | Transient Stability | Tas
S>SE6161_SETX2_SGBL | 567427.7623 | 0 | 55.5833 | 0 | Out= South East 132kV CB6161, avoid O/L Snuggery-Blanche 132kV line on trip of South East 132/275 TX2 ( this offloads Mayura-South East T 132kV line), Feedback | Outage | Thermal | SA
N>NIL_999 | 566129.968 | 0 | 10.8333 | 0 | Out= Nil, avoid O/L Bango999 to Cowra (999) on trip of Nil, Feedback | NIL | Thermal | NSW
N_FINLYSF_FLT_40 | 559692.6031 | 0 | 68.8333 | 0 | Limit Finley solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_SUNRSF_FLT_80 | 554767.4433 | 0 | 82.1667 | 0 | Limit Sunraysia solar farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>MPWW_94T_71 | 547860.7729 | 0 | 9.25 | 0 | Out = Mt. Piper to Wallerawang (70 or 71), avoid O/L Molong to Orange North (94T) on trip of the remaining Mt Piper to Wallerawang (71 or 70), [Note: Line 94E O/S as per OM521] | Outage | Thermal | NSW
F_T_AUFLS2_R6 | 542552.5103 | 2047387.7805 | 3634.8333 | 4364.5 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL | FCAS | FCAS
Q_KEP-HYB_25MW | 538709.4065 | 1878958.6907 | 268.1667 | 639.5 | Kennedy Energy Park upper limit of 25MW | Outage | Discretionary | Qld
S>>BWMP_TWPA_TPRS | 537709.0922 | 1498032.2632 | 39.4167 | 80.75 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
V_YATPSF_FLT_20 | 519716.3526 | 72031.6833 | 77.5 | 7.5833 | Limit Yatpool solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_TASCAP_RREG_0220 | 514628.3122 | 1200834.3232 | 4829.5 | 1136.0833 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS | FCAS
N_LIMOSF2_FLT_10 | 513934.4377 | 0 | 69 | 0 | Limit Limondale 2 solar farm upper limit to 10 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_KARADSF_FLT_20 | 505760.0384 | 79086.7383 | 76.0833 | 8.0833 | Limit Karadoc solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S_ISLE_CANUNDA_35 | 501489.9105 | 1121219.3878 | 37.5833 | 82.6667 | Discretionary upper limit on Canunda windfarm<=35MW & No. in-service wind turbines for canunda at 23 Turbines.(Note otherwise,Canunda will be constrained to 0 MW) | Outage | Discretionary | SA
S>>PARB_RBTU_WEWT | 485852.6156 | 236242.3323 | 76.9167 | 31.5 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_I+NIL_MG_R1 | 474051.1237 | 0 | 1963.4167 | 0 | Out = Nil, Raise 1 sec requirement for a NEM Generation Event. Requirement capped at 225 MW | Outage | FCAS | FCAS
V>NIL_WETX_NIL | 469875.1761 | 1376385.5742 | 79.5833 | 227.25 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback | NIL | Thermal | Vic
T_MRWF_GCS | 461193.5474 | 188324.3442 | 237.25 | 113.8333 | Musselroe wind farm Generator Control Scheme (GCS) constraint to maintain TAS FOS for a Tasmania generator event. Limit Musselroe wind farm based on load available/armed by Musselroe GCS | NIL | Other | Tas
F_I+BIP_ML_L1 | 449693.6434 | 0 | 1182.75 | 0 | Out = Nil, Lower 1 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. Requirement capped at 125 MW | Outage | FCAS | FCAS
N>N-NIL_JUTX_LV | 446880.0269 | 510099.6191 | 77.1667 | 82.8333 | Out= Nil, avoid O/L Junee#3 132/66kV transformer on trip of Nil, Feedback. 90% of Rating is used as operating margin. | NIL | Thermal | NSW
F_MAIN++RREG_0220 | 438638.1467 | 410905.233 | 1672.9167 | 410.3333 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
Q>>BCRG_CLWU_BCCP | 436669.6652 | 149239.8659 | 87.75 | 35 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
V^^N_NIL_1 | 435325.2953 | 8400019.2769 | 585 | 391.3333 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Voltage Stability | Vic
Q_MARYRSF1_RB | 428907.065 | 567950.5452 | 112.75 | 160.4167 | Maryrorough Run Back limit | NIL | Discretionary | Qld
V_KARADSF_FLT_25 | 428345.0785 | 512506.7375 | 95.0833 | 49.5833 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_SUNRSF_FLT_60 | 427304.4252 | 68516.1838 | 89.5 | 7.1667 | Limit Sunraysia solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_SILVERTWF_FLT_80 | 416266.6118 | 0 | 33.3333 | 0 | Limit Silverton Wind Farm upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
V:S_600_HY_TEST_DYN | 414784.4403 | 128697.9323 | 158.9167 | 56.75 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Oscillatory Stability | Vic
V_YATPSF_FLT_25 | 410097.002 | 269303.2174 | 130.4167 | 43 | Limit Yatpool solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
NSA_Q_GSTONE34_xxx | 406658.5288 | 251406.1617 | 136 | 98.4167 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Network Support | Qld
F_T+NIL_MG_RECL_R6 | 403355.45 | 881653.5083 | 306.0833 | 1823.5833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V_KIAMAL_ISL_0 | 398121.5799 | 0 | 32.75 | 0 | Kiamal Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V^^SML_NIL_3 | 379996.3493 | 7.6323 | 42.9167 | 0.083333 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Voltage Stability | Vic
V^SML_BUDP_3 | 376314.9789 | 79175.3113 | 153.4167 | 16.9167 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
Q_YARANSF1_RB | 372417.4805 | 1620208.8384 | 136.75 | 206.0833 | Yarrranlea Run Back limit | NIL | Discretionary | Qld
S>>NIL_TWPA_TPRS | 352652.3871 | 700728.5406 | 64.25 | 51.4167 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
F_I+NIL_MG_R6 | 349071.1094 | 461188.3814 | 6739.0833 | 5403.0833 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL | FCAS | FCAS
S_ISLE_LKB1+2+3_60 | 342218.0772 | 721934.7551 | 104.4167 | 166.75 | Discretionary upper limit on Lake Bonney (1+2+3) windfarms<=60 MW & No. in-service wind turbines for LKB at 41 Turbines.(Note otherwise, LKB 2+3 +1 will be constrained to 0 MW) | Outage | Discretionary | SA
N>9U2_969_NIL | 341908.8631 | 0 | 29.6667 | 0 | Out= 9U2 (Moree to Inverell ) 132kV line, avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | Outage | Thermal | NSW
V_ARARATWF_ISL_0 | 341702.1504 | 0 | 25.3333 | 0 | Limit Ararat Wind Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
S>>RBTU_RBPA_WTTP | 329785.6227 | 5360.3061 | 67.3333 | 2.3333 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
N>>NIL_33_34 | 324979.8931 | 0 | 75.4167 | 0 | Out= Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL | Thermal | NSW
V>>NIL_ARWB_RCWEKG | 316894.7797 | 512784.504 | 100.0833 | 83.9167 | Out = Nil, avoid O/L Ararat to Waubra 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
N_SILVERTWF_FLT_50 | 313905.0287 | 0 | 26.1667 | 0 | Limit Silverton Wind Farm upper limit to 50 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
N_WRWSF_055 | 311177.0167 | 392056.079 | 25.0833 | 27 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | System Strength | NSW
V_MURRAWRWF_FLT_80 | 310750.0492 | 102706.1809 | 25.9167 | 8.75 | Limit Murra Warra Wind Farm 1+2 upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
VS_050_DYN | 309521.1361 | 365612.1454 | 63.6667 | 28.25 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
F_MAIN++NIL_MG_R6 | 305900.3809 | 253487.8496 | 1811.9167 | 1508.5 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
N_LIMOSF11_ZERO | 299308.7031 | 112.0561 | 37.4167 | 0.083333 | Limondale 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N>NIL_901 | 291034.4569 | 0 | 53.1667 | 0 | Out= Nil, avoid O/L West Wyalong to Temora 132kV (901) line on trip of Nil, Feedback | NIL | Thermal | NSW
N_WRWSF_066 | 278845.0878 | 0 | 21.5 | 0 | White Rock wind farm and White Rock solar farm upper limit of 66 MW | Outage | System Strength | NSW
N>947+949_94T | 264430.9931 | 0 | 5.9167 | 0 | Out= Wellington to Orange North (947) 132kV line + Orange North to Mt Piper (949) 132kV line, avoid O/L Molong to Orange North (94T) 132kV line, Feedback | Outage | Thermal | NSW
N>NIL_99U | 251869.8397 | 31438.7548 | 31.3333 | 3.0833 | Out= Nil avoid O/L Sebastopol to Wagga North (99U) 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
S>>RBTX_WEWT_RBTX | 247640.9917 | 547578.0521 | 45.1667 | 90.6667 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage | Thermal | SA
N_LIMOSF21_ZERO | 245913.9589 | 0 | 37.8333 | 0 | Limondale 2 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_BANSF_BBD_S2 | 244026.8883 | 0 | 31.4167 | 0 | Out = Nil, Bannerton SF limitation segment 2 if Boundary Bend (BBD) loading is between 5 and 10 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
V_BANNERTSF_FLT_25 | 242147.4977 | 59219.6966 | 20.4167 | 6.0833 | Limit Bannerton Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_MAIN+NIL_DYN_RREG | 242071.672 | 4618602.7018 | 558.8333 | 586.1667 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL | FCAS | FCAS
Q>>LCCP_CLWU_BCCP | 241735.775 | 0 | 25.9167 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
Q_OKYTX4 | 237587.8639 | 69775.6794 | 36.4167 | 5.75 | Out = Oakey 4T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 71MW | Outage | Thermal | Qld
N_DARLSF_FLT_85 | 235608.4061 | 91329.6233 | 19.75 | 7.5833 | Limit Darlington Pt Solar Farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_WEMENSF_FLT_25 | 234750.9194 | 18272.3403 | 19.8333 | 3.0833 | Limit Wemen Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_MAIN++LREG_0210 | 234553.5627 | 86946.8891 | 2171.5833 | 643.4167 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
V>>NIL_BABE_HOMRKM | 232325.8049 | 0 | 112.1667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
S>>X_RBTU+RBTX_13 | 231620.7529 | 189750.9758 | 33.4167 | 25 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Waterloo-Templers 132kV line on trip of remaining Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_I+NIL_APD_TL_L60 | 226377.1805 | 86625.8596 | 7510.6667 | 5513.0833 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
V>>NIL_WEKG_HOBUCW | 225906.0343 | 280706.4896 | 20.0833 | 24.8333 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
V_BANSF_BBD_S3 | 225544.8383 | 0 | 39.6667 | 0 | Out = Nil, Bannerton SF limitation segment 3 if Boundary Bend (BBD) loading is between 10 and 20 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
V_GANWRSF_FLT_25 | 215888.7497 | 21376.3361 | 18.0833 | 2.25 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_TASCAP_LREG_0210 | 215373.8812 | 147739.531 | 3708.8333 | 1158.9167 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS | FCAS
S>MKRB_BWMP_HUWT | 212697.0037 | 182158.6319 | 24.0833 | 18.25 | Out= Mokota-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_MAIN++NIL_MG_R60 | 207518.5335 | 102506.1056 | 2054.3333 | 1716.4167 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
N_WAGGNSF1_ZERO | 206152.4729 | 2572.4802 | 19.5833 | 0.25 | Wagga North solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_T_NIL_FCSPS | 206044.6323 | 114993.6352 | 411.3333 | 208.25 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Other | Vic
N>NIL_94T_947 | 204223.1181 | 709152.5455 | 26.1667 | 94.5833 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947) line, Feedback | NIL | Thermal | NSW
S>>RBTU_N-2_WTTP | 204023.9305 | 0 | 50.75 | 0 | Out= Nil, avoid O/L Waterloo to Templers 132kV line on trip of Robertstown - Tungkillo 275kV line 1 and 2, Feedback | Outage | Thermal | SA
V^^N_LTUT_1 | 203951.1685 | 0 | 265.5833 | 0 | Out = Lower to Upper Tumut (64) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N>94K2_94K1_NIL | 202661.1487 | 0 | 28.0833 | 0 | Out= Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only), avoid O/L on Suntop to Wellington (94K/1) on trip of Nil, Feedback | Outage | Thermal | NSW
V>>NIL_WBBA_RCBSS | 200185.0426 | 0 | 27.6667 | 0 | Out= NIL, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Buronga (0X1) 220kV line, Feedback | NIL | Thermal | Vic
Q_STR_7C2K_COLSF_5 | 199677.3698 | 12068.6169 | 15.0833 | 1 | No limit to Collinsville Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG) (80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_DAYSF_5 | 199515.2375 | 2961.4836 | 15.0833 | 0.25 | No limit to Daydream Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
S>>MKRB_TWPA_TPRS | 195879.94 | 657137.8116 | 17.25 | 50.5 | Out= Mokota-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
F_I+RREG_0220 | 195188.5509 | 1694191.5039 | 1950.4167 | 6612.1667 | NEM Raise Regulation Requirement greater than 200 MW | NIL | FCAS | FCAS
S>>X_RBTU+RBTX_10 | 194857.6951 | 338640.7343 | 10.9167 | 20.6667 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Templers- Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
N_FINLYSF_FLT_30 | 189859.2472 | 2300.8687 | 20.75 | 0.66667 | Limit Finley solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N::N_UTRV_2 | 188039.9475 | 662653.4244 | 42.75 | 288.9167 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
N>947_94T | 187248.7742 | 0 | 7.5833 | 0 | Out= Wellington to Orange North (947) 132kV line, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
VSML_110 | 180669.7208 | 1047.7027 | 10.5833 | 1.6667 | Vic to SA on ML upper transfer limit of 110 MW | Outage | Discretionary | Vic
Q_STR_7C0K_KBWF_1 | 179967.2755 | 0 | 13.8333 | 0 | Limit 40% to Kaban WF if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar>=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Syncon ON, 1% if Kar<0,100% at night),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_RUGSF_7 | 178056.6046 | 232016.062 | 15 | 18.4167 | Limit to Rugby Run Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V:S_600_HY_TEST | 177314.0438 | 147813.2456 | 174.5833 | 65.6667 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
Q_STR_7C2K_HAMSF_5 | 175105.4367 | 1045.4952 | 13.0833 | 0.25 | No limit to Hamilton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
N_LIMOSF1_FLT_60 | 174310.9336 | 84298.3186 | 19.6667 | 8.0833 | Limit Limondale 1 solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>NIL_9R4_99A | 173462.9407 | 0 | 50.4167 | 0 | Out= Nil, avoid O/L Finley to Mulwala 132kV line (9R4) on trip of Finley to Uranquinty (99A) line, Feedback | NIL | Thermal | NSW
S>>RBTU_N-2_WEWT | 172221.2519 | 0 | 50.4167 | 0 | Out= Nil, avoid O/L Waterloo East to Waterloo #1 132kV line on trip of Robertstown - Tungkillo 275kV line 1 and 2, Feedback | Outage | Thermal | SA
Q_STR_7C2K_HAYSF_5 | 171318.2942 | 46.4201 | 12.5833 | 0.16667 | No limit to Hayman Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
F_I+LREG_0210 | 170345.7787 | 790181.2563 | 2326.0833 | 6842 | NEM Lower Regulation Requirement greater than 210 MW | NIL | FCAS | FCAS
N^^Q_LS_SVC_KPP_1 | 166992.1847 | 743.6296 | 125.0833 | 1.1667 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage Collapse on loss of Kogan Creek MW | Outage | Voltage Stability | NSW
Q_STR_7C8C_MEWF | 163653.7429 | 0 | 57.75 | 0 | Limit Mt Emerald Wind Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
N>NIL_9GL | 159934.1328 | 10711.9335 | 16.5833 | 1.0833 | Out= Nil, avoid O/L Bango973 to Yass (9GL) on trip of Nil, (Note: Swamped when 999 is O/S) | NIL | Thermal | NSW
S>>X_CNRB+RBTX_22 | 158408.7851 | 0 | 18 | 0 | Out= One Robertstown TX + Canowie-Robertstown 275kV line O/S, avoid O/L Templers-Roseworthy 275kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S>DVTX_NIL_DVTX | 156223.6267 | 861796.0803 | 13.6667 | 74.0833 | Out= One Davenport 275/132kV TX O/S, avoid O/L of remaining Davenport 132/275kV TX on NIL trip. | Outage | Thermal | SA
S-CRK_0 | 153565.8937 | 42560.4808 | 34.5 | 5.0833 | Discretionary upper limit for Cathedral Rocks windfarm generation of 0 MW | Outage | Unit Zero | SA
VSML_ROC_80 | 150574.3078 | 266839.6873 | 79.5 | 73.3333 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | Vic
V::N_NIL_xxx | 148210.3539 | 4899.8779 | 321.25 | 23.8333 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL | Transient Stability | Vic
Q>NIL_MRTX_MRTX_N-2 | 148181.0058 | 0 | 0.83333 | 0 | Out= Nil, avoid O/L Middle Ridge 275/110kV (1T) transformer on trip of remaining Middle Ridge 275/110kV (2T and 3T) transformers, Feedback | Outage | Thermal | Qld
S>S_WERB_TWPA_TPRS | 146573.1134 | 0 | 13.4167 | 0 | Out= Robertstown - MWP4 - Waterloo East O/S(offloads MWP4 SF), avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
V>NIL_WBBA_KMRC | 145305.7891 | 0 | 26.6667 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
N_COLEASF1_FLT_30 | 145007.6584 | 3537.0395 | 11.0833 | 0.25 | Limit Coleambally solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_HAYMSF1_ZERO | 144838.3353 | 0 | 11.3333 | 0 | Hayman solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_MAIN++APD_TL_L5 | 144497.8039 | 55100.7334 | 3083.8333 | 1846.0833 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
V_BULGANAWF_FLT_40 | 143909.0139 | 3462.5162 | 11.9167 | 0.58333 | Limit Bulgana Wind Farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q>NIL_DRLCLB_NIL | 143383.3447 | 0 | 10.4167 | 0 | Out= Nil, avoid OL on 7490 or 7491 (T280 Drillham to T194 Columboola) 132kV feeder, NIL trip. Feedback | NIL | Thermal | Qld
N_FINLYSF_FLT_50 | 142956.0178 | 91831.2836 | 15.6667 | 10.0833 | Limit Finley solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>>NIL_ELML_BAML2 | 138556.1875 | 8744.1549 | 219.0833 | 26.9167 | Out= Nil, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | NIL | Thermal | Vic
S>>X_RBTU+RBTX_15 | 138504.6439 | 508923.2001 | 24.4167 | 61.25 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>NIL_BWMP_RHBR-T | 138366.1023 | 63115.6778 | 22.8333 | 10.5833 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
N-DBWL_94J | 137660.503 | 0 | 13.9167 | 0 | Out = Dubbo132 to Wellington (94J) 132 kV line, Upper limit of 80 on Nevertire SF, EE advice on 13/02/2020 | Outage | Other | NSW
Q_STR_7C2K_SMSF_7 | 135343.68 | 161939.0617 | 12.0833 | 13.1667 | Limit to Sun Metals Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N>94K2_94T_947 | 134658.425 | 0 | 22.6667 | 0 | Out= Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only), avoid O/L on Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | Outage | Thermal | NSW
Q_STR_7C2K_HASF_8 | 132755.5536 | 0 | 9.75 | 0 | No limit to Haughton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
Q_NIL_STRGTH_KBWF | 129979.0352 | 28211.532 | 10.25 | 2.25 | Out = Nil, limit Kaban Wind farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N_COLEASF1_FLT_45 | 129778.3093 | 63246.6853 | 10.8333 | 5.3333 | Limit Coleambally solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_YATPSF_FLT_40 | 129204.2125 | 0 | 30.5833 | 0 | Limit Yatpool solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_MC_SH_WF_600 | 127348.6762 | 118394.8484 | 10.6667 | 13 | Limit the total MW from Macarthur and Stockyard Hill WF <= 600 MW to maintain generation contingency size in Victoria. | Outage | Discretionary | Vic
N>NIL_LSDU | 126566.5463 | 88439.2571 | 151.3333 | 172.25 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
N>NIL_COTX_LV | 125153.7094 | 122594.3743 | 30.5 | 20.1667 | Out= Nil, avoid O/L either Corowa 22kV/132kV Transformer on NIL trip, Feedback. NOTE: System normal is only one transformer in service. 90% of Rating and no operating margin is used as per Essential Energy advice. | NIL | Thermal | NSW
S_BRBG_CMWF_0 | 125133.5155 | 0 | 9.9167 | 0 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | Unit Zero | SA
N_LIMOSF2_FLT_25 | 124876.5432 | 0 | 13.9167 | 0 | Limit Limondale 2 solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C0K_HASF | 122768.3737 | 68914.348 | 10.0833 | 5.0833 | No limit to Haughton Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
F_I+NIL_MG_R60 | 122004.7742 | 164578.8962 | 5798.4167 | 4661.75 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL | FCAS | FCAS
F_MAIN++APD_TL_L60 | 120442.2664 | 239439.2039 | 1303.9167 | 1621.3333 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
T_GRANVH_ZERO | 120170.3583 | 0 | 9.6667 | 0 | Granville Harbour wind farm upper limit of 0 MW | Outage | Unit Zero | Tas
Q_STR_7C2K_DAYSF_7 | 119147.72 | 208450.9146 | 9.9167 | 16.6667 | Limit to Daydream Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
NRM_QLD1_NSW1 | 117739.5623 | 1635408.6589 | 12.0833 | 26.0833 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue | Negative Residue
V^^SML_ARWBBA_1 | 116876.6933 | 0 | 17.75 | 0 | Out = Ballarat to Waubra to Ararat 220kV line (or any line section between Ballarat and Ararat), avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
Q-X>RS2TX_TX_TX_O | 116872.4398 | 0 | 1.5 | 0 | Out= Two Ross 275/132 KV transformers, avoid O/L on the remaining Ross 275/132 KV transformer on trip of another Ross 275/132 KV transformer with 132 KV network between Ross and Woree Opened, Feedback | Outage | Thermal | Qld
S>NIL_SGBN_SGSE-T2 | 116853.7265 | 0 | 19.5833 | 0 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | Thermal | SA
V_SHWF_FLT_286 | 115890.4604 | 2203761.9166 | 82.6667 | 102.75 | Limit Stockyard Hill wind farm to 286 MW if Heywood flow is above 470 MW (SA to VIC direction). Swamp otherwise. This is to manage voltage oscillation. | NIL | System Strength | Vic
N_SILVERTWF_FLT_100 | 113958.9944 | 14563.132 | 9.6667 | 1.25 | Limit Silverton Wind Farm upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
Q_STR_7C2K_COLSF_7 | 111456.2127 | 195996.1583 | 9.5 | 15.9167 | Limit to Collinsville Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_KIATAWF_FLT_15 | 110870.7777 | 64553.1044 | 18.5833 | 8.5833 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V_MACARTHUR_ZERO | 109752.5405 | 0 | 8.5 | 0 | Macarthur upper limit of 0 MW | Outage | Unit Zero | Vic
Q_STR_7C2K_MEWF_5 | 107911.6628 | 3209664.1414 | 29 | 56.3333 | Limit Mt Emerald Windfarm to 80% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),(100% at night),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise Zero otherwise. | Outage | System Strength | Qld
Q>CMTX | 107333.6438 | 0 | 138.75 | 0 | Out = Clermont T1 or T2 132/66 kV transformer, limit to Clermont Solar Farm to 30MW to prevent overload on remaining transformer | Outage | Thermal | Qld
V^^N_DTKV_1 | 106445.1012 | 665976.4529 | 121.25 | 136 | Out = Dapto - Kangaroo Valley (18) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_STR_7C2K_SMSF_5 | 104945.2259 | 6024.0939 | 7.4167 | 0.5 | No limit to Sun Metals Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
N_DARLSF1_ZERO | 104454.3198 | 0 | 8.5 | 0 | Darlington Point solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
F_T+NIL_ML_L60 | 103656.6479 | 292119.2564 | 1105.1667 | 4297.8333 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N>NIL_997/2_99A | 103509.7311 | 0 | 32.0833 | 0 | Out= NIL, avoid O/L Mulwala to Corowa (996/2) 132kV line on trip of Finley to Uranquinty (99A) 132kV line, Feedback | NIL | Thermal | NSW
V_BANSF_BBD_60 | 102378.7911 | 2342852.9689 | 17.4167 | 386 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Discretionary | Vic
S>NIL_BWMP_HUWT | 102338.3158 | 90322.4253 | 13.0833 | 10.1667 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
S>>RBTX1_RBTX2_WEWT | 102091.5546 | 0 | 15.4167 | 0 | Out= one Robertstown 275/132kV TX, avoid O/L Waterloo East-Waterloo 132kV line on trip of remaining Robertstown 132/275kV TX, Feedback | Outage | Thermal | SA
S>>RBTU_RBPA_WEWT | 101733.4251 | 32579.5354 | 22.4167 | 16.25 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
T_GRANVH_060 | 99236.111 | 0 | 8.4167 | 0 | Discretionary 60 MW upper limit on Granville Harbour Wind Farm | Outage | Discretionary | Tas
N>NIL_9GM | 98687.6682 | 0 | 14.3333 | 0 | Out= Nil, avoid O/L Bango999 to Yass (9GM) on trip of Nil, Feedback | NIL | Thermal | NSW
N_FINLYSF_FLT_45 | 98603.9484 | 77511.6733 | 15.5833 | 7.3333 | Limit Finley solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>94K2_94T_998 | 97403.8687 | 0 | 44.4167 | 0 | Out= Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only), avoid O/L Molong to Orange North (94T) on trip of Forbes to Cowra (998) line, Feedback | Outage | Thermal | NSW
N>>DP_TIETX_D | 96372.3936 | 0 | 21.75 | 0 | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (220 KV to 330 kV) on Kerang-Bendigo trip; Feedback | Outage | Thermal | NSW
S>>PA6509_BWPA_WTTP | 95423.9332 | 0 | 17.6667 | 0 | Out= Para 275kV CB6509, avoid O/L Waterloo-Templers 132kV line on trip of Munno Para-Para 275kV line (this offloads Tungkillo-Para 275kV line 2 & Blyth West-Munno Para 275kV line & Munno Para TX), Feedback | Outage | Thermal | SA
Q_STR_7C8C_RUGSF | 95284.2381 | 47294.0705 | 8 | 3.6667 | Limit Rugby Run Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
Q>NIL_EMBW_EMLV_DS | 94432.2067 | 604363.095 | 110.5833 | 141.1667 | Out= Nil, limit Emerald SF to 40MW to avoid overload on Emerald - Lilyvale 66kV line on trip of Emerald - Comet - Blackwater 66kV line (6056 or 6011), swamp if Emerald CBs S612,S610 and Blackwater CB S605 are closed (DS only) | NIL | Thermal | Qld
N_SUNRSF_FLT_50 | 94053.3169 | 8182.968 | 21 | 1.1667 | Limit Sunraysia solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V^^V_NIL_SWVIC | 93906.1904 | 31655.7743 | 192.5833 | 20.5833 | Out = Nil, manage flow towards Moorabool across Haunted Gully to Moorabool and Mortlake to Moorabool 500kV lines to avoid voltage instability for the loss of Haunted Gully to Moorabool 500kV line and both APD potlines | NIL | Voltage Stability | Vic
SVML_FLT_125 | 93864.8913 | 5.9665 | 26.6667 | 0.16667 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
VS_050 | 93339.7925 | 0 | 26.6667 | 0 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Discretionary | Vic
S:V_PA_SVC_470 | 92835.1269 | 161713.4855 | 199.0833 | 219.25 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 470 MW | Outage | Oscillatory Stability | SA
N>N-BEBO-94B-1 | 92798.5913 | 0 | 9.3333 | 0 | Out= Beryl to Bodangora WF 132kV line (94B/2), avoid O/L Crudine Ridge WF to Ilford Tee (9ML/1) on trip of Nil, Feedback | Outage | Thermal | NSW
F_MAIN+RREG_0220 | 92699.8552 | 2059983.0486 | 416.0833 | 1138.9167 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V::S_NIL_MAXG_xxx | 92210.6399 | 243644.3163 | 34.75 | 57.25 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Transient Stability | SA
S^^V_SETB_1 | 91587.5478 | 24512.9911 | 85.25 | 8.75 | Out= one South East to Tailem Bend 275kV line, voltage collapse equation Tailem Bend-Keith #2 132kV Line <=135 MW on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage | Thermal | SA
N>72_94T_79 | 91568.9324 | 0 | 6.75 | 0 | Out = Mt Piper to Wellington line (72), avoid O/L on Molong to Orange North (94T) on trip of Wellington to Wollar West (79), Feedback | Outage | Thermal | NSW
N::Q_8C8J_KC_N-2 | 91477.4807 | 0 | 58 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | NSW
N>>17_39_11 | 89539.2646 | 0 | 13.5833 | 0 | Out = Avon-Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage | Thermal | NSW
Q_STR_7C2K_HAYSF_7 | 89026.5115 | 250232.8127 | 8 | 20.5833 | Limit to Hayman Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_COLSF | 88239.2917 | 14986.0178 | 7.4167 | 1.1667 | Limit Collinsville Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
Q_STR_7C8C_DAYSF | 87367.7379 | 13821.8458 | 7.3333 | 1.0833 | Limit Daydream Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
N>>NIL_4 | 86989.4388 | 816.0391 | 7.5833 | 0.5 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL | Thermal | NSW
S_WP_ISL | 86105.0503 | 5507.7667 | 7.0833 | 0.41667 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Wattle Pt WF islanded | Outage | Islanding - Unit | SA
N_BOMENSF1_ZERO | 85904.9123 | 0 | 39.9167 | 0 | Bomen SF upper limit of 0 MW | Outage | Unit Zero | NSW
Q_KEP-HYB_38MW | 85022.2909 | 0 | 68 | 0 | Kennedy Energy Park upper limit of 38MW | Outage | Discretionary | Qld
V_KARADSF_FLT_45 | 84489.4149 | 0 | 20.5833 | 0 | Limit Karadoc solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_OKYTX3 | 83903.8941 | 19257.1393 | 10.8333 | 1.8333 | Out = Oakey 3T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 67.3MW | Outage | Thermal | Qld
S_DVRB_270 | 83338.0471 | 842314.2141 | 18.25 | 99 | Out = DV-BL 275kV line Or MK-RB 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF + Hallet Hill WF (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
N_STWF1_ZERO | 83143.3403 | 269416.4575 | 5.9167 | 21 | Silverton wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_CWWF_FLT_55 | 82309.3937 | 55118.4368 | 12.1667 | 7.8333 | Limit Crowlands Wind Farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_DARLSF_FLT_80 | 79554.3637 | 0 | 9.8333 | 0 | Limit Darlington Pt Solar Farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C2K_HAMSF_7 | 79474.8518 | 184562.6717 | 9.75 | 15.1667 | Limit to Hamilton Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N_NYNGANSF_010 | 79265.8691 | 0 | 7.0833 | 0 | Nyngan Solar Farm upper limit of 10 MW | Outage | Discretionary | NSW
T_WCOAST_220G_144 | 79132.7124 | 0 | 7.5 | 0 | Total generation of Bastyan, Granville Harbour, John Butters, Tribute, Reece 1 and 2 limited to <= 144 MW | Outage | Discretionary | Tas
Q_STR_7C2K_RRSF_5 | 78919.1998 | 201.4719 | 14.9167 | 0.25 | No limit to Ross River Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
F_T+NIL_WF_TG_R6 | 78801.2754 | 401393.4027 | 116.9167 | 1046.25 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T++RREG_0050 | 78798.9684 | 113321.071 | 689.3333 | 531 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
N_BDKV | 77500 | 0 | 0.41667 | 0 | Out= Bendeela - Kangaroo Valley (19) line | Outage | Unit Zero | NSW
N>NIL_99F | 76017.4332 | 0 | 15.3333 | 0 | Out= Nil, avoid O/L Narrandera to Uranquinty (99F) 132 kV line on trip of Nil, Feedback | NIL | Thermal | NSW
Q_KEP-HYB_ZERO | 75953.2329 | 999753.8061 | 25.1667 | 234.8333 | Kennedy Energy Park upper limit of 0MW | Outage | Unit Zero | Qld
Q_DAYDSF1_ZERO | 75672.7543 | 0 | 5.8333 | 0 | Daydream solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_WARMR_736_SF2 | 75444.9969 | 0 | 9.6667 | 0 | Out= Warwick to Middle Ridge 110kV feeder (736), limit Warwick SF2 to 20MW as per Ergon ramp down scheme | Outage | Thermal | Qld
S>>X_RBTX+MNWT_24 | 73473.9012 | 0 | 9.6667 | 0 | Out= One Robertstown 275/132 kV TX + Mintaro-Waterloo 132 kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX2 on trip of Waterloo East-Waterloo 132 kV line, Feedback | Outage | Thermal | SA
F_T+NIL_ML_L6 | 73454.9943 | 377504.2254 | 1071.9167 | 4584.3333 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
SV_470_DYN | 73074.6967 | 130505.2364 | 118.1667 | 132.75 | SA to Victoria on Heywood upper transfer limit of 470 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 50 MW | Outage | Discretionary | SA
S>>NIL_RBTU_RBTU | 72496.6359 | 0 | 27.6667 | 0 | Out= NIL, avoid O/L Robertstown-Tungkillo 275kV line 1 or 2 on trip of parallel Robertstown-Tungkillo 275kV line 2 or 1, Feedback | NIL | Thermal | SA
F_MAIN+NIL_DYN_LREG | 71897.7795 | 90648.1452 | 362.3333 | 263.0833 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL | FCAS | FCAS
N>>NIL_5_61_N | 70751.6342 | 0 | 4.5833 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) 330kV line on trip of Crookwell to Bannaby (61) 330kV line, Feedback | NIL | Thermal | NSW
V_MACWF_FLT_0 | 69745.3067 | 275767.7525 | 4.4167 | 24.1667 | Limit Macarthur Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_WARMR_736_SF1 | 68548.9807 | 0 | 8.6667 | 0 | Out= Warwick to Middle Ridge 110kV feeder (736), limit Warwick SF1 to 20MW as per Ergon ramp down scheme | Outage | Thermal | Qld
V_WEMENSF_FLT_53 | 68430.8914 | 21389.6495 | 5.9167 | 3.8333 | Limit Wemen Solar Farm upper limit to 53 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_MAIN+NIL_MG_R6 | 67316.8079 | 2379180.4153 | 421.9167 | 1178.9167 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_I+NIL_APD_TL_L5 | 67087.2054 | 40306.979 | 5761.8333 | 5703.4167 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
S>>NIL_RBTU_WTTP | 66116.3055 | 177038.6958 | 20.3333 | 32.5 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of one Robertstown - Tungkillo 275kV line, Feedback | NIL | Thermal | SA
Q_STR_7C8C_SMSF | 65776.4246 | 0 | 5.5 | 0 | Limit Sun Metals Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
N^^Q_DM_TW_SVC_B1 | 65256.9314 | 0 | 39.8333 | 0 | Out = Dumaresq or Tamworth SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
Q_STR_7C2K_KEP_5 | 64703.3346 | 213.4718 | 26 | 0.25 | No limit to Kennedy Energy Park if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
Q_MARYRSF1_ZERO | 64379.1096 | 0 | 5.0833 | 0 | Maryrorough Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
N_DARLSF_FLT_100 | 64378.8895 | 118283.2168 | 5 | 8.4167 | Limit Darlington Pt Solar Farm upper limit to 100 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>>NIL_84_83_OPEN | 63221.2682 | 15312.1915 | 9.3333 | 6 | Out = Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | Thermal | NSW
V_BANNERTSF_FLT_53 | 63161.1654 | 48501.2152 | 5.5 | 9 | Limit Bannerton Solar Farm upper limit to 53 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S:V_550_HY_TEST_DYN | 62967.5909 | 2681.3269 | 136.1667 | 6.5 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
VSML_020 | 62024.2017 | 0 | 6.6667 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage | Discretionary | Vic
N>9R6_9R5_901 | 61041.1943 | 0 | 4.6667 | 0 | Out= 9R6 (Wagga North to Wagga 132) 132kV line, avoid O/L Wagga North to Wagga (9R5) on trip of Temora to Wyalong 132kV (901) line, Feedback | Outage | Thermal | NSW
Q_STR_7C0K_MEWF_2 | 60776.2753 | 0 | 26 | 0 | Limit 70% to Mt Emerald WF if Stan>=2+Stan+Cal>=3+Glad>=2+(Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% Haughton Syncon ON,100% night), 40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG)(25% if Syncon OFF),Zero otherwise. | Outage | System Strength | Qld
V>>SML_NIL_7B | 60702.4583 | 454.6006 | 3.6667 | 0.16667 | Out = Nil, avoid O/L Buangor to Ararat 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL | Thermal | Vic
N_WRWF1_ZERO | 60125.5918 | 132898.7346 | 5 | 10.1667 | White Rock WF upper limit of 0 MW and all turbines disconnected | Outage | Unit Zero | NSW
S>>RBTX_TWPA_TPRS | 60119.1237 | 154474.5301 | 5.6667 | 24.0833 | Out= one Robertstown 275/132kV transformed, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
Q>NIL_TV66 | 59668.0457 | 491394.0796 | 4 | 10.5833 | Out=Nil, limit Sun metals SF and Mt Stuart GTs to avoid over load on 66kV feeders on trip of one of the 66kV feeders in the Townsville area | NIL | Thermal | Qld
S>>X_RBTU+RBTX_14 | 59629.0784 | 360285.1559 | 10.6667 | 32.75 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of remaining Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
Q_STR_7C0K_HASF_1 | 59172.6755 | 0 | 4.9167 | 0 | No limit to Haughton Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>2_NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N::N_SDUT_2 | 59047.4465 | 27156.4935 | 14.25 | 21.1667 | Out = Upper Tumut-Stockdill (1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
VSML_030 | 58352.4134 | 0 | 17.3333 | 0 | Vic to SA on ML upper transfer limit of 30 MW | Outage | Discretionary | Vic
N_BROKENHSF_FLT_32 | 56982.8582 | 18678.6453 | 5 | 5.4167 | Limit Broken Hill Solar Farm upper limit to 32 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N::N_CNSD_2 | 56200.9113 | 1281.9885 | 13.5 | 2.25 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
S>>X_RBPA+RBTX2_16 | 55861.6666 | 284369.1385 | 10.25 | 28 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo East-Waterloo 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
V^^SML_NSWRB_2 | 54310.1687 | 194297.2169 | 17.25 | 81.75 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Voltage Stability | Vic
F_MAIN+LREG_0210 | 54285.5706 | 203092.5266 | 388.3333 | 1105.9167 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
Q_CHILDSF1_ZERO | 54205.5079 | 12715.4267 | 4.4167 | 1.0833 | Childers Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
V_COHUNASF_FLT_17 | 54181.9229 | 29725.538 | 4.5 | 3.1667 | Limit Cohuna Solar Farm upper limit to 17 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_OAKHILL_TFB_42 | 54157.615 | 0 | 4.5833 | 0 | Out = Nil, Oaklands Hill Windfarm upper limit of 42.7 MW due to Oaklands Hill windfarm TFB mode operation, DS only. Swamp out if TFB mode is OFF | NIL | Discretionary | Vic
N_WRWSF_ZERO | 53806.577 | 231363.6753 | 4.6667 | 12.5 | White Rock wind farm and White Rock solar farm upper limit of zero MW | Outage | Discretionary | NSW
N>999_9GL_NIL | 53614.6277 | 8816.4778 | 6.25 | 1 | Out= Bango999 WF to Cowra 132kV line(999), avoid O/L Bango973 to Yass (9GL) on trip of Nil, Feedback | Outage | Thermal | NSW
V::N_HYSE_xxx | 53443.9677 | 26795.5632 | 55.4167 | 12.4167 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
N_X_MBTE_3A & N_X_MBTE_3B | 52425.8612 | 355582.8566 | 390 | 438.8333 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | Unit Zero | NSW
Q_STR_7C2K_KBWF_13 | 52366.674 | 0 | 4.25 | 0 | Limit 40% to Kaban WF if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG) (100% if Haughton Syncon ON or at night, 1% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>X_RBPA+RBTX2_22 | 52126.5123 | 407146.2718 | 8.9167 | 38.1667 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo-Templers 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
F_I+BIP_ML_L6 | 51228.333 | 15529.5447 | 6008.6667 | 33.3333 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL | FCAS | FCAS
S^NIL_CRK+MTM_95 | 51176.8002 | 7624079.5494 | 35.8333 | 353.6667 | Out= Nil, upper limit for Cathedral Rocks WF + Mt Millar WF <= 95 MW to maintain voltage stability limits | NIL | Voltage Stability | SA
Q_STR_7C2K_KBWF_12 | 50824.9525 | 0 | 4.1667 | 0 | No limit to Kaban if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton syncon ON(Haughton syncon OFF 50% daytime,100% at night) ,1% if Kar < 2 or Kareeya >=2, NQLD>250&Ross_FN>100, Zero otherwise. | Outage | System Strength | Qld
VSML_165 | 50356.3762 | 55478.0921 | 7.1667 | 6.75 | Vic to SA on ML upper transfer limit of 165 MW | Outage | Discretionary | Vic
N>>964_86_85_S | 50236.1558 | 0 | 82.6667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Armidale to Tamworth (86) on trip of Uralla to Tamworth (85) line, Feedback | Outage | Thermal | NSW
N_MBTE1_B | 50143.6969 | 91480.1905 | 208.0833 | 102.1667 | Out= one Directlink cable, Qld to NSW limit | Outage | Unit Zero | NSW
S_WATERLWF_RB | 49888.4957 | 185748.0566 | 24.25 | 17 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | Discretionary | SA
N^^V_NIL_1 | 49574.6072 | 10754.1215 | 65.5 | 17.75 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | Voltage Stability | NSW
N>NIL_94B | 49366.2042 | 93561.9191 | 7.4167 | 12.5 | Out= Nil, avoid O/L Beryl to Wellington 132 kV (94B/1) on nil trip, Feedback. Metering at Wellington is used | NIL | Thermal | NSW
N_COLEASF1_FLT_105 | 49126.1976 | 662.6669 | 4 | 1.0833 | Limit Coleambally solar farm upper limit to 105 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>>NIL_84_88_S | 48258.4813 | 31479.9162 | 74.9167 | 43 | Out= NIL, avoid O/L Tamworth to Liddell (84) using 15 min rating on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL | Thermal | NSW
N>>NIL_86_85_S | 48249.4024 | 0 | 71.5833 | 0 | Out= NIL, avoid O/L Armidale to Tamworth (86) on trip of Uralla to Tamworth (85) line, Feedback | NIL | Thermal | NSW
N>NIL_9R5_9R6_N | 48033.3558 | 0 | 0.25 | 0 | Out= NIL, avoid O/L Wagga330 to Wagga North (9R5) 132kV line on trip of Wagga132 to Wagga North (9R6) 132kV line, Feedback | NIL | Thermal | NSW
N_LIMOSF1_FLT_132 | 47465.1385 | 25528.3744 | 4.9167 | 3.8333 | Limit Limondale 1 solar farm upper limit to 132 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>>3H_998_4 | 47332.5825 | 0 | 6.25 | 0 | Out = Crookwell to Gullen Range(3H) 330kV line, avoid O/L Cowra to Forbes (998) 132kV line on trip of Collector to Marulan (4) 330kV line, Feedback | Outage | Thermal | NSW
Q_KEP-HYB_20MW | 47050.2965 | 1621001.7216 | 13.5833 | 260.75 | Kennedy Energy Park upper limit of 20MW | Outage | Discretionary | Qld
V_ARARATWF_FLT_160 | 46927.9249 | 0 | 4.3333 | 0 | Limit Ararat Wind Farm upper limit to 160 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_WANDBL1_ZERO | 46500 | 0 | 0.25 | 0 | Wandoan South BESS (load component) upper limit of 0 MW | Outage | Unit Zero | Qld
N>945_94T | 45738.0535 | 0 | 4.5833 | 0 | Out= Wellington to Molong (945) 132kV line, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
N::N_CRGR_2 | 45181.1706 | 0 | 5.25 | 0 | Out = Crookwell to Gullen Range (3H), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | Transient Stability | NSW
Q_STR_7C2K_KBWF_10 | 45146.1127 | 0 | 3.6667 | 0 | Limit to Kaban Solar Farm 60% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Haughton Syncon ON, Zero otherwise. | Outage | System Strength | Qld
S_LB2WF_CONF | 45066.3286 | 3913.0209 | 7.3333 | 2.9167 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | Voltage Stability | SA
N_SUNRSF_FLT_120 | 45059.9663 | 43714.7793 | 6.3333 | 5.75 | Limit Sunraysia solar farm upper limit to 120 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>>NIL_BEKG_HOMRKM | 45053.6975 | 288440.3322 | 17.8333 | 133.6667 | Out= Nil, avoid O/L Bendigo to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
Q_STR_7C8C_HAYSF | 44941.2332 | 12155.7347 | 5.3333 | 1.0833 | Limit Hayman Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
V^^N_DTMN_1 | 44790.4381 | 93932.4651 | 18.3333 | 51.8333 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
T_BLINK_TV_NGZ | 44588.1735 | 87902.4913 | 30.25 | 22.5 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | NIL | Other | Tas
F_T+NIL_ML_L5 | 44207.65 | 48275.6637 | 844.25 | 2208.9167 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
Q_CS_1100 | 43920.7679 | 570416.9445 | 11.1667 | 70.6667 | Qld Central to Qld South upper transfer limit of 1100MW (discretionary) | Outage | Discretionary | Qld
Q_STR_7C2K_KBWF_17 | 43457.3834 | 0 | 3.5 | 0 | Limit Kaban Solar Farm to 40% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N_LIMOSF2_FLT_18 | 43329.7077 | 23049.6341 | 4.5833 | 3.75 | Limit Limondale 2 solar farm upper limit to 18 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S>>PA6509_BWPA_RBTU | 43133.6377 | 0 | 5.3333 | 0 | Out= Para 275kV CB6509, avoid O/L Robertstown-Tungkillo 275kV line 1 or 2 on trip of Munno Para-Para 275kV line (this offloads Tungkillo-Para 275kV line 2 & Blyth West-Munno Para 275kV line & Munno Para TX), Feedback | Outage | Thermal | SA
CA_SYDS_5494AABA_1 | 43088.9447 | 0 | 8.25 | 0 | Constraint Automation, O/L 99F:L99F:Z:132@NARRAND@NSW for Nil Trip Base Case. Generated by STNET[NORCR1] Host NORREGEEMP7(EMPSYD) | Outage | Thermal | Constraint Automation
Q_STR_7C2K_KBWF_7 | 42337.1749 | 0 | 3.3333 | 0 | Limit to Kaban Solar Farm 25% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG),1% if NQLD>250&270(AVG),Ross_FN>100&120(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_LILYSF1_ZERO | 42237.6133 | 0 | 3 | 0 | Lilyvale Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V_KIAMSF_FLT_120 | 41921.2212 | 8514.4334 | 3.5833 | 4.5833 | Limit Kiamal Solar Farm upper limit to 120 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V>>NIL_EPTT_DDSM_SIP | 41054.7568 | 0 | 1.9167 | 0 | Out= Nil, avoid O/L Eildon to Thomastown 220kV line on trip of one Dederang to South Morang 330kV line, 5 min line rating, Feedback. Swamp if SIPS not available | NIL | Thermal | Vic
V_KARADSF_FLT_54 | 40181.1902 | 49884.3481 | 6 | 9.3333 | Limit Karadoc solar Farm upper limit to 54 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_YATPSF_FLT_49 | 39631.7373 | 47132.7289 | 5.75 | 9.5833 | Limit Yatpool solar Farm upper limit to 49 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>>RBTU_RBTU_WTTP | 38787.3784 | 0 | 11.4167 | 0 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Waterloo to Templers 132kV line on trip of Robertstown to Tungkillo 275kV line 1 or 2, Feedback | Outage | Thermal | SA
F_S++HYSE_L60 | 38523.5976 | 354706.3885 | 86.25 | 231 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage | FCAS | FCAS
N^^V_SM_SCAP_R & N^^V_SM_SCAP_P | 38173.3649 | 1206521.5173 | 59.25 | 159.6667 | Out = both South Morang 330 kV series capacitor banks, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_FINLYSF_FLT_93 | 38169.8265 | 70384.6133 | 4.6667 | 7.25 | Limit Finley solar farm upper limit to 93 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>>V_NIL_0X1_60 | 38140.491 | 5043.8828 | 15.6667 | 4.1667 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_KBWF_18 | 38108.94 | 0 | 3.3333 | 0 | Limit to Kaban Wind Farm 40% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), 80% at night, Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_COLSF_2 | 37900.5212 | 0 | 3.3333 | 0 | Limit Collinsville SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
N>NIL_9R6 | 37900.4078 | 0 | 4.3333 | 0 | Out= NIL, avoid O/L Wagga North - Wagga (9R6) 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
N::N_CNLT_2 | 37883.3271 | 0 | 1.0833 | 0 | Out = Lower Tumut-Canberra (07), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
Q_YARANSF1_ZERO | 37233.39 | 32880.4233 | 5.9167 | 6.1667 | Yarranlea Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
N>945_94K1 | 37099.6634 | 0 | 3.6667 | 0 | Out= Wellington to Molong 132kV line (945), avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | Outage | Thermal | NSW
N_TARALGAWF_005 | 36764.6402 | 1676590.5329 | 9.75 | 359.9167 | Taralga WF upper limit of 5 MW | Outage | Discretionary | NSW
N>NIL_MBDU | 36654.4843 | 454269.6909 | 108.5833 | 50.25 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
Q_STR_7C8C_HAMSF | 35542.7367 | 6432.0662 | 5.75 | 0.5 | Limit Hamilton Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
N>>NIL_39_17 | 35472.8698 | 0 | 2.8333 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL | Thermal | NSW
F_MAIN++BIP_ML_L1 | 35114.7887 | 0 | 577 | 0 | Out = Nil, Lower 1 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS. Requirement capped at 125 MW | Outage | FCAS | FCAS
T::T_HA_GT_PM_4 | 35098.574 | 0 | 48.25 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Transient Stability | Tas
N>>NIL_996_62 | 35025.6396 | 0 | 5.5 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback (Note: constraint swamped when 996 is O/S) | NIL | Thermal | NSW
V_OWF_TGTSNRBHTN_30 | 34328.0292 | 161232.8951 | 2.9167 | 11.3333 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Discretionary | Vic
F_MAIN+APD_TL_L60 | 33871.2814 | 45155.5263 | 407.75 | 1176.9167 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>>WEWT_BWPA_WTTP | 33714.7392 | 0 | 6.1667 | 0 | Out= Waterloo East-Waterloo 132kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
Q_STSTN_864 | 33225.4971 | 0 | 0.33333 | 0 | Out= 864 Stanwell Power Station 275kV line | Outage | Unit Zero | Qld
V>SMLMHNW1 | 32934.2018 | 0 | 9.6667 | 0 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | SA
Q_STR_7C0K_COLSF_1 | 32925.0856 | 0 | 2.8333 | 0 | No limit to Collinsville Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
N>>NIL_85_86_S | 32859.7759 | 0 | 38.0833 | 0 | Out= NIL, avoid O/L Uralla to Tamworth (85) on trip of Armidale to Tamworth (86) line, Feedback | NIL | Thermal | NSW
N>NIL_997/1_62 | 32628.2608 | 0 | 3.5 | 0 | Out= NIL, avoid O/L Corowa to Albury (997/1) 132kV line on trip of Wagga to Jindera (62) 330kV line, Feedback | NIL | Thermal | NSW
V_S_NIL_ROCOF | 32461.2662 | 72951.7662 | 29.5 | 22 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | Vic
T_ROCOF_3 | 32248.6982 | 5834.9215 | 60.5 | 8.5833 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | ROC Frequency | Tas
Q_STR_7C0K_SMSF_1 | 32150.5023 | 0 | 3.4167 | 0 | No limit to Sun metals Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_MARYRSF1_10 | 31719.9541 | 177614.0539 | 18.0833 | 32.4167 | Maryrorough Solar Farm upper limit of 10 MW | Outage | Discretionary | Qld
T>T_HA_TX_2 | 31656.8022 | 3819.6473 | 26.0833 | 7.4167 | Out = Hadspen 220/110 kV txfmr, avoid O/L Palmerston 220/110 kV txfmr (flow from 110 kV to 220 kV) on trip of remaining Hadspen 220/110 kV txfmr, feedback | Outage | Thermal | Tas
Q_STR_7C0K_DAYSF_2 | 31236.801 | 0 | 2.75 | 0 | Limit Daydream SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
V>>NIL_ARTSTL_ARCW | 30894.0403 | 0 | 4.3333 | 0 | Out = Nil, avoid O/L Ararat to Stawell 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service, Feedback | NIL | Thermal | Vic
Q_KEP-HYB_29MW | 30799.8027 | 0 | 10.9167 | 0 | Kennedy Energy Park upper limit of 29MW | Outage | Discretionary | Qld
Q>>BCRG_BCCP_CLWU | 30538.9232 | 2133.0978 | 6 | 2.3333 | Out= Bouldercombe to Raglan (811), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
V::N_DDSM_xxx | 30437.3016 | 376802.0229 | 52.9167 | 318.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>>BUCW_DPTX_KGBE | 30237.7949 | 0 | 3.0833 | 0 | Out= Bulgana to Crowlands 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
VSML_ZERO | 30057.1125 | 13872.9695 | 2.8333 | 3.5833 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | Vic
S-MAPS3-PV_0 | 29092.2859 | 0 | 10.5833 | 0 | Discretionary upper limit for SA WATER Mannum Adelaide Pumping Station No 3 PV (Kanmantoo) generation of 0 MW | Outage | Unit Zero | SA
N^^V_CNCW_1 | 28503.4081 | 63771.4778 | 35.1667 | 40.6667 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W) or Dapto-Kangaroo Valley (18), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
SVML_ROC_80 | 28496.2034 | 146443.6791 | 87.1667 | 78.5 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | SA
Q_STR_7C2K_KIDSF_5 | 28271.3206 | 2.0201 | 13.5 | 0.16667 | No limit to Kidston Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
N>>NIL_61_4 | 27838.6975 | 0 | 0.83333 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) on trip of Collector to Marulan (4) line, Feedback | NIL | Thermal | NSW
S>>BWMP_BRTW_WTTP | 27785.5248 | 22008.0998 | 10.75 | 9 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
CA_SYDS_53C9C000_1 | 27632.3999 | 0 | 2.25 | 0 | Constraint Automation, O/L XFMR 4H@DARL_PT@NSW for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP7(EMPSYD) | Outage | Thermal | Constraint Automation
N>79_94T_72 | 27577.0944 | 0 | 3.9167 | 0 | Out= Wollar West to Wellington (79) 330kV line or Wollar 500/330kV TX or Wollar to Wollar West (75) 330kV line, avoid O/L on Molong to Orange North (94T) on trip of Wellington to Mt Piper line (72), Feedback | Outage | Thermal | NSW
VTBL_ROC | 27512.7281 | 511991.7303 | 16.5833 | 11.5833 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Vic
N>966+KK_966/1_NIL | 27436.9188 | 0 | 7.8333 | 0 | Out= 966 (Armidale to Koolkhan) 132kV line [NOTE: Open at Koolkan end ONLY, Armidale end remains closed] O/S , avoid O/L Metz Tee to Armidale (966/1) kV line on trip of Nil, Feedback | Outage | Thermal | NSW
F_MAIN++APD_TL_L6 | 27347.2076 | 48077.7602 | 594.25 | 1042.4167 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_I+NIL_MG_R5 | 26682.9088 | 38699.2072 | 5124.4167 | 5182.1667 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL | FCAS | FCAS
F_MAIN++NIL_MG_R5 | 26629.4926 | 10459.2603 | 2410.4167 | 934.75 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
Q_STR_7C2K_WHTSF_5 | 26412.8533 | 0.00017 | 7.5833 | 0.083333 | No limit to Whitsunday Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
I_CTRL_ISSUE_ML | 26231.1975 | 22740.2581 | 17.3333 | 7.1667 | DC Link Control Issue Constraint for Murraylink | Outage | Other | Other
S>>BWMP_DVBR_RHBG-T | 25960.4496 | 77117.6821 | 9.3333 | 17.5 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill- Brinkworth 132kV T line on trip of Davenport-Brinkworth 275kV line, Feedback | Outage | Thermal | SA
F_MAIN+NIL_MG_R60 | 25803.4948 | 927575.0914 | 380.6667 | 1082.8333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
T>T_NIL_110_1 | 25615.7878 | 78403.8087 | 35 | 49.75 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Thermal | Tas
V_BULGANAWF_FLT_60 | 25536.4826 | 0 | 2 | 0 | Limit Bulgana Wind Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_STR_7C0K_DAYSF_1 | 25161.517 | 0 | 2.1667 | 0 | No limit to Daydream Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HASF_5 | 25077.5278 | 88382.3 | 1.9167 | 6.1667 | No limit to Haughton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N>>3H_5_4_N | 24790.8194 | 0 | 3.3333 | 0 | Out = Crookwell to Gullen Range (3H), avoid O/L Yass to Marulan (5) 330kV line on trip of Collector to Marulan (4) 330kV line, Feedback | Outage | Thermal | NSW
F_Q++BCDM_L6 | 24720.9683 | 9879.941 | 40.1667 | 24.4167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C8C_RRSF | 24609.5125 | 9865.7305 | 5.75 | 5.8333 | Limit Ross River Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
N>968_969_NIL | 24367.2224 | 0 | 1.8333 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line, avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | Outage | Thermal | NSW
V::N_X_SMSC_O1 | 24200.1564 | 686116.0389 | 51.3333 | 95.25 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
CA_BRIS_5347C6C8_1 | 24190.5868 | 0 | 2 | 0 | Constraint Automation, O/L SNWHUM_T:LHS:I:132@BUNGAM@SA for CTG LS6X on trip of CLAR_N - MINTAR 132KV LINE. Generated by STNET[BNECR3] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
T::T_NIL_3 | 24081.3253 | 183297.9348 | 65.6667 | 120.8333 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Transient Stability | Tas
QN_1200_DYN_TEST | 24061.1861 | 889.1208 | 12.75 | 3.1667 | QLD to NSW on QNI upper transfer limit of 1200 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | Qld
S>>X_CR+RBTX+TPRS_13 | 24000.8735 | 0 | 3.75 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
VSML_100 | 23942.8677 | 0 | 4.8333 | 0 | Vic to SA on ML upper transfer limit of 100 MW | Outage | Discretionary | Vic
N::X_2+3J_2 | 23517.9899 | 0 | 24.5 | 0 | Out = Upper Tumut-Ravine (6X) 330kV line/Ravine-Yass (2) 330kV line + Yass-Gullen Range (3J) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
V^^N_BURC_1 | 23431.0219 | 0 | 11.5 | 0 | Out = Buronga to Red Cliffs (0X1) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N>>NIL_39_11 | 23210.5321 | 0 | 2 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | Thermal | NSW
N^^V_MLNK_1 | 23130.3644 | 1874.6589 | 30.25 | 2.4167 | Out = Murraylink, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_7C2K_RRSF_7 | 22847.4672 | 43543.2931 | 12.5 | 19 | Limit to Ross River Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V>>N-62_66_65_RADIAL | 22191.505 | 0 | 36.5833 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | Vic
V_S_HEYWOOD_UFLS | 22097.9367 | 59224.0708 | 22.75 | 23.8333 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC. Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL | Other | Vic
N>NIL_997/2_62 | 21990.4664 | 0 | 5.75 | 0 | Out= NIL, avoid O/L Mulwala to Corowa (997/2) 132kV line on trip of Wagga to Jindera (62) 330kV line, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_RUGSF_5 | 21783.8784 | 8026.1701 | 1.8333 | 0.58333 | No limit to Rugby Run Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG)(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise | Outage | System Strength | Qld
S-OUT_WTPT_SC+INV_1 | 21741.4098 | 17922.4136 | 1.9167 | 2.25 | Out=HUBG Or HUWT line Or one CB(HU 6135/6060,BG 6246,WT 7022/7021), limit output of Wattle Pt WF based on Wattle Pt statcom status & the number of Dalrymble battery inverters I/S (Note:swamped for No. of Dalrymple bat. inverters < 10 && 1or2 SC O/S) | Outage | Other | SA
F_T++NIL_MG_RECL_R6 | 21598.3956 | 31823.2181 | 356.3333 | 83.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V>>ARWB_X3_BEKG | 21485.2651 | 0 | 3.3333 | 0 | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage | Thermal | Vic
V>>NIL_MBDD_MBDD | 21015.0186 | 118367.5363 | 41.3333 | 20.25 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Thermal | Vic
F_Q++86_L6 | 20957.7665 | 0 | 36.6667 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
V_BANSF_BBD_80 | 20884.9026 | 154046.2245 | 10.0833 | 30.3333 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
N>94T_947_72 | 20669.0494 | 0 | 2.0833 | 0 | Out= Molong to Orange North (94T) 132kV line, avoid O/L Wellington to Orange North (947) 132kV line on trip of Wellington to Mt Piper (72) 330kV line, Feedback | Outage | Thermal | NSW
N>>NIL_5_3L_N | 20560.9952 | 0 | 1.25 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) using 15 mins rating on trip of Yass to Collector (3L) line, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_SMSF_10 | 20207.2822 | 0 | 1.6667 | 0 | Limit Sun Metals Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
N_NIL_TE_B | 19494.2034 | 2649005.8076 | 59.5 | 92.3333 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | Other | NSW
N>>81_964_82 | 19279.488 | 4824.6192 | 11.1667 | 3.25 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, (Note: Swamps if 964 O/S) | Outage | Thermal | NSW
Q_STR_7C2K_HAMSF_10 | 19198.4542 | 0 | 1.5833 | 0 | Limit Hamilton Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
F_I+NIL_APD_TL_L6 | 19094.3486 | 44799.8375 | 1687.5 | 3570.8333 | Lower 6 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
F_I+GFT_TG_R60 | 19064.6275 | 30396.8104 | 711.3333 | 476.5833 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
Q_YARANSF1_37 | 18956.1556 | 116507.3481 | 8.4167 | 17.6667 | Yarranlea Solar Farm upper limit of 37 MW | Outage | Discretionary | Qld
F_T++NIL_ML_L6 | 18753.8621 | 242.9106 | 1312.75 | 47.4167 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL | FCAS | FCAS
N>>NIL_7_3 | 18602.1477 | 79635.9527 | 0.75 | 0.66667 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, [Note: unswamped when both 1 & 2 LSC disabled] | NIL | Thermal | NSW
S:V_550_HY_TEST | 18510.3679 | 1170.5179 | 49.6667 | 3.6667 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
F_T+NIL_MG_RECL_R60 | 18284.9691 | 164881.1694 | 391 | 2002.4167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
N>>NIL_88_84_S | 18228.4798 | 7192.1718 | 25.9167 | 11 | Out= NIL, avoid O/L Tamworth to Muswellbrook (88) using 15 min rating on trip of Tamworth to Liddell (84) line, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_HAYSF_10 | 18165.8789 | 0 | 1.5 | 0 | Limit Hayman Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
V>>N_NIL_65_66 | 18106.6828 | 360207.6003 | 37.5833 | 133.25 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Thermal | Vic
Q_STR_7C0K_CLRSF_1 | 18094.1596 | 0 | 1.5833 | 0 | No limit to Clare Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
V_BANNERTON_ZERO | 17804.452 | 106474.9637 | 1.4167 | 9.0833 | Bannerton Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
T_FAJB | 17800.22 | 0 | 0.25 | 0 | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
V^^N_DPWG_X5_1 | 17585.8701 | 10649.7071 | 14.25 | 7.6667 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
VS_250_DYN | 17387.1869 | 11796.8367 | 1 | 4.75 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
Q_KEP-HYB_50MW | 17239.4314 | 0 | 6.25 | 0 | Kennedy Energy Park upper limit of 50MW | Outage | Discretionary | Qld
Q_STR_7C2K_COLSF_10 | 17187.5133 | 0 | 1.4167 | 0 | Limit Collinsville Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_DAYSF_10 | 17181.0452 | 0 | 1.4167 | 0 | Limit Daydream Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_HAYSF_1 | 17006.8676 | 0 | 1.6667 | 0 | No limit to Hayman Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
V_VS_MLMO_NETT | 16832.479 | 0 | 12.8333 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage | FCAS | Vic
S>>RBTU_RBTU_WEWT | 16818.738 | 0 | 4.3333 | 0 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Waterloo East to Waterloo #1 132kV line on trip of Robertstown to Tungkillo 275kV line 1 or 2, Feedback | Outage | Thermal | SA
S>>NIL_RBTU_RBPA | 16237.6313 | 5172.4286 | 4.75 | 1.5833 | Out= Nil, avoid O/L Robertstown-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
Q_STR_7C2K_RUGSF_10 | 16199.9093 | 0 | 1.3333 | 0 | Limit Rugby Run Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
N>Q-NIL_757_758 | 16189.9497 | 18227.0854 | 54.6667 | 59.4167 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL | Thermal | NSW
S>>TBTU_TUTB_MOTB | 16127.9979 | 0 | 31.5833 | 0 | Out= One Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of remaining Tungkillo-Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
N>>964_85_86_S | 16019.0747 | 0 | 30.8333 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Uralla to Tamworth (85) on trip of Armidale to Tamworth (86) line, Feedback | Outage | Thermal | NSW
V^^N_LTMS_1 | 15624.7743 | 0 | 6.5833 | 0 | Out = Murray to Lower Tumut 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
T>T_NIL_BL_3B | 15500 | 0 | 0.083333 | 0 | Out = Nil, avoid pre-contingent O/L of the Palmerston to Hadspen No. 2 220kV line (flow to North), feedback | NIL | Thermal | Tas
N>>NIL_DPTX_HV | 15472.4293 | 0 | 1.1667 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL | Thermal | NSW
F_Q++86_L60 | 15235.3803 | 0 | 35.1667 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C8C_CLRSF | 15176.3302 | 2414.3223 | 2.75 | 2.6667 | Limit Clare Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
Q_NIL_STRGTH_HAUSF | 14950.4992 | 11500.0971 | 16.5833 | 1.25 | Out = Nil, limit Haughton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q:N_1078 | 14924.9568 | 827232.3616 | 26.75 | 13 | QNI oscillatory stability limit of 1078 MW | Outage | Oscillatory Stability | Qld
T>>T_NIL_BL_EXP_7C | 14882.8287 | 7833.7266 | 34.75 | 9.9167 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
SVML_FLT_130 | 14816.293 | 234854.6082 | 18.8333 | 26.1667 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
Q_NQ_SEMI_RAMP_ZERO | 14762.0526 | 740005.2962 | 1 | 41.6667 | Ramp North Qld semi-scheduled generators to zero and hold at zero | Outage | Unit Zero | Qld
V>>NIL_RCWE_HOBUCW | 14722.6982 | 48014.3422 | 14.3333 | 23.4167 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
S^NIL_PL_MAX | 14385.6435 | 1902712.4965 | 3.8333 | 43.9167 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | Voltage Stability | SA
S_CMWF_0 | 14195.2276 | 0 | 1.25 | 0 | Discretionary upper limit for Clements Gap WF generation of 0 MW | Outage | Unit Zero | SA
Q_STR_7C2K_KBWF_15 | 14133.7057 | 0 | 1.25 | 0 | Limit to Kaban Wind Farm 50% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar>=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), no limit if Haughton syncon ON or at night,1% if Kar < 2 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG), Zero otherwise. | Outage | System Strength | Qld
N>947+94P_94T | 14056.0752 | 0 | 0.33333 | 0 | Out= Wellington to Orange North (947) 132kV line + Manildra to Molong (94P) 132kV, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
V>DDMB_MBDD_EPTT | 14051.1125 | 0 | 5.3333 | 0 | Out= one Dederang to Mount Beauty 220 kV line, avoid O/L the remaining Mount Beauty to Dederang 220kV line on trip of the Eildon to Thomastown 220 kV line, feedback | Outage | Thermal | Vic
N_MOREESF1_21INV | 13903.7398 | 0 | 1.0833 | 0 | Moree Solar Farm inverter limit of 21. Constraint to violate if Moree Solar Farm inverter availability greater than 21. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_FINLYSF1_ZERO | 13863.7269 | 34095.0886 | 2.25 | 2.1667 | Finley solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
F_MAIN+APD_TL_L5 | 13776.5752 | 14375.6285 | 406.8333 | 978.8333 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N_COLEASF1_FLT_40 | 13689.9885 | 0 | 1.0833 | 0 | Limit Coleambally solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
NQ_750_DYN_TEST | 13669.6342 | 0 | 13 | 0 | NSW to QLD on QNI upper transfer limit of 750 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | NSW
V>>XGTML2_KTTX2_1_R2 | 13596.0841 | 0 | 3 | 0 | Out= Geelong to Moorabool No.2 220kV line and Keilor A2 500/220kV transformer, avoid O/L Moorabool to Geelong No.1 220kV line on trip of Sydenham to Keilor 500kV line (offloading Keilor A4 500/220kV transformer), radial mode, YWPS1 on 220kV mode, Feedback | Outage | Thermal | Vic
N^^V_NIL_ARWBBA | 13576.1259 | 20296.064 | 38 | 31.4167 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL | Voltage Stability | NSW
Q>COLTX | 13434.1841 | 2710.4158 | 1.0833 | 0.58333 | Out = Collinsville North T1 or T2 132/33 kV transformer, limit Collinsville Solar Farm to 33.9MW to prevent overload on RMU of the remaining transformer | Outage | Thermal | Qld
V_KIAMSF_40INV_DYN | 13395.635 | 16173.2608 | 1.3333 | 1.5833 | Limit Kiamal Solar Farm upper limit to 0 MW if number of inverter available exceeds 40 and Murra Warra 2 WF Syncon O/S. Constraint swamps out otherwise. DS only | Outage | System Strength | Vic
T_MRWF_QLIM_xx | 13257.6094 | 107573.4367 | 12.75 | 10.3333 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Transient Stability | Tas
S_ISLE_CRK_60 | 13180.4574 | 0 | 6.0833 | 0 | Discretionary upper limit on Cathedral Rocks windfarm <=60 MW when 4 syn cons I/S for SA is at risk of islanding - otherwise limited to 10 MW | Outage | Discretionary | SA
F_MAIN++NIL_BL_L60 | 13146.1743 | 59233.0395 | 288.5 | 877.0833 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
N_MOREESF1_055 | 12927.3372 | 0 | 1.5833 | 0 | Moree Solar Farm upper limit of 55 MW | Outage | System Strength | NSW
Q_STR_7C0K_RRSF_1 | 12860.6844 | 0 | 2.6667 | 0 | No limit to Ross River Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
V::N_JNWG_xxx | 12775.3856 | 1233.6945 | 20.1667 | 1.5833 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
N_NYNGANSF_ZERO | 12750.1259 | 0 | 0.83333 | 0 | Nyngan Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
S>>PARB_TWPA_TPRS | 12687.1453 | 716.7741 | 1.0833 | 0.33333 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
V::N_X_SMSC_xxx | 12437.9363 | 1062045.5876 | 21.4167 | 191 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
N>>NIL_86_8U_S | 12328.7356 | 65429.0894 | 24.6667 | 73.1667 | Out= NIL, avoid O/L Armidale to Tamworth (86) using 15 min rating on trip of the other Armidale to Uralla line (8U), Feedback | NIL | Thermal | NSW
F_V_APD01_R60 | 12309.5233 | 0 | 47.0833 | 0 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>>NIL_9_18_N | 12304.2202 | 0 | 0.91667 | 0 | Out= Nil, avoid O/L Canberra to Yass (9) using 15 mins rating on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | Thermal | NSW
N>9R6_9R5_NIL | 12301.2613 | 0 | 1.0833 | 0 | Out= 9R6 (Wagga North to Wagga 132) 132kV line, avoid O/L Wagga North to Wagga (9R5) on trip of Nil, Feedback | Outage | Thermal | NSW
N>>994_99F_63 | 12286.1506 | 189581.9781 | 10.0833 | 22.5833 | Out= Narrandera to Wagga (994) 132kV line, avoid O/L Yanco to Uranquinty (99F) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,(Note: Option C on OM521) | Outage | Thermal | NSW
V^^N_DTSS_1 | 11622.6126 | 0 | 12.3333 | 0 | Out = Dapto-Sydney South(11), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^S_PAVC1_MAXG | 11485.6252 | 3081.408 | 6.25 | 2 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
N::Q_NIL_KC | 11175.5954 | 31409.4175 | 25.4167 | 0.25 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | Transient Stability | NSW
Q_STR_7C0K_HAMSF_1 | 11121.5245 | 0 | 3 | 0 | No limit to Hamilton Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
F_T++NIL_BL_R60_3 | 10969.8987 | 0 | 253.75 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 3, FCSPS available | NIL | FCAS | FCAS
N>NIL_9R5 | 10923.9626 | 0 | 0.91667 | 0 | Out= NIL, avoid O/L Wagga North-Wagga (9R5) 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
S_PPT+SNPT+BLVR_220 | 10846.9652 | 0 | 0.83333 | 0 | SA Pelican Point + Snapper Point generation +Bolivar PS<= 220 MW | Outage | Discretionary | SA
N>GITN-96R_967_89 | 10845.1344 | 0 | 7 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89),(Noted: Swamped out when 967 O/S) | Outage | Thermal | NSW
V::S_TBCP1_MAXG | 10807.7769 | 42.7643 | 4.6667 | 0.083333 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage | Transient Stability | SA
N_METZSF_106 | 10751.4685 | 0 | 3.5833 | 0 | Metz Solar farm upper limit of 106 MW | Outage | System Strength | NSW
T_T_FASH_HM_OPEN_1 | 10696.5286 | 0 | 10.4167 | 0 | Out = one Farrell to Sheffield 220kV line, West Coast 220/110 kV parallel open, Farrell 220 kV bus not split, limit West Coast gen <= 110% of West Coast load | Outage | Other | Tas
T^V_NIL_9 | 10562.4595 | 33681.1072 | 24.5833 | 33.5 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Voltage Stability | Tas
F_Q++MUTW_L6 | 10390.1681 | 0 | 16.0833 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
Q>NIL_BI_xxx | 10366.2531 | 0 | 0.33333 | 0 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines | NIL | Thermal | Qld
S>>NIL_RBTX_RBTX_2 | 10338.7277 | 4400.5656 | 1.5 | 0.91667 | Out= Nil, avoid O/L of one Robertstown 132/275kV TX on trip of other Robertstown 132/275kV TX, Feedback | NIL | Thermal | SA
F_T++NIL_BL_R6_3 | 10209.0424 | 0 | 168.3333 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 3, FCSPS available | NIL | FCAS | FCAS
V>NIL_GNTX_GNTX_TEMP | 10179.594 | 0 | 14 | 0 | Out= Nil, maintain post-contingent loading (from 66 to 220kV) on either Glenrowan B txfmr less than 187.5 MVA for loss of one Glenrowan B txfmr, Feedback | NIL | Thermal | Vic
Q_WARTX_SF2 | 10169.38 | 0 | 1.5 | 0 | Out= Warwick 110/33kV Transformer T1 or T2 O/S, limit Warwick SF 2 to 16.7MW as per Ergon ramp down scheme | Outage | Thermal | Qld
CA_SYDS_544A2F7F_2 | 10153.54 | 0 | 2.5833 | 0 | Constraint Automation, O/L 998:L998:I:132@COWRA@NSW for CTG LNQT on trip of COLLECWF-MARULAN 4 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP7(EMPSYD) | Outage | Thermal | Constraint Automation
N>>NIL_YSTX_LV | 10138.6355 | 0 | 1.4167 | 0 | Out= Nil, avoid O/L Either of Yass 132/330 Transformers on trip of Nil, Feedback | NIL | Thermal | NSW
F_T++NIL_ML_L60 | 9838.6809 | 477.7059 | 940.1667 | 33.6667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_S+NIL_HPR_G+L_LREG | 9824.3382 | 0 | 0.083333 | 0 | Out= NIL, Hornsdale Battery Joint HPRG1+HPRL1 Energy & FCAS LowerReg ramping constraint | NIL | FCAS | FCAS
V^^S_PAVC1_SETB | 9628.1723 | 760.3296 | 11.4167 | 1.9167 | Out= Para one SVC(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
Q_KEP-HYB_35MW | 9605.9227 | 0 | 4 | 0 | Kennedy Energy Park upper limit of 35MW | Outage | Discretionary | Qld
Q>>LCCP_BCCP_CLWU | 9581.7617 | 0 | 1.3333 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
NSA_T_DVGATE_10 | 9357.2947 | 0 | 2.0833 | 0 | Devils Gate >= 10 MW for Network Support Agreement | Outage | Network Support | Tas
Q::N_8C8J_AR_2LG_N-2 | 9138.0477 | 22508.9333 | 18.0833 | 3 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | Qld
S>>NIL_TWPA_BWMP | 9051.6018 | 0 | 1.1667 | 0 | Out= Nil, avoid O/L Blyth West-Munno Para 275kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
S>NIL_RBMWP3_RBNW1 | 9016.6563 | 10412.1751 | 9.5 | 15.1667 | Out= Nil, avoid O/L Robertstown-North West Bend #1 132kV line on trip of Robertstown-Morgan Pipeline 3-Morgan Pipeline 2-Morgan Pipeline 1-North West Bend 132kV #2 line, Feedback | NIL | Thermal | SA
S>X_CNRB+RBTX1_23 | 8892.0803 | 0 | 28.25 | 0 | Out= Robertstown TX1 + Canowie-Robertstown 275kV line O/S, avoid O/L Robertstown 275/132kV TX2 on trip of Robertstown-Waterloo East 132kV line (This trip MWP4 SF) line, Feedback | Outage | Thermal | SA
N_MOREESF1_20INV | 8849.9797 | 0 | 0.66667 | 0 | Moree Solar Farm inverter limit of 20. Constraint to violate if Moree Solar Farm inverter availability greater than 20. Swamp out otherwise. DS only | Outage | System Strength | NSW
F_Q++BCDM_L60 | 8840.4076 | 8087.7004 | 25.9167 | 22.5833 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
S>>X_CNRB+RBTX1_07 | 8760.4123 | 0 | 2.1667 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
F_Q++8E_L6 | 8589.4648 | 10214.3999 | 14.4167 | 24.9167 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
V>>ARCW_DPTX_KGBE | 8490.1539 | 0 | 16.1667 | 0 | Out= Ararat to Crowlands 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
N>>14_39_12 | 8420.6901 | 0 | 1.5833 | 0 | Out = Kemps Creek to Sydney North (14), avoid O/L Bannaby to Sydney West (39) on trip of Sydney South to Liverpool (12) line, Feedback | Outage | Thermal | NSW
Q_STR_32282_DAYSF | 8366.7583 | 15624.9511 | 0.66667 | 1.1667 | Limit 50% to Daydream SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_HAYSF | 8366.7549 | 1633.7826 | 0.66667 | 1.0833 | Limit 50% to Hayman SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
V>>NIL_RCWE_HOMRKM | 8220.8363 | 0 | 6.1667 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
CA_BRIS_540A554F_1 | 8196.7996 | 0 | 0.83333 | 0 | Constraint Automation, O/L 9R6:L9R6:Z:132@WAGGANTH@NSW for CTG LN7V on trip of YASS-MURRUMBR 99M 132KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP5(EMPBRI) | Outage | Thermal | Constraint Automation
F_I+GFT_TG_R6 | 8195.7015 | 8566.8629 | 253.5833 | 246.75 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
S>>X_RBPA+RBTX_06 | 8165.8232 | 0 | 3.75 | 0 | Out=Robertstown-Para 275 kV line + one Robertstown TX 275/132 kV, avoid O/L remaining Robertstown 275/132kV TX on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
N>>LDTM_964_81_OPEN | 8115.2558 | 9083.0565 | 12.4167 | 5.25 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage | Thermal | NSW
V^^N_CNCW_1 | 8073.86 | 0 | 2.5 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_STR_7C2K_MEWF_12 | 8068.4311 | 0 | 2.75 | 0 | Limit Mt Emerald Wind Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_WARTX_SF1 | 8028.2223 | 0 | 1.3333 | 0 | Out= Warwick 110/33kV Transformer T1 or T2 O/S, limit Warwick SF 1 to 16.7MW as per Ergon ramp down scheme | Outage | Thermal | Qld
N>96M_969_NIL | 7949.3384 | 0 | 2.5833 | 0 | Out= Any one 132kV feeder between Moree to Boggabri East (96M,9UH,9UJ),avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | Outage | Thermal | NSW
S>>RBTX1_RBTX2_WTTP | 7942.5891 | 0 | 3.8333 | 0 | Out= one Robertstown 275/132kV TX, avoid O/L Waterloo-Templers 132kV line on trip of remaining Robertstown 132/275kV TX, Feedback | Outage | Thermal | SA
F_MAIN+BIP_ML_L6 | 7877.7279 | 20.53 | 314.3333 | 8.5833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL | FCAS | FCAS
V::N_HWSM_xxx | 7856.0395 | 0 | 24.6667 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_T_NIL_MINP_R6 | 7824.7601 | 102445.4138 | 41.3333 | 673.0833 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL | FCAS | FCAS
V^^S_TBEBUS_MAXG | 7822.619 | 0 | 4.5833 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA | Outage | Voltage Stability | SA
VSML_010 | 7774.0527 | 0 | 0.5 | 0 | Vic to SA on ML upper transfer limit of 10 MW | Outage | Discretionary | Vic
F_MAIN+NIL_MG_R1 | 7694.9322 | 0 | 22.25 | 0 | Out = Nil, Raise 1 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS. Requirement capped at 225 MW | Outage | FCAS | FCAS
V::N_X_ARWBBA_xxx | 7693.6958 | 0 | 7.6667 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>>NIL_WEKG_HOMRKM | 7643.5423 | 267.7091 | 1.0833 | 0.25 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
V^^N_UTRV_1 | 7638.926 | 106349.9816 | 12.3333 | 21.5833 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_STR_7C0K_RUGSF_1 | 7612.3876 | 0 | 0.66667 | 0 | No limit to Rugby Run Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
F_S++HYSE_L6_1 | 7582.8381 | 297151.4206 | 59.1667 | 191 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage | FCAS | FCAS
VSML_060 | 7575.5884 | 0 | 2.75 | 0 | Vic to SA on ML upper transfer limit of 60 MW | Outage | Discretionary | Vic
T>NIL_SH_IMPORT | 7546.8564 | 0 | 8.3333 | 0 | Credible risk of losing entire Sheffield 220kV network, Limit importing flow into Sheffield on Sheffield to Palmerston and Sheffield to George Town 220kV lines to <= 10 MVA. Feedback | Outage | Other | Tas
SVML_FLT_150 | 7392.542 | 4316.6024 | 19.3333 | 2.0833 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | SA
S>>NIL_RBTU_WEWT | 7385.3238 | 126070.7331 | 2.5833 | 21.5833 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of one Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
Q_STR_32282_HAMSF | 7344.2025 | 14332.235 | 0.58333 | 1.0833 | Limit 50% to Hamilton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_SMSF | 7344.2017 | 474.4328 | 0.58333 | 0.41667 | Limit 50% to Sun Metals SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_COLSF | 7344.1999 | 6268.2065 | 0.58333 | 0.5 | Limit 50% to Collinsville SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
V_GANWR_SF_BAT_50 | 7341.9852 | 7790.1554 | 1.4167 | 3.25 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Discretionary | Vic
S::V_TBSE_TBSE_2 | 7284.0835 | 1102.8311 | 6.25 | 1.0833 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
F_T++NIL_WF_TG_R6 | 7245.2213 | 1036.5455 | 180 | 12.6667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
T_V_NIL_BL1 | 7244.3293 | 176826.6605 | 13.3333 | 13.25 | Out=Nil, Basslink no go zone limits Tas to Vic. Limit Basslink upper limit to 125 MW on 1st DI out of no go zone. i.e. BL <= 125 MW | NIL | Other | Tas
T^T_LIPM_1 | 7234.6256 | 5941.5322 | 0.5 | 6.3333 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line | Outage | Voltage Stability | Tas
Q_WDGPH1_ZERO | 7213.5936 | 0 | 0.58333 | 0 | Western Downs Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_STR_7C2K_MEWF_13 | 7205.6168 | 0 | 3.6667 | 0 | Limit Mt Emerald Windfarm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),(100% at night),Zero otherwise. | Outage | System Strength | Qld
V_KIAMAL_SC_DYN | 7203.1898 | 0 | 0.66667 | 0 | Out = Kiamal Syncon, Limit Kiamal solar farm to 135 MW when Murra Warra 2 WF syncon I/S. Limit Kiamal solar farm to 100 MW when Murra Warra 2 WF syncon O/S. DS only. Swamp out if Kiamal Syncon is in service | NIL | Discretionary | Vic
F_T+NIL_WF_TG_R60 | 7069.2904 | 101661.0571 | 159.4167 | 1147.3333 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>RBTX1_RBTX2_WEMWP4 | 7068.2397 | 93195.4463 | 18.1667 | 76.3333 | Out= one Robertstown 275/132kV TX, avoid O/L MWP4-Robertstown 132kV line on trip of remaining Robertstown 275/132kV TX | Outage | Thermal | SA
N^^V_2_6X_3J_1 | 6990.1966 | 0 | 11.1667 | 0 | Out = Ravine-Yass or Upper Tumut to Ravine (2 or 6X) 330kV line and Gullen Range to Yass (3J), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
NQTE_ROC | 6946.287 | 102303.1776 | 38.75 | 32.5833 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | NSW
N>PKTX_TX_NIL | 6939.3504 | 0 | 0.66667 | 0 | Out= One Parkes 132/66kV transformer , avoid O/L the remaining Parkes 66/132kV transformer on trip of Nil, Feedback | Outage | Thermal | NSW
N_WR_30_WT-INV | 6911.4082 | 2555.4082 | 0.66667 | 0.33333 | White Rock Wind & Solar Farm inverter limit of 30. Constraint to violate if White Rock Wind & Solar Farm inverter availability greater than 30. Swamp out otherwise. DS only | Outage | System Strength | NSW
F_Q++MUTW_L60 | 6898.6573 | 0 | 15.5 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
V_MTMERCER_ZERO | 6874.3697 | 7305.2108 | 4.5833 | 2.0833 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Unit Zero | Vic
S>>PARB_RBTU_RBMWP4 | 6846.7282 | 2170.9552 | 3.5833 | 1.25 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N>991_9R6_9R5 | 6748.5305 | 0 | 0.75 | 0 | Out= Wagga North to Murrumburrah 132kV line (991), avoid O/L Wagga North to Wagga132 (9R6) on trip of Wagga North to Wagga330 (9R5) line, Feedback | Outage | Thermal | NSW
S>>BWMP_BGBR_HUWT | 6725.1876 | 235.8477 | 1.1667 | 0.16667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap WF), Feedback | Outage | Thermal | SA
V_T_NIL_BL1 | 6699.9986 | 7028.0606 | 11.25 | 9.25 | Out=Nil, Basslink no go zone limits Vic to Tas. Limit Basslink lower limit to -125 MW on 1st DI out of no go zone. i.e. BL >= -125 MW | NIL | Other | Vic
T_FISH | 6696.3815 | 0 | 0.5 | 0 | Out=Sheffield-Fisher 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
V>>V_DDSM_1 | 6573.9975 | 261018.6597 | 5.4167 | 136.9167 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Thermal | Vic
T_FARC2_2 | 6491.7746 | 0 | 2.4167 | 0 | Out=Farrell - Reece 2 220KV line. Discretionary 144 MW limit on Reece 1 + Granville Harbour WF | Outage | Discretionary | Tas
N::N_CNCW_2 | 6460.6527 | 40918.75 | 4.8333 | 7.75 | Out = Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line | Outage | Transient Stability | NSW
F_V_APD01_R6 | 6341.8475 | 0 | 47.1667 | 0 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>X_RBTX+MNWT_18 | 6322.8043 | 0 | 1.1667 | 0 | Out= One Robertstown 275/132 kV TX + Mintaro-Waterloo 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage | Thermal | SA
QN_1200_TEST | 6310.6571 | 126.4013 | 6 | 0.83333 | Qld to NSW on QNI upper transfer limit of 1200 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | Qld
Q_STR_32282_RGBSF | 6301.6293 | 16954.648 | 0.5 | 1.25 | Limit 50% to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_Q++LDTW_L6 | 6265.6083 | 0 | 9.5 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
Q>NIL_DRLCLB_DRLCLB | 6257.4552 | 0 | 0.5 | 0 | Out= Nil, avoid OL on 7490 or 7491 (T280 Drillham to T194 Columboola) 132kV feeder on trip of 7491 or 7490 (T280 Drillham to T194 Columboola) 132kV feeder, Feedback | NIL | Thermal | Qld
Q_STR_7C0K_MEWF_6 | 6250.8658 | 0 | 2.1667 | 0 | Limit 80% to Mt Emerald WF if Stan>=2+Stan+Cal>=3+Glad>=2+(Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% at night), 40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG)(25% if Syncon OFF),Zero otherwise. | Outage | System Strength | Qld
N_MOREESF1_35INV | 6160.8987 | 0 | 0.41667 | 0 | Moree Solar Farm inverter limit of 35. Constraint to violate if Moree Solar Farm inverter availability greater than 35. Swamp out otherwise. DS only | Outage | System Strength | NSW
F_T+NIL_BL_R5 | 6146.3356 | 0 | 102.3333 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available, LoL = 400ms | NIL | FCAS | FCAS
T>T_NWSD_110_1 | 6034.6408 | 1993.1867 | 5 | 0.66667 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752, avoid O/L Scottsdale Tee to Norwood 110kV line on Nil trip, Feedback | Outage | Thermal | Tas
N^^V_DDSM1 | 6025.9713 | 22901.2299 | 14.75 | 22.6667 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | Voltage Stability | NSW
F_MAIN++ML_L6_APD_LD | 5860.7404 | 560.611 | 38.25 | 32.1667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage | FCAS | FCAS
S:VS_PA_SVC_620 | 5847.975 | 10866.8527 | 6.25 | 9.9167 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murraylink upper transfer limit of 620 MW | Outage | Oscillatory Stability | SA
Q_STR_7C0K_SMSF_2 | 5840.8611 | 0 | 3 | 0 | Limit Sun Metals SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
F_Q++LDTW_L60 | 5815.3432 | 0 | 9.4167 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C0K_RUGSF_2 | 5754.5291 | 0 | 1.6667 | 0 | Limit Rugby Run SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
F_T++LREG_0050 | 5743.4279 | 34578.9877 | 94.25 | 285.5833 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
V^T_NIL_9 | 5671.4936 | 13344.4892 | 6.3333 | 24.4167 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL | Voltage Stability | Vic
V>>DDTX2_DDTX3_DDTX1 | 5607.3298 | 0 | 1.25 | 0 | Out= Dederang H2 txfmr, avoid O/L Dederang H3 330/220kV txfmr on trip of Dederang H1 330/220kV txfmr, Feedback | Outage | Thermal | Vic
S>VMLMHNW1 | 5591.6705 | 0 | 5.25 | 0 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | SA
F_T++NIL_MG_RECL_R60 | 5570.0832 | 5881.9943 | 184.3333 | 89 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
Q_STR_7C8C_KIDSF | 5540.1085 | 69989.759 | 10.6667 | 5.5833 | Limit Kidston Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
F_MAIN++NIL_MG_R1 | 5510.9617 | 0 | 17.8333 | 0 | Out = Nil, Raise 1 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS. Requirement capped at 225 MW | Outage | FCAS | FCAS
N>>NIL_8U_86_S | 5350.5363 | 0 | 10.8333 | 0 | Out= NIL, avoid O/L Armidale to Uralla (8U) on trip of Armidale to Tamworth (86) line, Feedback | NIL | Thermal | NSW
VSML_085 | 5347.6899 | 0 | 0.91667 | 0 | Vic to SA on ML upper transfer limit of 85 MW | Outage | Discretionary | Vic
N_AVLSF1_47INV | 5299.8789 | 0 | 0.41667 | 0 | Avonlie Solar Farm inverter limit of 47. Constraint to violate if Avonlie Solar Farm inverter availability greater than 47. Swamp out otherwise. DS only | Outage | System Strength | NSW
F_I+TTS_TG_R60 | 5243.6614 | 13510.8006 | 670.4167 | 695.4167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
Q_STR_7C2K_RRSF_10 | 5235.0361 | 0 | 1.3333 | 0 | Limit Ross River Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
V>>NIL_MLGT_MLGT_A | 5233.9925 | 0 | 4.25 | 0 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | NIL | Thermal | Vic
NRM_NSW1_QLD1 | 5120.3877 | 104730.2175 | 0.75 | 2.4167 | Negative Residue Management constraint for NSW to QLD flow. | NIL | Negative Residue | Negative Residue
F_T+NIL_MG_R6 | 5106.0205 | 576460.7307 | 43.75 | 1839.5 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V^^S_SETB_TBSE_2 | 5101.6765 | 30238.4757 | 2.3333 | 5 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Voltage Stability | SA
T>T_NIL_BL_110_4 | 5066.0098 | 10986.7828 | 6.5833 | 8.6667 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Thermal | Tas
N^^V_DTSS_1 | 5026.5639 | 0 | 3.0833 | 0 | Out = Dapto-Sydney South(11), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>V_460_DYN | 5014.2976 | 1073.722 | 6.5833 | 1.5 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | SA
Q_STR_7C8C_KEP | 4990.1467 | 0 | 4.5 | 0 | Limit Kennedy Energy Park output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
S>>NIL_BWMP_WTTP | 4964.4276 | 2818.3299 | 1.9167 | 0.25 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
F_MAIN+GFT_TG_R60 | 4924.8794 | 291180.4903 | 38 | 114.8333 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>LFPP_PGPA_PGPE | 4899.8034 | 0 | 0.33333 | 0 | Out= Lefevre-Pelican Point 275kV line, avoid O/L Parafield Gardens West-Paralowie 66kV line on trip of Parafield Gardens West-Para 275kV line, Feedback | Outage | Thermal | SA
V>>NIL_SMTX_SMTX_R5 | 4786.2513 | 0 | 12.3333 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 500kV mode, Feedback | NIL | Thermal | Vic
Q_STR_7C0K_MEWF_1 | 4713.877 | 0 | 2.0833 | 0 | No limit to Mt Emerald Wind Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
V::N_MLTX_xxx | 4684.817 | 0 | 7.75 | 0 | Out = Moorabool Transformer 500/220kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::S_PAVC1_SETB | 4635.2574 | 3003.5211 | 8.4167 | 3.3333 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
I_CTRL_ISSUE_TE | 4622.1455 | 1605.6657 | 17.9167 | 6 | DC Link Control Issue Constraint for Terranora | Outage | Other | Other
V>>MLSY_KTTX_SYML_5R | 4617.9699 | 0 | 0.16667 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage | Thermal | Vic
N>>99D_99K_63 | 4548.4236 | 0 | 0.58333 | 0 | Out= Darlington Point to Yanco (99D) 132kV line, avoid O/L Darlington Point to Griffith (99K) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, [Note:Wagga to Darlington Point network solid, X5 trip scheme disarmed, option C OM521] | Outage | Thermal | NSW
Q_STR_7C2K_MEWF_9 | 4518.3405 | 0 | 1.5 | 0 | Limit to Mt Emerald Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_KIDSF_7 | 4460.8687 | 25769.6533 | 10.8333 | 19.5 | Limit to Kidston Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N>>V_NIL_65_66 | 4397.9516 | 136.5806 | 0.5 | 0.083333 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; (Note: constraint is swamped out if TL 64 is O/S) | NIL | Thermal | NSW
S>NIL_PL_GENMAX_YDMD | 4389.1321 | 1125.9306 | 4.1667 | 2.5833 | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating. | NIL | Thermal | SA
S>V_RBNW_RBMWP3 | 4339.2191 | 163.1108 | 5.3333 | 0.33333 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage | Thermal | SA
Q_STR_7C2K_WHTSF_7 | 4332.956 | 18234.1953 | 5.4167 | 13.3333 | Limit to Whitsunday Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_MAIN++BIP_ML_L6 | 4320.5487 | 4.69 | 418.0833 | 1.5833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_MAIN++GFT_TG_R60 | 4313.4082 | 19786.6225 | 116.9167 | 166.25 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
V^^N_CRGR_1 | 4285.6112 | 0 | 6.9167 | 0 | Out = Crookwell to Gullen Range (3H), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S>>BWMP_RBTU_RBPA | 4262.8123 | 4375.1532 | 0.75 | 1.6667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Robertstown-Para 275kV line on trip of Robertstown -Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N_MOREESF1_40INV | 4244.493 | 4876.4468 | 0.33333 | 0.33333 | Moree Solar Farm inverter limit of 40. Constraint to violate if Moree Solar Farm inverter availability greater than 40. Swamp out otherwise. DS only | Outage | System Strength | NSW
N^^V_LTWG_1 | 4238.3963 | 6038.7247 | 2.0833 | 2.25 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
F_I+GFT_TG_R5 | 4223.3742 | 3535.3593 | 684.8333 | 557.75 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
V_MURRAWRWF_FLT_135 | 4180.1822 | 26924.5028 | 0.41667 | 7.25 | Limit Murra Warra Wind Farm 1+2 upper limit to 135 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
NRM_VIC1_NSW1 | 4177.1916 | 123629.6966 | 1 | 2.3333 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue | Negative Residue
Q_STR_7C2K_CLRSF_5 | 4064.8459 | 2961.4852 | 0.33333 | 0.25 | No limit to Clare Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),(80% if Haughton Syncon is OFF),25%(40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise. | Outage | System Strength | Qld
VT_250 | 4057.1902 | 0 | 6.25 | 0 | Vic to Tas on Basslink upper limit of 250 MW | Outage | Discretionary | Vic
S>>BWMP_HUWT_RHBG-T | 4036.6924 | 8236.6707 | 0.66667 | 1.3333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill-Brinkworth 132kV T line on trip of Hummocks-Waterloo 132kV line, Feedback | Outage | Thermal | SA
V^SML_HORC_3 | 4017.0294 | 0 | 20.25 | 0 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
QNTE_ROC | 3978.8741 | 84465.9212 | 44 | 31.75 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | Qld
Q_MIDDLSF1_ZERO | 3927.4562 | 7676.0818 | 2.5833 | 0.58333 | Middlemount Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_Q++MUTW_L5 | 3868.261 | 0 | 11.6667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
V::S_SEVC1_MAXG | 3855.6444 | 10158.7589 | 4.3333 | 1 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
Q_STR_7C0K_MEWF | 3843.4015 | 0 | 2.0833 | 0 | No limit to Mt Emerald Wind farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise. | Outage | System Strength | Qld
N::Q_DM_TW_SVC_KC | 3811.9914 | 0 | 9.3333 | 0 | Out = Dumaresq or Tamworth SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
N>>NIL_966/1_87_S | 3800.1667 | 0 | 0.33333 | 0 | Out=Nil, avoid O/L Metz Tee to Armidale (966/1) kV line on trip of Coffs Harbour to Armidale (87) 330kV line, Feedback | NIL | Thermal | NSW
T>T_NIL_BL_IMP_7CC | 3779.1009 | 11823.9287 | 14.6667 | 12.9167 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
S-BUPV1_0 | 3776.4006 | 7352.1577 | 0.33333 | 0.5 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | Unit Zero | SA
F_S++HYSE_L5 | 3742.7456 | 4630.1343 | 30.6667 | 30.1667 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage | FCAS | FCAS
N_X_MBTE2_A & N_X_MBTE2_B | 3737.2663 | 121.9433 | 49.1667 | 0.41667 | Out= two Directlink cables, NSW to Qld limit | Outage | Unit Zero | NSW
VSML_195 | 3716.3754 | 8434.2478 | 0.33333 | 1.0833 | Vic to SA on ML upper transfer limit of 195 MW | Outage | Discretionary | Vic
N^^V_BADP_1 | 3698.4049 | 7074.9398 | 4 | 4.6667 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
F_T+NIL_BL_R6_1 | 3677.7685 | 0 | 173.6667 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 400ms | NIL | FCAS | FCAS
F_Q++8C_L6 | 3649.1785 | 17492.6259 | 4.1667 | 24.8333 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
S-MWPS2-PV_0 | 3587.5201 | 37505.1227 | 0.41667 | 9.3333 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 2 PV generation of 0 MW | Outage | Unit Zero | SA
V::N_X_SMSC_O2 | 3505.0916 | 526569.5399 | 7.75 | 96.75 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
TVBL_ROC | 3479.9004 | 181035.4268 | 9.5833 | 6.3333 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Tas
S-MWPS3-PV_0 | 3441.3893 | 3733.1051 | 0.33333 | 2.1667 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 3 PV generation of 0 MW | Outage | Unit Zero | SA
S-MWPS1-PV_0 | 3376.9117 | 37046.7326 | 0.33333 | 9.0833 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 1 PV generation of 0 MW | Outage | Unit Zero | SA
N^^V_JNWG_63_X5_1 | 3376.7692 | 238.6665 | 5.6667 | 0.75 | Out = Jindera to Wagga(62) 330kV line, 63 + X5 open, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N^N-X_LS_SVC+96R | 3360.2353 | 0 | 29.5833 | 0 | Out= Lismore SVC + 96R/96L O/S, avoid Voltage collapse on TL (87) trip; [Swamped for 3 DLK cables are O/S Or when ECS is enabled with DLK is exporting to QLD,sets DLK to -29 MW for -29< DLK FLOW<0, checks ETS status & unswamps if O/S) | Outage | Voltage Stability | NSW
F_I+TTS_TG_R5 | 3286.6049 | 4414.8134 | 659.25 | 720.4167 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
V^^N_HWSM_1 | 3284.829 | 0 | 8 | 0 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V::N_SETB_O1 | 3210.2514 | 0 | 8.3333 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
Q_HAMISF1_ZERO | 3201.6488 | 112302.512 | 0.25 | 6.6667 | Hamilton solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S_DLBAT-G_ISL | 3178.665 | 128055.8544 | 1.5 | 1.0833 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Dalrymple Battery (Gen Mode) islanded | Outage | Islanding - Unit | SA
Q_STR_SMSF_ZERO | 3175.8637 | 0 | 0.25 | 0 | Limit 0MW to Sun Metals Solar farm for system strength requirement | Outage | System Strength | Qld
N^N_KKLS_1 | 3166.3559 | 272.1603 | 16 | 1.4167 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
F_Q++85_L6 | 3149.2256 | 0 | 8 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
F_T+NIL_MG_R60 | 3139.6917 | 253800.3875 | 97.8333 | 1860.3333 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V::V_1900 | 3125.2205 | 217.7356 | 0.41667 | 0.25 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Oscillatory Stability | Vic
N>9GM_999_NIL | 3124.5977 | 0 | 0.41667 | 0 | Out= Bango999 WF to Yass 132kV line(9GM), avoid O/L Bango999 to Cowra (999) on trip of Nil, Feedback | Outage | Thermal | NSW
V>>NIL_BABE_KMRC | 3112.7703 | 0 | 2.25 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
F_T++NIL_MG_RECL_R5 | 3061.8146 | 71402.0668 | 132.6667 | 75.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V_KIATAWF_FLT_18 | 3013.4748 | 13746.1819 | 1.5 | 3.0833 | Limit Kiata Wind Farm upper limit to 18 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
Q_STR_32282_CLRSF | 2988.7412 | 1984.7314 | 0.25 | 1.25 | Limit 50% to Clare SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_T+NIL_BL_R60_1 | 2987.465 | 0 | 189.75 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 400ms | NIL | FCAS | FCAS
Q_CLERMSF1_ZERO | 2982.3293 | 948.4943 | 0.91667 | 0.083333 | Clermont Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_WARWSF1_ZERO | 2913.8212 | 75525.6017 | 0.25 | 7.6667 | Warwick Solar Farm 1 upper limit of 0 MW | Outage | Unit Zero | Qld
F_S+MLMO_TL_L60 | 2879.9276 | 0 | 6.25 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage | FCAS | FCAS
N_BROKENH1_ZERO | 2774.1782 | 951452.6471 | 0.33333 | 91.8333 | Broken Hill Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
F_MAIN+NIL_MG_R5 | 2748.5243 | 8342.419 | 378.75 | 1078.5833 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
Q_EMERASF1_ZERO | 2709.9606 | 115033.3944 | 0.25 | 10.75 | Emerald Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>>WERB_BWPA_WTTP | 2707.6223 | 0 | 0.91667 | 0 | Out= Robertstown - MWP4 - Waterloo East O/S(offloads MWP4 SF), avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
N_FINLEYSF_49_INV | 2703.6749 | 186498.2644 | 0.41667 | 1.3333 | Finley Solar Farm inverter limit of 49. Constraint to violate if Finley Solar Farm inverter availability greater than 49. Swamp out otherwise. DS only | Outage | System Strength | NSW
N>NIL_947_94T | 2637.717 | 57353.3966 | 0.58333 | 5.0833 | Out= Nil, avoid O/L Wellington to Orange North (947) on trip of Molong to Orange North (94T), Feedback | NIL | Thermal | NSW
V^^N_SDUT_1 | 2613.2952 | 34268.3677 | 6.4167 | 2.25 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N>>NIL_DPTX_LV | 2581.7834 | 50450.9235 | 0.75 | 0.33333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | Thermal | NSW
Q_YARANSF1_37MW_N-1 | 2566.5791 | 109572.8032 | 1 | 12.5 | Limit Yarrenlea Solar Farm to 37 MW when feeder 733/1 or 733/3 or 734/1 or 734/3 (T10 Yarranlea to H14 Middle Ridge) trip, Swamp when the feeders are in service. DS formulation only | NIL | Unit Zero | Qld
V_SV_MLMO_NETT | 2566.452 | 0 | 1.5 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW | Outage | FCAS | Vic
Q_RGBYRSF1_ZERO | 2543.586 | 10290.1982 | 0.16667 | 0.75 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V>>S_MWP3RB_NWRB1 | 2535.4271 | 0 | 0.5 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L North West Bend-Roberstown #1 132kV line on Nil trip, Feedback | Outage | Thermal | SA
V>>NIL_SMTX_SMTX_R2 | 2531.7441 | 0 | 5.5833 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 220kV mode, Feedback | NIL | Thermal | Vic
S>>TBTU_TBTU_TBMO | 2506.0316 | 0 | 4.5833 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of remaining Tailem Bend-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
T>T_NIL_BL_IMP_7C | 2496.9931 | 9098.9154 | 10.5 | 13.4167 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
Q_COLUMSF1_ZERO | 2471.9842 | 0 | 1.75 | 0 | Columboola Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_Q++85_L60 | 2443.086 | 0 | 7.5833 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
F_T++NIL_WF_TG_R60 | 2418.8924 | 1646.3629 | 153.3333 | 29.8333 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
N_FINLEYSF_80INV | 2413.3789 | 0 | 0.25 | 0 | Finley Solar Farm inverter limit of 80. Constraint to violate if Finley Solar Farm inverter availability greater than 80. Swamp out otherwise. DS only | Outage | System Strength | NSW
V::N_SETB_O2 | 2408.5915 | 0 | 6.4167 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
V^^S_MLSY_3 | 2390.027 | 0 | 3.5 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage | Voltage Stability | Vic
S>>NIL_TBCG_TBTU_1 | 2358.0475 | 817.3915 | 0.16667 | 0.58333 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | Thermal | SA
N::Q_8C8J_TNT_N-2 | 2342.9889 | 0 | 1.1667 | 0 | Out = Nil, NSW to Qld Transient Stability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | NSW
S^NIL_CRK_VCS_STATUS | 2315.6842 | 147003.3528 | 1.6667 | 34.8333 | Out= Nil, upper limit for Cathedral Rocks WF based on Mt Millar Voltage Control System (VCS) availability, (Note: CRK <=55 MW when VCS OFF; CRK<= 60 MW when VCS ON) | NIL | Voltage Stability | SA
V::S_RBTU_SETB | 2310.5076 | 0 | 1.8333 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Transient Stability | SA
Q_STR_7C2K_MEWF_14 | 2274.6767 | 0 | 1.1667 | 0 | Limit Mt Emerald WF to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),(80% if Haughton Syncon ON,100% at night),25%(40% if Haughton Syncon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG),Zero otherwise. | Outage | System Strength | Qld
V^^S_NIL_MAXG_xxx | 2271.8215 | 2219.8773 | 2.5 | 1.4167 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Voltage Stability | SA
Q_STR_32282_MEWF | 2257.0818 | 59630.5331 | 0.75 | 3.6667 | Limit 50% to Mt Emerald WF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
S>V_460 | 2237.9527 | 430.4155 | 3.9167 | 0.91667 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage | Thermal | SA
F_Q++MUTW_R60 | 2226.7087 | 0 | 3.3333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
N::Q_BWTX_KC | 2225.4869 | 0 | 3.1667 | 0 | Out= Bayswater 500/330kV tie Tx, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
T::T_GTHA_2 | 2212.1706 | 0 | 6.75 | 0 | Out = George Town to Hadspen 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage | Transient Stability | Tas
N::Q_ARSR_1 | 2208.2942 | 0 | 6.25 | 0 | Out= Armidale - Saphhire (8E) 330kV line, NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | Transient Stability | NSW
S:V_PASVC_420OSC_AT | 2199.3035 | 0 | 1.6667 | 0 | Out = one Para SVC, Upper transfer limit of 420 MW on SA to VIC on Heywood, Active only when I25 mode cannot be monitored. | Outage | Oscillatory Stability | SA
F_T+NIL_MG_RECL_R5 | 2198.2467 | 16477.7177 | 247.5 | 1277.4167 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>X-WTTP+CB_1 | 2197.8289 | 0 | 0.16667 | 0 | Out= Waterloo-Templers 132kV line + associated line CBs O/S, avoid O/L Snowtown-Bungama T 132kV line on trip of Mintaro-Waterloo 132kV line(this offloads Hummocks-Waterloo 132kV line), Feedback | Outage | Thermal | SA
T^V_HAPM_220_1 | 2196.4084 | 0 | 2.9167 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage | Voltage Stability | Tas
N_WSTWYSF_ZERO | 2195.8861 | 0 | 0.33333 | 0 | West Wyalong SF upper limit of 0 MW | Outage | Unit Zero | NSW
S>LFPP_PGPA_PGPS | 2167.2451 | 0 | 0.16667 | 0 | Out= Lefevre-Pelican Point 275kV line, avoid O/L Parafield Gardens West-Parafield Gardens 66kV line on trip of Parafield Gardens West-Para 275kV line, Feedback | Outage | Thermal | SA
Q_STR_7C0K_WHTSF_1 | 2163.981 | 0 | 0.91667 | 0 | No limit to Whitsunday Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
N_NEWENSF1+2_100-INV | 2156.5067 | 0 | 1.0833 | 0 | New England Solar inverter limit of 100. Constraint to violate if New England Solar inverter availability greater than 100. Swamp out otherwise. DS only | Outage | System Strength | NSW
V>>N_NIL_65 | 2106.9449 | 10104.6593 | 3.9167 | 10.25 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Thermal | Vic
F_T++NIL_MG_R6 | 2104.2768 | 14290.9587 | 47.4167 | 13.5 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL | FCAS | FCAS
N>NIL_973 | 2102.7411 | 0 | 0.16667 | 0 | Out= Nil, avoid O/L Bango973 to Cowra (973) on trip of Nil, Feedback | NIL | Thermal | NSW
V>>DBT_DDTX3_DDTX | 2084.15 | 0 | 0.41667 | 0 | Out = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage Schemes), avoid O/L Dederang H3 330/220kV transformer for loss of Dederang H1 or H2 330/220kV transformer, feedback | Outage | Thermal | Vic
V^^S_TBCB94_35_SETB | 2068.7679 | 0 | 11.5 | 0 | Out= Tailem Bend 275kV CB6594 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Voltage Stability | SA
Q>NIL_757_758_ECS | 2060.1726 | 1070285.7186 | 4.9167 | 40.8333 | Out= Nil, ECS for managing Mudgeeraba to Terranora (757 or 758) 110kV lines, Summer and Winter ECS ratings selected by SCADA status | NIL | Thermal | Qld
F_V_APD01_R5 | 2059.8648 | 0 | 47.0833 | 0 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
CA_SYDS_52C88A79_1 | 2056.7371 | 0 | 4.25 | 0 | Constraint Automation, O/L 65:LSM1:I:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
N>>24_93_90 | 2056.0469 | 0 | 0.25 | 0 | Out = Eraring to Vales Point (24), avoid O/L Eraring to Newcastle (93) on trip of Eraring to Newcastle (90) line, Feedback | Outage | Thermal | NSW
N>947+94P_94K_1 | 2054.0659 | 0 | 0.25 | 0 | Out= Wellington to Orange North (947) 132kV line + Manildra to Molong (94P) 132kV, avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | Outage | Thermal | NSW
S>WT-BUS_MNWT_SNBG-T | 2028.756 | 0 | 0.91667 | 0 | Out= Waterloo 132kV South bus outage (this offloads TX 5), avoid O/L Snowtown-Bungama 132kV line on trip of Mintaro-Waterloo 132kV line (this offloads Hummocks-Waterloo 132kV line), Feedback | Outage | Thermal | SA
F_MAIN+APD_TL_L6 | 2021.7613 | 14394.4149 | 94.8333 | 830.1667 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
Q>N-MUTE_758 | 2015.0314 | 179.4182 | 4.4167 | 4.5833 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
N^^N_NIL_1 | 1958.675 | 110996.6381 | 1.4167 | 1.8333 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | Voltage Stability | NSW
T^V_NIL_8 | 1944.2413 | 271549.5851 | 3.5 | 9 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Voltage Stability | Tas
S:V_XPAVC_310 | 1931.3173 | 22045.8774 | 8 | 26.1667 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
NQ_750_TEST | 1907.4001 | 0 | 4 | 0 | NSW to Qld on QNI upper transfer limit of 750 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | NSW
V_GANWRSF_ISL_0 | 1902.6354 | 6108.5025 | 0.16667 | 0.5 | Gannawarra Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V::S_RBTU_MAXG_2 | 1875.8189 | 0 | 1.6667 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
Q_STR_32282_RRSF | 1870.9849 | 1416.2127 | 0.58333 | 0.91667 | Limit 50% to Ross River SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_T+FARE_N-2_TG_R6_2 | 1842.6588 | 5764.5577 | 0.83333 | 5.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage | FCAS | FCAS
Q_STR_7C0K_KEP_1 | 1840.2079 | 0 | 2.25 | 0 | No limit to Kennedy Energy Park if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
V_GANWR_BAT_L_FLT_0 | 1824.3786 | 0 | 0.25 | 0 | Limit Gannawarra Battery (Load Component) upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>>MKRB_CNRB_WEMWP4 | 1823.1125 | 6312.8418 | 2.8333 | 4.25 | Out= Mokota-Robertstown 275kV line, avoid O/L Morgan Whyalla 4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage | Thermal | SA
F_T++FA_B_N-2_TG_R6 | 1810.6114 | 0 | 8 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V>>RCWE_DPTX_ARWB | 1777.1795 | 0 | 4.75 | 0 | Out= Any 220kV line section between Red Cliffs and Wemen, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Ararat to Waubra to Ballarat 220kV line, Feedback | Outage | Thermal | Vic
N>>964_8U_86_S | 1747.1205 | 0 | 14.1667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Armidale to Uralla (8U) on trip of Armidale to Tamworth (86) line, Feedback | Outage | Thermal | NSW
F_MAIN+BIP_ML_L1 | 1745.72 | 0 | 12.5833 | 0 | Out = Nil, Lower 1 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS. Requirement capped at 125 MW | Outage | FCAS | FCAS
S:VS_700_HY_TEST_DYN | 1742.9066 | 0 | 3.5 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
V::S_TBEBUS_SETB | 1726.2489 | 0 | 2.4167 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage | Transient Stability | SA
F_MAIN+GFT_TG_R6 | 1725.0416 | 7476.4549 | 11.5833 | 40.3333 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
T:T_LIPM_1 | 1697.2326 | 213.2373 | 3.75 | 0.5 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South). Swamp if no Gordon units online. | Outage | Transient Stability | Tas
N>947_94K1 | 1685.3507 | 0 | 0.16667 | 0 | Out= Wellington to Orange North (947) 132kV line, avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | Outage | Thermal | NSW
Q_STR_32282_HASF | 1681.5349 | 3962.0705 | 0.75 | 1.3333 | Limit 50% to Haughton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
QNI_SOUTH_1000_DYN | 1681.415 | 0 | 4.25 | 0 | QLD to NSW on QNI upper transfer limit of 1000 MW, dynamic headroom with Max calc on the QNI, DS formulation only. | Outage | Transient Stability | Qld
N_METZSF_43 | 1680.1724 | 0 | 0.41667 | 0 | Metz Solar farm upper limit of 43 MW | Outage | System Strength | NSW
V_MOORBWF_ZERO | 1664.4005 | 0 | 0.41667 | 0 | Moorabool Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
CA_SYDS_52F01146_1 | 1657.3903 | 0 | 0.16667 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
V::N_HYTR_O1 | 1651.3078 | 2790.317 | 3.6667 | 1.4167 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
Q_STR_7C2K_CLRSF_7 | 1627.5084 | 12673.56 | 2.8333 | 15.8333 | Limit to Clare Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
VS_250 | 1598.4615 | 4136.5407 | 2.8333 | 3.9167 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Discretionary | Vic
T>T_GTHA_IMP_4N | 1574.6956 | 0 | 1.9167 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
S_DLBAT-L_ISL | 1564.1899 | 45028.9934 | 1.1667 | 0.5 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Dalrymple Battery (Load Mode) islanded | Outage | Islanding - Unit | SA
N>>81_964_84 | 1556.7177 | 0 | 0.91667 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tamworth (84) line,(Note: Swamps if 964 O/S) | Outage | Thermal | NSW
V_ELAINEWF_ZERO | 1546.1441 | 27685.6741 | 0.66667 | 13.4167 | Elaine Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
T>T_NIL_BL_220_6B | 1530.704 | 0 | 3 | 0 | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Thermal | Tas
S_BIPS_ZERO | 1529.8901 | 0 | 0.33333 | 0 | Barker Inlet upper limit of 0 MW | Outage | Unit Zero | SA
V_T_FCSPS_RAMP | 1523.746 | 0 | 1.8333 | 0 | Ramp down (200 MW per DI) Basslink (Vic to Tas) to 144 MW for outage of FCSPS | Outage | Ramping | Vic
N::V_DDSM_UTMS | 1493.5126 | 2448.0937 | 0.25 | 0.41667 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit for trip of Upper Tumut - Murray (65) line | Outage | Transient Stability | NSW
V^^S_RBPA_SETB | 1490.1296 | 0 | 0.41667 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Voltage Stability | SA
V_STOCKYH_ZERO | 1479.2167 | 8454.7822 | 0.83333 | 0.66667 | Stockyard Hill wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
F_Q++BCDM_R6 | 1478.2244 | 32.45 | 3.6667 | 1 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
V_MTGELIBRAND_66 | 1472.3963 | 0 | 2.25 | 0 | Mt Gelibrand wind farm upper limit of 66 MW | Outage | Discretionary | Vic
N>>99K_99D_63 | 1472.0345 | 0 | 0.33333 | 0 | Out= Darlington Point to Griffith (99K) 132kV line, avoid O/L Darlington Pt to Yanco (99D) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,(Note: assumed X5 trip scheme disarmed & Wagga to Darlington Point network solid, option C on OM521) | Outage | Thermal | NSW
Q^^N_TW+LS_SVC_SRAR | 1443.5927 | 0 | 10.3333 | 0 | Out = Tamworth SVC and Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
S-MAPS2-PV_0 | 1403.0187 | 1115.6693 | 1.9167 | 0.33333 | Discretionary upper limit for SA WATER Mannum Adelaide Pumping Station No 2 PV (Palmer) generation of 0 MW | Outage | Unit Zero | SA
N_SUNRSF1_ZERO | 1384.6828 | 184413.8491 | 0.25 | 22.25 | Sunraysia 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N^^Q_MIMR_TWO_B1 | 1377.1685 | 0 | 0.91667 | 0 | Out = Two parallel feeders between R4 Millmerran to H14 Middle Ridge (9914+9915 or 9908+9907), avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
F_Q++LDTW_L5 | 1376.1665 | 0 | 7.6667 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
S>RBTX2_RBTX1_WEMWP4 | 1363.6848 | 0 | 4.6667 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage | Thermal | SA
S>>CGTB1_TUTB_MOTB | 1321.9179 | 41.2225 | 1.75 | 0.91667 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
Q^^N_LS_SVC_SRAR | 1319.6726 | 0 | 7.5833 | 0 | Out = Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
N_WALGR_BAT_G_ZERO | 1318.0529 | 0 | 0.41667 | 0 | Wallgrove Battery (Generation Component) upper limit of 0 MW | Outage | Unit Zero | NSW
V::S_PAVC1_MAXG | 1316.9756 | 0 | 1.6667 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | Transient Stability | SA
V>>X5_WBBA_KGBE | 1316.8088 | 0 | 3.5 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
F_MAIN+TTS_TG_R60 | 1312.7571 | 3688.1909 | 26.9167 | 26.5833 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V::S_NIL_TBSE_1 | 1304.1047 | 2468.3893 | 1.3333 | 2.9167 | Out = Nil(Both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (Both South East Capacitors (61 and 62) Available). | NIL | Transient Stability | SA
T>T_PMSH_IMP_4F | 1295.7737 | 0 | 2.0833 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
F_T+FA_B_N-2_RREG | 1294.4178 | 0 | 9.4167 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, Bastyan, John Butters, Reece 1 & 2, and Tribute Raise Regulation Requirement = 0 | Outage | Unit Zero - FCAS | FCAS
F_T++NIL_ML_L5 | 1272.522 | 224.28 | 164.75 | 11.5 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL | FCAS | FCAS
V>>KMCB_BABE_KMRC | 1254.1437 | 0 | 0.41667 | 0 | Out= Kiamal 220kV CB (one or more MR2B or 7422A or 7422B), avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | Outage | Thermal | Vic
Q_STR_7C2K_CLRSF_10 | 1245.9652 | 0 | 0.75 | 0 | Limit Clare Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
F_Q++86_L5 | 1245.7845 | 0 | 10.6667 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
N_GNNDHSF1_82INV | 1243.9595 | 0 | 0.25 | 0 | Gunnedah Solar Farm inverter limit of 82. Constraint to violate if Gunnedah Solar Farm inverter availability greater than 82. Swamp out otherwise. DS only | Outage | System Strength | NSW
F_I+TTS_TG_R6 | 1241.505 | 19810.4101 | 250.0833 | 412.4167 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
V>>ARWB_DPTX_KGBE | 1229.9058 | 0 | 2.25 | 0 | Out= Any 220kV line section between Ararat and Ballarat, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
N>NIL-BHTX_BHTX_NIL | 1226.8101 | 0 | 0.16667 | 0 | Out= NIL with one Broken Hill 22/220kV TX switched O/S (Note: only one TX can be I/S for system normal), avoid O/L remaining Broken Hill 22/220kV TX on trip of Nil, (Note: Swamped when both TX1&2 are I/S, otherwise unswamped; Assumed 22kV CB 2112 I/S) | NIL | Thermal | NSW
F_T++NIL_WF_TG_R5 | 1143.4664 | 678.7516 | 130.8333 | 41.1667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
V>>NIL_MLGT_MLGT_B | 1142.4913 | 0 | 0.33333 | 0 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 220 kV mode, Feedback | NIL | Thermal | Vic
N_WRWSF_060 | 1139.8043 | 0 | 0.083333 | 0 | White Rock wind farm and White Rock solar farm upper limit of 60 MW | Outage | System Strength | NSW
Q_STR_7C2K_KIDSF_10 | 1134.6825 | 0 | 1.5833 | 0 | Limit Kidston Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C0K_RRSF_2 | 1131.3002 | 0 | 2.8333 | 0 | Limit Ross River SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
V_MURRAWR2_ZERO | 1130.1007 | 0 | 0.083333 | 0 | Murra Warra 2 wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
T>T_GTSH_IMP_4K | 1120.9734 | 0 | 2.75 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
S>>X_RBTU+RBTX_12 | 1119.2744 | 0 | 0.16667 | 0 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Blyth West-Munno Para275kV line on trip of remaining Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>X-MNWT+CB_01 | 1117.3746 | 0 | 0.083333 | 0 | Out= Mintaro-Waterloo 132kV line + associated line CBs O/S, avoid O/L Snowtown-Bungama T 132kV line on trip of Waterloo -Templers 132kV line (this offloads Hummocks-Waterloo 132 kV line), Feedback | Outage | Thermal | SA
S>>V_NIL_NIL_RBMW3 | 1115.1999 | 476.547 | 1.25 | 0.5 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL | Thermal | SA
V>>EPTT_DDSM_DDSM | 1112.5714 | 0 | 0.83333 | 0 | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to South) for loss of the parallel line, 15 min rating, feedback. Swamp if VBB/SIPS available | Outage | Thermal | Vic
N_MOREESF1_ZERO | 1110.186 | 3295.59 | 0.083333 | 0.25 | Moree Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_COLMBSF_60_INV | 1105.0114 | 4335.2578 | 0.083333 | 0.33333 | Coleambally Solar Farm inverter limit of 60. Constraint to violate if Coleambally Solar Farm inverter availability greater than 60. Swamp out otherwise. DS only | Outage | System Strength | NSW
N>>64_07_03 | 1093.2998 | 0 | 0.083333 | 0 | Out = LowerTumut-UpperTumut (64), avoid O/L Lower Tumut to Canberra (07) on trip of Lower Tumut to Yass (03) line, Feedback | Outage | Thermal | NSW
S>>BRTW_BWPA_WTTP | 1092.751 | 15335.9192 | 1.3333 | 1.3333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V:T_HAPM_BL_1 | 1069.4769 | 0 | 2.25 | 0 | Out = Hadspen to Palmerston 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to Palmerston 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
N>>NIL_964_88_S | 1068.0393 | 0 | 0.75 | 0 | Out= NIL, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL | Thermal | NSW
Q_SRSF1_ZERO | 1063.736 | 0 | 0.083333 | 0 | Susan River Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
N_GNNDHSF1_63INV | 1060.3554 | 0 | 0.083333 | 0 | Gunnedah Solar Farm inverter limit of 63. Constraint to violate if Gunnedah Solar Farm inverter availability greater than 63. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q^^N_AR+LS_SVC_SRAR | 1058.2497 | 0 | 3.5833 | 0 | Out = Lismore SVC + Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
N_DARLSF_FLT_193 | 1053.76 | 19097.322 | 0.083333 | 1.3333 | Limit Darlington Pt Solar Farm upper limit to 193 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>>NIL_4_61_N | 1052.4291 | 0 | 0.25 | 0 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Crookwell to Bannaby (61) line, Feedback | NIL | Thermal | NSW
S>>RBTU_RBPA_BWMP | 1045.3426 | 0 | 0.16667 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Blyth West-Munno Para 275kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
S-MBPS2-PV_0 | 1032.5756 | 0 | 0.75 | 0 | Discretionary upper limit for SA WATER Murray Bridge (Hahndorf ) - Onkaparinga Pipeline Pumping Station 2 PV of 0 MW | Outage | Unit Zero | SA
V_BULGWF_ISL_0 | 1032.1697 | 0 | 0.083333 | 0 | Bulgana Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
F_Q++BCDM_R60 | 1029.8353 | 137.2522 | 3.75 | 1.5 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
N_COLEASF1_FLT_50 | 1020.4639 | 59985.7027 | 0.083333 | 4.5833 | Limit Coleambally solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_MWWF_0_WT12 | 1019.1298 | 0 | 1.25 | 0 | Limit Murra Warra Wind Farm upper limit to 0 MW if Murra Warra wind farm turbine collector group 1 and/or 2 generating. Constraint swamp out if only turbine collector group 3 and/or 4 generating. DS only | Outage | System Strength | Vic
V^^S_SEVC1_MAXG | 1018.6018 | 1677.1121 | 1.8333 | 0.75 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
S-MWPS4-PV_0 | 977.6438 | 35786.3552 | 0.083333 | 7.0833 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 4 PV generation of 0 MW | Outage | Unit Zero | SA
S::V_TBSE_TBSE | 962.7814 | 148770.4682 | 2.4167 | 106.9167 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
Q_STR_7C2K_KBWF_8 | 956.9926 | 0 | 0.083333 | 0 | Limit to Kaban Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Haughton Syncon ON, Zero otherwise. | Outage | System Strength | Qld
N_METZSF_34INV | 951.6069 | 0 | 0.16667 | 0 | Metz Solar Farm inverter limit of 34. Constraint to violate if Metz Solar Farm inverter availability greater than 34. Swamp out otherwise. DS only | Outage | System Strength | NSW
N^^V_MLNK_ARWBBA | 945.535 | 535.1539 | 1.6667 | 1.3333 | Out = Murraylink, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | Outage | Voltage Stability | NSW
N>BWLD33_BWLD34 | 937.0969 | 0 | 0.5 | 0 | Constraint Automation, O/L 34:LN34:Z:330@BAYSWATR@NSW for CTG LNPI on trip of BAYSWATR-LIDDELL 33 330KV LINE. Generated by RTCA[EMS] | Outage | Thermal | NSW
S:V_PA_SVC_420 | 932.8333 | 1585322.7456 | 0.5 | 99.5 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
VSML_150 | 931.5643 | 0 | 0.083333 | 0 | Vic to SA on ML upper transfer limit of 150 MW | Outage | Discretionary | Vic
V_SH_DD_MAC_FLT_965 | 899.0662 | 0 | 0.083333 | 0 | Limit Stockyard Hill, Dundonnell and Macarthur wind farm total output to 965 MW if Heywood flow is above 500 MW (SA to VIC direction). Swamp otherwise. This is to manage voltage oscillation. | NIL | System Strength | Vic
F_Q++NIL_R60 | 898.7841 | 201.334 | 2.75 | 0.16667 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL | FCAS | FCAS
N>>V_NIL_66_65 | 891.363 | 1774.5976 | 0.16667 | 0.33333 | Out = Nil, avoid Lower Tumut to Murray(66) using 15 mins rating O/L on Upper Tumut to Murray(65) trip; (Note: Swamped when TL 64 is O/S) | NIL | Thermal | NSW
F_T++FARE_N-2_TG_R6 | 889.8755 | 103.6889 | 8.1667 | 0.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S>NIL_NIL_MHNW2 | 888.7364 | 0 | 0.083333 | 0 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
N_NEWENSF1+2_201-INV | 886.5393 | 0 | 0.75 | 0 | New England Solar inverter limit of 201. Constraint to violate if New England Solar inverter availability greater than 201. Swamp out otherwise. DS only | Outage | System Strength | NSW
T>T_SH_TX | 877.5419 | 0 | 0.75 | 0 | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Thermal | Tas
F_Q++BCDM_L5 | 868.6874 | 297.3008 | 5.25 | 1.3333 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
S:VS_XPAVC_460 | 834.0985 | 0 | 1.3333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood and Murraylink combined upper transfer limit of 460 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
N_METZSF_20INV | 829.8296 | 0 | 0.41667 | 0 | Metz Solar Farm inverter limit of 20. Constraint to violate if Metz Solar Farm inverter availability greater than 20. Swamp out otherwise. DS only | Outage | System Strength | NSW
F_T+FASH_1_RREG | 828.0428 | 0 | 0.083333 | 0 | Out = Farrell to Sheffield No.1 line; Bastyan, John Butters, Tribute and Reece 1, 2 and Mackintosh unavailable for raise regulation | Outage | Unit Zero - FCAS | FCAS
V::S_NIL_SETB_SECP_1 | 806.5722 | 119514.3022 | 0.91667 | 5.1667 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | Transient Stability | SA
V>>N-BUDP_2N | 800.2584 | 0 | 1 | 0 | Out= Buronga-(X5), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, (Note: assumed Darlington-Wagga 132kV mesh operated CLOSED) | Outage | Thermal | Vic
T^T_NIL_BL_6 | 797.2724 | 0 | 0.25 | 0 | Outage = Nil, avoid voltage instability or violations for loss of a Liapootah-Waddamana-Palmerston 220 kV line | NIL | Voltage Stability | Tas
S>WERB_WTTP_CLNBR | 793.9337 | 0 | 0.16667 | 0 | Out= Robertstown -MWP4 -Waterloo East O/S(offloads MWPF SF), avoid O/L Claire North-Brinkworth 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | Thermal | SA
F_Q++8E_L60 | 788.0308 | 9282.8411 | 4 | 24.3333 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
T>T_HA_TX | 786.7003 | 0 | 1.75 | 0 | Out = Hadspen 220/110 kV txfmr, avoid O/L Palmerston 220/110 kV txfmr (flow from 220 kV to 110 kV) on trip of remaining Hadspen 220/110 kV txfmr, feedback | Outage | Thermal | Tas
Q>>BCCP_CLWU_RGLC | 785.5169 | 0 | 0.25 | 0 | Out= Bouldercombe to Calliope River (812), avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
SV_420_DYN | 784.7802 | 220181.6105 | 0.33333 | 160.5833 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 50 MW | Outage | Discretionary | SA
F_T+NIL_WF_TG_R5 | 781.3781 | 18992.7423 | 90.3333 | 1013.9167 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T++FASH_1_TG_R6 | 780.3193 | 0 | 2.75 | 0 | Out= Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
N::Q_AR_VC_KC | 778.7054 | 0 | 1.5 | 0 | Out= Armidale SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
Q_STR_32282_KIDSF | 766.7318 | 1345.3126 | 0.66667 | 1.0833 | Limit 50% to Kidston SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
CA_SYDS_52C76ACC_1 | 761.3015 | 0 | 1.25 | 0 | Constraint Automation, O/L 65:LSM1:I:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR2] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
F_Q++8C_L60 | 750.6719 | 14609.1328 | 2.8333 | 24.5 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C8C_WHTSF | 726.7629 | 10797.0614 | 2.5833 | 1 | Limit Whitsunday Solar Farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone and Kareeya generators, Zero if it does not meet minimum generator online. | Outage | System Strength | Qld
T>T_FASH_3_N-2 | 719.4303 | 0 | 2.4167 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV line (flow to Burnie) for loss of both Farrell to Sheffield 220 kV lines | Outage | Thermal | Tas
N>>964_88_84_S | 698.3587 | 191.0389 | 1.4167 | 0.5 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | Outage | Thermal | NSW
S>>X_RBTU+RBTX_01 | 674.476 | 0 | 0.16667 | 0 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown-Tungkillo 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
N_MOREESF1_55INV | 670.5887 | 0 | 0.083333 | 0 | Moree Solar Farm inverter limit of 55. Constraint to violate if Moree Solar Farm inverter availability greater than 55. Swamp out otherwise. DS only | Outage | System Strength | NSW
V:T_HAGT_BL_1 | 665.5038 | 0 | 2 | 0 | Out = Hadspen to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to George Town 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
N::Q_MUTW_1 | 662.9362 | 0 | 2.75 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | Transient Stability | NSW
F_MAIN+TTS_TG_R6 | 661.8894 | 425.6723 | 12.4167 | 6.1667 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N>N-BAMB_132_OPEN_B | 649.1576 | 0 | 4.6667 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage | Thermal | NSW
N^^Q_ARTW_B1 | 642.4707 | 60857.5418 | 2.4167 | 15.6667 | Out = Armidale to Tamworth (85 or 86 or 8U), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | Voltage Stability | NSW
V::N_ROSM_O1 | 636.5928 | 1585.0939 | 1.0833 | 1.5 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
F_MAIN++GFT_TG_R6 | 632.1118 | 3463.8964 | 20 | 55.8333 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_MAIN++GFT_TG_R5 | 628.3728 | 850.6331 | 122 | 95.8333 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
V^^S_RBPA_MAXG | 622.9047 | 0 | 0.16667 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA | Outage | Voltage Stability | SA
N::Q_MIMR_TWO_KC | 615.3415 | 0 | 0.5 | 0 | Out = Two parallel feeders between R4 Millmerran to H14 Middle Ridge (9914+9915 or 9908+9907), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
S>WERB_WTTP_STBG-T | 614.5823 | 0 | 0.083333 | 0 | Out= Robertstown - MWP4 - Waterloo East O/S(offloads MWP4 SF), avoid O/L Snowtown-Bungama T 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | Thermal | SA
F_Q++8U_L6 | 613.4758 | 0 | 1 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
V^S_HYCP | 606.9472 | 8150.7335 | 1 | 14.5833 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL | Voltage Stability | Vic
N>>99J_99D_63 | 602.7646 | 0 | 0.58333 | 0 | Out= Griffith to Yanco (99J) 132kV line, avoid O/L Darlington Point to Yanco (99D) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, (Note:X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521) | Outage | Thermal | NSW
S:VS_700_HY_TEST | 593.3186 | 0 | 1.25 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
V:T_SHGT_BL_1 | 584.831 | 0 | 1 | 0 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
V>>N-62_65_66_RADIAL | 578.4689 | 0 | 1.9167 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | Vic
N>WLTX_94T_WLTX | 572.2327 | 1135.1008 | 0.083333 | 0.25 | Out= one of the Wellington 132/330kV Transformers, avoid O/L on Molong to Orange North (94T) on trip of remaining Wellington 132/330kV transformer, Feedback | Outage | Thermal | NSW
S>>RBTX_BWPA_WTTP | 568.2734 | 2863.5634 | 0.25 | 1.3333 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V::S_RBPA_SETB | 560.5297 | 0 | 0.41667 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Transient Stability | SA
N>>NIL_5_3J_N | 559.7663 | 0 | 0.33333 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) using 15 mins rating on trip of Yass to Gullen Range (3J) line, Feedback | NIL | Thermal | NSW
Q>NIL_SRMB_M020/1 | 541.7878 | 6078.2159 | 2 | 1.3333 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Thermal | Qld
N_SAPHWF1_28WT | 541.0354 | 0 | 0.25 | 0 | Constraint to violate if Sapphire WF turbines On greater than 28. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
S>BWMP_MKRB_CNRB | 537.6851 | 0 | 0.083333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Canowie-Robertstown 275kV on trip of Mokota-Robertstown 275kV line(this offloads Belalie-Mokota 275kV line and trips Hallet 2 Hill WF) , Feedback | Outage | Thermal | SA
S:V_460 | 534.0362 | 0 | 0.66667 | 0 | Maintain maximum transfer limit of 460 MW on Heywood IC from SA to VIC to avoid oscillatory instability | Outage | Oscillatory Stability | SA
QNTE_OSCILLATE | 532.8937 | 3592.1323 | 1.0833 | 2.9167 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Discretionary | Qld
V^^N_2_6X_3J_1 | 525.6258 | 0 | 1.5833 | 0 | Out = Ravine-Yass or Upper Tumut to Ravine (2 or 6X) 330kV line and Gullen Range to Yass (3J), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N^^V_2+3J+DDSM_1 | 524.1479 | 0 | 1.75 | 0 | Out = Ravine-Yass (2)/Upper Tumut-Ravine (6X) + Yass-Gullen Range (3J) + one Dederang-South Morang line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q>>NIL_BCCP_RGLC | 523.3445 | 86959.9101 | 1.25 | 25.8333 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
Q_KEP-HYB_21MW | 512.7097 | 0 | 0.33333 | 0 | Kennedy Energy Park upper limit of 21MW | Outage | Discretionary | Qld
N_METZSF_25INV | 500.3103 | 0 | 0.16667 | 0 | Metz Solar Farm inverter limit of 25. Constraint to violate if Metz Solar Farm inverter availability greater than 25. Swamp out otherwise. DS only | Outage | System Strength | NSW
V>>MLSY_KTDPT_SYML | 495.7631 | 0 | 0.5 | 0 | Out = Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid O/L Keilor to Deer Park 220 kV line on trip of remaining Moorabool to Sydenham 500 kV line, feedback | Outage | Thermal | Vic
F_T+NIL_MG_R5 | 492.5788 | 21051.3262 | 21.3333 | 1727.75 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>>NIL_RBTX_RBTX_1 | 490.1245 | 0 | 2.25 | 0 | Out= Nil, avoid O/L of one Robertstown 275/132kV TX on trip of other Robertstown 275/132kV TX, Feedback | NIL | Thermal | SA
CA_BRIS_542A136B_1 | 486.2867 | 0 | 3.8333 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage | Thermal | Constraint Automation
Q^^N_NIL_SRAR | 481.3164 | 9113504.9277 | 3.3333 | 319.6667 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Voltage Stability | Qld
T_T_FASH_HM_OPEN_2 | 473.0301 | 0 | 1.5833 | 0 | Out = one Farrell to Sheffield 220kV line, West Coast 220/110 kV parallel open, Farrell 220 kV bus not split, limit West Coast gen >= 90% of West Coast load | Outage | Other | Tas
F_N_WALGR_BAT_G_RREG | 472.4127 | 0 | 0.66667 | 0 | Out= Nil, Wallgrove BESS (generation component) Raise Regulation Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T++NIL_MG_R5 | 459.5757 | 1632.1514 | 9.1667 | 59.4167 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL | FCAS | FCAS
T>T_HAPM_IMP_4N | 458.9711 | 0 | 0.83333 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
F_Q++8U_L60 | 453.2595 | 0 | 0.75 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
N^^V_LTUT_1 | 446.5095 | 0 | 0.66667 | 0 | Out = Lower to Upper Tumut (64) 330kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V>>BAML1_ELML_BAML2 | 432.7869 | 0 | 2.6667 | 0 | Out= Ballarat to Moorabool No.1 220kV line, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | Outage | Thermal | Vic
V>S_460_DYN | 429.9419 | 23720.666 | 0.41667 | 11.0833 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | Vic
QN_1000 | 425.9533 | 0 | 1.5833 | 0 | Qld to NSW on QNI upper transfer limit of 1000 MW | Outage | Discretionary | Qld
Q:N_1110 | 410.6705 | 0 | 1 | 0 | QNI oscillatory stability limit of 1110 MW | Outage | Oscillatory Stability | Qld
F_I+ML_L6_APD_LD | 407.8606 | 398.4676 | 12.8333 | 11.5 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage | FCAS | FCAS
N>NIL_9R5_9R6 | 407.8053 | 0 | 0.083333 | 0 | Out= Nil, avoid O/L Wagga North to Wagga330 (9R5) on trip of Wagga North to Wagga 132 (9R6) line, Feedback | NIL | Thermal | NSW
NQ_700_DYN_TEST | 404.5585 | 17523.3538 | 0.25 | 15.75 | NSW to QLD on QNI upper transfer limit of 700 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | NSW
F_T+FARE_N-2_TG_R6 | 398.9011 | 0 | 2.25 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_Q++8E_R6 | 397.1206 | 408.0811 | 4.25 | 1.1667 | Out = Sapphire to Armidale (8E) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
T_ROCOF_2 | 396.9765 | 0 | 0.75 | 0 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of TAS largest unit with Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | ROC Frequency | Tas
V::S_TBEBUS_MAXG | 390.0362 | 0 | 0.41667 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage | Transient Stability | SA
F_S+MLMO_TL_L6_1 | 389.0123 | 0 | 4.6667 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage | FCAS | FCAS
S>>X_CR+RBTX+TPRS_04 | 377.7862 | 0 | 0.83333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>WEWT_TWPA_TPRS | 372.3648 | 0 | 0.33333 | 0 | Out= Waterloo East-Waterloo 132kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
V>S_460 | 370.1595 | 19319.2194 | 0.91667 | 15.0833 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage | Thermal | Vic
Q_STR_7C0K_KIDSF_1 | 369.6048 | 0 | 1.9167 | 0 | No limit to Kidston Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2 (80% if Kareeya =0), NQLD>350&370(AVG),Ross_FN>150&170(AVG),25% (40% if Haughton Synon ON)NQLD>250&270(AVG),Ross_FN>100&120(AVG) ,Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_WHTSF | 366.7315 | 2624.8975 | 0.66667 | 1.1667 | Limit 50% to Whitsunday SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
N_WALGR_BAT_L_ZERO | 365.8846 | 245.1662 | 0.16667 | 0.25 | Wallgrove Battery (Load Component) upper limit of 0 MW | Outage | Unit Zero | NSW
T>T_PMSH_IMP_4D | 363.009 | 0 | 0.5 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V::N_KMRC_O2 | 357.6633 | 0 | 0.91667 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
F_MAIN+GFT_TG_R5 | 350.88 | 1873.6104 | 37.9167 | 114.25 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T++BL_650_R6_3 | 339.62 | 0 | 0.75 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage | FCAS | FCAS
N_HILLSTSF1_ZERO | 332.99 | 0 | 0.083333 | 0 | Hillston solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_NEWENSF1+2_110-INV | 318.7159 | 0 | 0.41667 | 0 | New England Solar inverter limit of 110. Constraint to violate if New England Solar inverter availability greater than 110. Swamp out otherwise. DS only | Outage | System Strength | NSW
Q_WHITSF1_ZERO | 315.9917 | 37052.5307 | 0.25 | 5.8333 | Whitsunday solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_N_WALGR_BAT_G_R6 | 314.9278 | 4.29 | 0.83333 | 0.25 | Out= Nil, Wallgrove BESS (generation component) Raise 6 sec Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>V_MWP3RB_RBNW1 | 312.6194 | 0 | 4.5833 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L Roberstown-North West Bend 132kV line on trip of Nil trip, Feedback | Outage | Thermal | SA
T^^V_GTHA_1 | 306.9106 | 0 | 0.91667 | 0 | Out = George Town to Hadspen 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining George Town to Hadspen 220 kV line. | Outage | Voltage Stability | Tas
T>T_PMSH_IMP_4E | 303.2859 | 0 | 0.58333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
S>>RBTX_BRTW_WTTP | 302.7454 | 0 | 0.083333 | 0 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo - Templers 132kV on trip of Brinkworth - Templers West 275kV line, Feedback | Outage | Thermal | SA
V>>NIL_BANBGR_ARCW | 301.2611 | 0 | 0.33333 | 0 | Out = Nil, avoid O/L Ballarat North to Buangor 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service, Feedback | NIL | Thermal | Vic
V::N_HYTR_xxx | 298.5512 | 2729.7103 | 0.66667 | 1.25 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
F_N_WALGR_BAT_G_R60 | 295.4566 | 9.61 | 0.58333 | 0.25 | Out= Nil, Wallgrove BESS (generation component) Raise 60 sec Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T++NIL_BLSPS_R6 | 294.0334 | 0 | 1.0833 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, FCSPS unavailable. DS Only | NIL | FCAS | FCAS
F_Q++8U_L5 | 292.9733 | 0 | 0.5 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
N>96L/96R_967_89_S | 291.7942 | 0 | 6.6667 | 0 | Out= Lismore to Tenterfield (96L) or Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Lismore to Koolkhan (967) 132kV line on trip of Lismore to Coffs Harbour (89) 330kV line, Feedback | Outage | Thermal | NSW
F_ESTN++HYTR_L60 | 290.0992 | 77.6 | 19.5 | 8.5833 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
N>N-BAMB_132_OPEN_A | 289.8889 | 0 | 3.1667 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | Thermal | NSW
V::N_KMRC_O1 | 284.7123 | 0 | 0.41667 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
Q:N_1150 | 284.2967 | 0 | 2.1667 | 0 | QNI oscillatory stability limit of 1150 MW | Outage | Oscillatory Stability | Qld
VT_350 | 272.8984 | 0 | 0.25 | 0 | Vic to Tas on Basslink upper limit of 350 MW | Outage | Discretionary | Vic
Q_STR_7C0K_KEP_2 | 272.3379 | 0 | 0.5 | 0 | Limit Kennedy Energy park to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
V:S_570_OSC_AUTO | 264.8839 | 33.1285 | 0.083333 | 0.083333 | Out = NIL (Note: with both Black Range series capacitors I/S), Upper transfer limit of 570 MW on VIC to SA on Heywood, Active only when I25 mode cannot be monitored. | NIL | Oscillatory Stability | Vic
V>>051_68_67_R | 251.4392 | 0 | 0.16667 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, (Note: Assumed Wagga-Yass 132kV network Split, X5, 63 & 9R4 opened, & with 2 Yass Transformer I/S; Swamped if SIPS ENABLED) | Outage | Thermal | Vic
N_WELLSF1_ZERO | 250.06 | 27115.7544 | 0.083333 | 1.5 | Wellington solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V::N_MLMO_xxx | 248.6006 | 0 | 0.83333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_T++FARE_N-2_TG_R60 | 248.5686 | 0 | 5.5833 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 60 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S>>MKRB_BWMP_WTTP | 241.2547 | 8529.0009 | 0.25 | 1.4167 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_I+BIP_ML_L60 | 240.7725 | 15515.33 | 40.5 | 23.9167 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL | FCAS | FCAS
F_T++NIL_MG_R60 | 235.3599 | 1819.2865 | 45.5833 | 30.3333 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL | FCAS | FCAS
N_NEWENSF1+2_260-INV | 233.8303 | 0 | 0.25 | 0 | New England Solar inverter limit of 260. Constraint to violate if New England Solar inverter availability greater than 260. Swamp out otherwise. DS only | Outage | System Strength | NSW
F_I+GFT_TG_R1 | 232.49 | 0 | 1 | 0 | Out = Nil, Raise 1 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT for a trip of ARTS - WBTS - BATS 220kV line. Requirement capped at 225 MW | Outage | FCAS | FCAS
N_METZSF_38INV | 230.9174 | 0 | 0.083333 | 0 | Metz Solar Farm inverter limit of 38. Constraint to violate if Metz Solar Farm inverter availability greater than 38. Swamp out otherwise. DS only | Outage | System Strength | NSW
T>T_NIL_BL_3C | 222.0348 | 2229.135 | 0.66667 | 2.1667 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
V^^N_BADP_1 | 212.3322 | 55575.4422 | 0.58333 | 4.8333 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S>>MKRB_BRTW_WTTP | 211.0654 | 16937.2073 | 0.16667 | 1.5833 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
V^^N_JNWG_1 | 210.6824 | 0 | 0.66667 | 0 | Out = Jindera to Wagga (62) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
F_T+NIL_TL_L6_DS | 205.8036 | 0 | 0.25 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_BRYBWF_ZERO | 199.8801 | 1693.3997 | 0.083333 | 0.41667 | Berrybank Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
F_S++HYSE_L6_2 | 199.0592 | 2781.9607 | 3.0833 | 0.33333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage | FCAS | FCAS
Q_STR_7C2K_KEP_7 | 194.6299 | 0 | 0.33333 | 0 | Limit to Kennedy Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_I+BIPP_ML_L1 | 192.88 | 0 | 0.16667 | 0 | Out = Nil, Lower 1 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. Requirement capped at 125 MW | Outage | FCAS | FCAS
V_ARWF_FSTTRP_5 | 192.0089 | 0 | 0.083333 | 0 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Discretionary | Vic
F_T+CO_752_TL_L6 | 191.0565 | 0 | 0.5 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_I+NILL_MG_R1 | 190.48 | 0 | 0.58333 | 0 | Out = Nil, Raise 1 sec requirement for a NEM Generation Event. Requirement capped at 225 MW | Outage | FCAS | FCAS
S>>X_RBPA+RBTX2_06 | 188.8036 | 455501.9425 | 0.5 | 50.5 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
F_Q++NIL_R6 | 183.0981 | 0 | 0.83333 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 6 sec requirement for loss of a NSW 750 MW unit | NIL | FCAS | FCAS
T^^V_GTSH_1 | 176.9252 | 0 | 0.66667 | 0 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Voltage Stability | Tas
V_GANWR_BAT_L_ISL_0 | 173.76 | 65101.9556 | 0.083333 | 3.4167 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V_SALTCREEK_ZERO | 169.3429 | 0 | 0.083333 | 0 | Salt Creek wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
Q_KEP-HYB_27MW | 167.7935 | 1803.6098 | 0.083333 | 1 | Kennedy Energy Park upper limit of 27MW | Outage | Discretionary | Qld
S>>X_CR+RBTX+TPRS_21 | 165.641 | 0 | 0.083333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of MWP4-Robertstown 132kV line (This trip MWP4 SF) line, Feedback | Outage | Thermal | SA
F_T++COGT_TL_L6 | 164.7133 | 0 | 1.4167 | 0 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V::N_KGRC_O2 | 164.6108 | 0 | 0.5 | 0 | Out = Kerang to Red Cliffs 220kV line (or any section in between), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
F_Q++8U_R60 | 163.7967 | 0 | 0.58333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
N_GOONSF_11_INV | 162.3783 | 3476.1174 | 0.083333 | 0.5 | Goonumbla Solar Farm inverter limit of 11. Constraint to violate if Goonumbla Solar Farm inverter availability greater than 11. Swamp out otherwise. DS only | Outage | System Strength | NSW
N>>NIL_X3_060 | 159.7578 | 0 | 0.083333 | 0 | Out= Nil, avoid O/L Balranald to Buronga (X3) on trip of Jindera to Wodonga (060) line, Feedback | NIL | Thermal | NSW
F_T_FISHER_L6 | 159.1233 | 0 | 1.9167 | 0 | Out= NIL, Fisher L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN+TTS_TG_R5 | 158.24 | 220.6873 | 26.9167 | 26.6667 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V>>CWHO_X3_BEKG | 155.3347 | 0 | 0.41667 | 0 | Out = Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage | Thermal | Vic
N_FINLEYSF_81INV | 155.2374 | 0 | 0.083333 | 0 | Finley Solar Farm inverter limit of 81. Constraint to violate if Finley Solar Farm inverter availability greater than 81. Swamp out otherwise. DS only | Outage | System Strength | NSW
S>>X_CR+RBTX+TPRS_12 | 154.4762 | 0 | 0.33333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
V::N_ROSM_O2 | 153.1994 | 1749.1923 | 0.25 | 1.3333 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
F_T+FARE_N-2_TG_R6_1 | 151.5926 | 3140.5103 | 0.33333 | 3.3333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage | FCAS | FCAS
F_MAIN++TTS_TG_R60 | 146.0179 | 2420.3093 | 22 | 71.8333 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL | FCAS | FCAS
V_T_FCSPS_DS | 145.963 | 0 | 0.25 | 0 | Basslink limit from Vic to Tas for FCSPS scheme outage, DS only. Swamped when FCSPS scheme in service and load available for arming | NIL | Other | Vic
N_METZSF_38 | 142.78 | 0 | 0.083333 | 0 | Metz Solar farm upper limit of 38 MW | Outage | System Strength | NSW
V^SML_KGRC_4 | 139.4274 | 0 | 3.0833 | 0 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Voltage Stability | Vic
N>N-X_9U6_9G2_2 | 138.1056 | 0 | 2.75 | 0 | Out = one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 132kV line between Mullumbimby and Ballina (9G2, 9G3, 9G4 or 9G5), avoid O/L remaining 132kV line, Qld to NSW limit | Outage | Thermal | NSW
N_MBTE1_A | 138.0745 | 55.8806 | 0.83333 | 0.66667 | Out= one Directlink cable, NSW to Qld limit | Outage | Unit Zero | NSW
N>>V_051_65_66_R | 136.3407 | 0 | 0.16667 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Upper Tumut to Murray (65) on trip of Lower Tumut to Murray (66) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | NSW
F_T_FARC2_R60 | 134.34 | 0 | 0.33333 | 0 | Out=Farrell-Reece 2 220KV line. R60 <= 0MW | Outage | Unit Zero - FCAS | FCAS
V^^S_TBEBUS_SETB | 134.0228 | 0 | 0.083333 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line | Outage | Voltage Stability | SA
N_GOONSF_9_INV | 132.5036 | 0 | 0.083333 | 0 | Goonumbla Solar Farm inverter limit of 9. Constraint to violate if Goonumbla Solar Farm inverter availability greater than 9. Swamp out otherwise. DS only | Outage | System Strength | NSW
N_GNNDHSF1_ZERO | 129.7608 | 2138.4317 | 0.16667 | 0.16667 | Gunnedah solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V^^S_XPAVC_SETB | 129.0323 | 0 | 0.083333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
F_QNV+HYTR_L60 | 126.7206 | 0 | 2.25 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_I+BIP_ML_L5 | 123.49 | 6.37 | 33.1667 | 2.1667 | Out = Nil, Lower 5 min requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL | FCAS | FCAS
N_NEWENSF1+2_279 | 123.3535 | 0 | 0.16667 | 0 | New England Solar farms 1 + 2 upper limit of 279 MW | Outage | System Strength | NSW
F_S+MLMO_TL_L6_2 | 121.3588 | 0 | 2.3333 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage | FCAS | FCAS
F_I+TTS_TG_R1 | 120.31 | 0 | 0.58333 | 0 | Out = Nil, Raise 1 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) for contingency trip of line 63. Capped at 225 MW | Outage | FCAS | FCAS
F_MAIN++NIL_BL_L6 | 119.91 | 845.8795 | 1.6667 | 33.5 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
F_T+FARE_N-2_RREG | 117.1556 | 5395.3431 | 6.1667 | 8.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | Unit Zero - FCAS | FCAS
Q_STR_7C2K_WHTSF_10 | 116.1393 | 0 | 0.58333 | 0 | Limit Whitsunday Solar Farm to 40% if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON ,Zero otherwise. | Outage | System Strength | Qld
Q>>BCCP_BCRG_CLWU | 115.7556 | 0 | 0.16667 | 0 | Out= Bouldercombe to Calliope River (812), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
F_I+ML_ST1_L6 | 113.47 | 12.93 | 5.25 | 4.4167 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
S>NIL_NIL_NWMH2 | 112.9594 | 15100 | 0.25 | 0.083333 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
F_T++FA_B_N-2_TG_R60 | 112.467 | 0 | 3.5833 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 60 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
N_WR_55_WT-INV | 112.3604 | 0 | 0.083333 | 0 | White Rock Wind & Solar Farm inverter limit of 55. Constraint to violate if White Rock Wind & Solar Farm inverter availability greater than 55. Swamp out otherwise. DS only | Outage | System Strength | NSW
V::S_SEVC1_SETB | 111.6237 | 1618.415 | 0.33333 | 1.25 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
V^^S_PAVC_MAXG | 111.2023 | 0 | 0.083333 | 0 | Out= Para one SVC (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V>>N_051_66_65_R | 107.3593 | 594.2216 | 0.33333 | 1.5 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line,(Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | Vic
F_Q++NIL_R5 | 105.762 | 0 | 2.4167 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL | FCAS | FCAS
T_T_FASH2_1 | 101.0115 | 0 | 2.3333 | 0 | Out = Farrell 220 kV bus split, limit John Butters, Bastyan and Mackintosh to less than 110% West Coast load | Outage | Other | Tas
S_PPT+SNPT_270 | 100.7483 | 63625.4405 | 0.083333 | 3.8333 | SA Pelican Point + Snapper Point generation <= 270 MW | Outage | Discretionary | SA
V::S_NIL_MG_PS_N-2_1 | 99.976 | 0 | 0.25 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA with loss of Pelican Point + Snapper Point PS declared as credible.( Note: South East Capacitor Available) | Outage | Transient Stability | SA
Q_STR_7C0K_HAMSF_2 | 99.4676 | 0 | 2.25 | 0 | Limit Hamilton SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
F_MAIN+ML_L6_APD_LD | 97.5 | 10.92 | 1.25 | 1.5 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage | FCAS | FCAS
S>>X_CNRB+RBTX_13 | 96.1902 | 0 | 0.083333 | 0 | Out= One Robertstown TX + Canowie-Robertstown 275kV line O/S, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_MAIN++BIP_ML_L5 | 93.9362 | 2.16 | 12 | 0.41667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_Q++MUTW_R5 | 93.8079 | 0 | 0.58333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage | FCAS | FCAS
N>9U6/9U7_8507_9U7 | 89.9304 | 0 | 4.5833 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L Balina to Astonville (8507) 66kV line on trip of other 9U7 or 9U6 132kV line, Feedback | Outage | Thermal | NSW
F_ESTN++HYTR_L6 | 89.9047 | 33.84 | 14.8333 | 9.1667 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
V_GANWR_BAT_G_ISL_0 | 89.81 | 0 | 0.083333 | 0 | Gannawarra Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
NQTE_090 | 82.2389 | 0 | 0.33333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of 90 MW | Outage | Discretionary | NSW
N>>LDTM_964_84_OPEN | 81.6303 | 0 | 0.16667 | 0 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Liddell (84) line, Feedback | Outage | Thermal | NSW
F_T++BL_650_R60_3 | 77.68 | 0 | 1 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage | FCAS | FCAS
V>>N_NIL_66_65 | 77.6761 | 1013115.7968 | 0.083333 | 6.75 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL | Thermal | Vic
VT_ZERO | 73.5035 | 0 | 0.083333 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Interconnector Zero | Vic
F_T++COGT_TL_L5 | 71.61 | 0 | 1.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
VSML_FLT_150 | 69.9602 | 0 | 0.91667 | 0 | Vic to SA on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
F_T++CO_752_TL_L6 | 69.4576 | 0 | 1.25 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | Outage | FCAS | FCAS
N>>9R3_99D_63 | 67.0321 | 0 | 0.58333 | 0 | Out= Finley to Deniliquin (9R3), avoid O/L Darlington Point to Yanco (99D) 132kV line on trip of Darling Point to Wagga (63) 330kV line, X5 trip scheme disarmed, Feedback | Outage | Thermal | NSW
N>N_LSDU_9U6_2 | 66.829 | 0 | 3.25 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage | Thermal | NSW
F_T_FARC1_R6 | 65.8613 | 0 | 1.0833 | 0 | Out=Farrell-Reece 1 220KV line. R6 <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN++TTS_TG_R5 | 64.1432 | 454.5563 | 22.4167 | 29.0833 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL | FCAS | FCAS
Q>X_SRMB_PBMB | 63.7501 | 0 | 0.083333 | 0 | Out = T015 (Susan River to T59 Maryborough) 66kV line and T014 (Pialba to T59 Maryborough) 66kV line, limit Susan River to 60MW | Outage | Thermal | Qld
V>>N-DPWG_X5_A | 63.1152 | 0 | 0.16667 | 0 | Out = to Wagga (63) and Darlington Point to Balranald (X5), avoid Murray to Upper Tumut (65) O/L on Murray to Lower Tumut (66) trip; Feedback | Outage | Thermal | Vic
F_Q++85_L5 | 62.2665 | 0 | 1.25 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
F_T+FARE_N-2_TG_R60 | 58.0759 | 191.3967 | 2.5833 | 3.8333 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V>>N_64_66_65_N | 55.8041 | 0 | 0.083333 | 0 | Out = LowerTumut-UpperTumut (64), avoid Murray to Lower Tumut (66) O/L on Murray to Upper Tumut (65) trip; Feedback | Outage | Thermal | Vic
V::S_SETB_MG_PPGT1 | 54.9643 | 0 | 0.16667 | 0 | Out= one South East -Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT1 + DPV trip) in SA (SE Cap Available). (NOTE: with one Black Range series capacitors I/S. Co-optimised eq PPGT1 LHS | Outage | Transient Stability | SA
F_MAIN++TTS_TG_R1 | 54.09 | 0 | 0.25 | 0 | Out = Nil, Raise 1 sec req. for Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF, DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) for loss of line 63, Basslink able to transfer FCAS. Capped at 225 MW | Outage | FCAS | FCAS
T_FASH_MAXG_SB3 | 54.0138 | 0 | 0.41667 | 0 | Upper limit on West Coast Gens with both Farrell to Sheffield 220 kV lines declared credible, West Coast 220/110 kV parallel closed. Constraint active if MORE THAN TWO West Coast Hydro machines online. CP-04, Scenario B | Outage | Other | Tas
F_ESTN++MLMO_L60 | 53.69 | 0 | 6.9167 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
NQTE_-090 | 52.1656 | 0 | 0.16667 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -90 MW | Outage | Discretionary | NSW
F_T++NIL_TL_L6_DS | 49.9963 | 0 | 1.1667 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_MAIN++APD_TL_L1 | 47.8628 | 0 | 0.41667 | 0 | Out = Nil, Lower 1 sec requirement for Mainland Network event, simultaneous loss of both APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS. Requirement capped at 125 MW | Outage | FCAS | FCAS
F_Q++MUTW_R6 | 46.8425 | 0 | 1.4167 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
F_QNV++HYTR_L60 | 46.3219 | 18.069 | 2.4167 | 0.33333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
SVML_030 | 45.1205 | 0 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 30 MW | Outage | Discretionary | SA
S>>BWMP_DVBR_BGTX2 | 45.0463 | 1265.013 | 0.083333 | 1.1667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Bungama 275/132kV (TX2) on trip of Davenport-Brinkworth 275 kV line, Feedback | Outage | Thermal | SA
F_MAIN++GFT_TG_R1 | 44.56 | 0 | 0.41667 | 0 | Out= Nil, Raise 1 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT for a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS. Capped at 225 MW | Outage | FCAS | FCAS
F_S_LBBL1_LREG | 43.02 | 875430.0946 | 0.91667 | 24.8333 | Out= NIL, Lake Bonney Battery (Load Component) LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>NIL_WERB_WEWT | 43 | 0 | 0.083333 | 0 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | Thermal | SA
T_PMPO_220 | 42.1299 | 0 | 0.25 | 0 | Out=A single Palmerston-Poatina 220KV line. One line out of service only | Outage | Unit Zero | Tas
T_BLINK_VT_NGZ | 41.9125 | 0 | 0.25 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow < 0, Basslink Target MW <= 0, swamped if Basslink Metered Flow > -0.1 DS only. | NIL | Other | Tas
V>>NIL_SMDD_SMDD | 40.0793 | 0 | 0.16667 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL | Thermal | Vic
F_T_FARC1_R60 | 39.25 | 0 | 0.83333 | 0 | Out=Farrell-Reece 1 220KV line. R60 <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q_STR_7C0K_KIDSF_2 | 36.989 | 0 | 0.83333 | 0 | Limit Kidston SF to 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kar >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG)(100% if Haughton Syncon ON),40% if Kar<0 or if NQLD>250&270(AVG),Ross_FN>100&120(AVG) (25% if Syncon OFF), Zero otherwise. | Outage | System Strength | Qld
F_T++CO_752_TL_L5 | 34.73 | 0 | 0.66667 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S:V_PA_SVC_270 | 34.2193 | 26772.0004 | 0.083333 | 41.1667 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage | Oscillatory Stability | SA
Q^^N_DM+LS_SVC_SRAR | 33.5835 | 0 | 0.41667 | 0 | Out = Dumaresq SVC + Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
QN_1300_DYN_TEST | 32.5531 | 0 | 0.083333 | 0 | QLD to NSW on QNI upper transfer limit of 1300 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | Qld
NQ_700_TEST | 31.7127 | 7751.4379 | 0.083333 | 6.6667 | NSW to Qld on QNI upper transfer limit of 700 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | NSW
V^^S_MLSY_2 | 31.4706 | 0 | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Voltage Stability | Vic
S>RBPA_BWMP_HUWT | 30.1743 | 0 | 0.083333 | 0 | Out= Robertstown-Para 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_ESTN+MCSH_TG_R60 | 28.77 | 9.125 | 3.5 | 1.5 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line | Outage | FCAS | FCAS
Q::N_30+38_AR_2L-G | 28.4616 | 0 | 0.5 | 0 | Out = Liverpool to Sydney West (30) + Regentville to Sydney West (38) 330 kV lines, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
V>>ARWB_X5DP_KGBE | 28.2044 | 0 | 0.25 | 0 | Out= Any 220kV line section between Ararat and Ballarat, avoid O/L Balranald to Darlington Point (X5) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
F_T++NIL_BL_R6_4 | 27.1216 | 0 | 0.083333 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 4, FCSPS available | NIL | FCAS | FCAS
N::Q_TW_SVC_TNT | 26.9504 | 0 | 0.25 | 0 | Out = Tamworth SVC, NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage | Transient Stability | NSW
S>>NIL_TUTB_TUTB_1 | 25.4749 | 0 | 0.083333 | 0 | Out= NIL, avoid O/L Tungkillo-Tailem Bend 275kV line 1 or 2 on trip of parallel Tungkillo-Tailem Bend 275 kV line 2 or 1, Feedback | NIL | Thermal | SA
F_Q++8C_L5 | 24.99 | 4885.1575 | 0.58333 | 10.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage | FCAS | FCAS
N>>NIL_64_65 | 24.2327 | 0 | 0.083333 | 0 | Out = Nil, avoid Lower Tumut to Upper Tumut(64) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL | Thermal | NSW
T^V_HA_GT_220_1 | 23.6691 | 0 | 0.25 | 0 | Out= one George Town to Hadspen 220kV line, limit post-contingency loading on Palmerston to Sheffield 220kV line (flow to north) to avoid voltage collapse on trip of the remaining Hadspen to George Town 220kV line. | Outage | Voltage Stability | Tas
F_QNV+HYTR_L6 | 23.63 | 0 | 1.6667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_N_WALGR_BAT_L_RREG | 23.48 | 0 | 0.083333 | 0 | Out= Nil, Wallgrove BESS (load component) Raise Regulation Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>V_NIL_NIL_RBNW1 | 22.9333 | 0 | 0.25 | 0 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL | Thermal | SA
F_T++FARE_N-2_TG_R5 | 21.99 | 0 | 3.0833 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 5 min requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T+FARE_N-2_TG_R5 | 21.88 | 6418.4731 | 3.8333 | 9.6667 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
CA_BRIS_542A0DC2_1 | 21.8707 | 0 | 0.16667 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage | Thermal | Constraint Automation
F_QNV+MLMO_L60 | 21.63 | 0 | 0.5 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
T>T_TUNN3_110_2 | 21.5459 | 0 | 0.16667 | 0 | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
V:S_PA_SVC_550 | 21.3461 | 0 | 0.083333 | 0 | Out= one Para SVC (Note: with both Black Range series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 550 MW | Outage | Oscillatory Stability | Vic
F_MAIN+BIP_ML_L60 | 20.67 | 10.58 | 1.75 | 5.25 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_T++CO_752_TL_L60 | 20.54 | 0 | 0.75 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V::N_SMTT_O2 | 20.3586 | 0 | 0.25 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
S>>X_CR+RBTX+TPRS_15 | 19.8188 | 0 | 0.083333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L Templers West-Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
N::Q_8C8J_LDTW_N-2 | 19.2436 | 0 | 0.16667 | 0 | Out = Nil, NSW to Qld Transient Stability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | NSW
Q>>WOPW_WOSP_WOGP_2 | 19.0817 | 3699909.6338 | 0.083333 | 65.25 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
F_S_DLBAT-L_L60 | 18.1 | 1395.1473 | 2.25 | 22.25 | Out= NIL, Dalrymple Battery (Load Component) L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>TBTX4_TBTU_TBTU | 17.1894 | 0 | 0.083333 | 0 | Out= Tailem Bend 275/132kV #4 TX (Black Range series caps I/S), avoid O/L of one Tailem Bend-Tungkillo 275 kV line on trip of other Tailem Bend-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
F_I+ML_ST1_L60 | 15.84 | 0 | 0.33333 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 60 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
F_S_DLBAT-G_R6 | 15.31 | 2987.3922 | 2.3333 | 22.0833 | Out= NIL, Dalrymple Battery (Generation Component) R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_ESTN++MLMO_L6 | 15.28 | 0 | 1.3333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_T+BL_650_R5 | 15.02 | 0 | 1 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available, LoL = 650 ms | Outage | FCAS | FCAS
F_I+ML_ST1_L5 | 14.52 | 0 | 0.33333 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 5 min Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
F_T++NIL_BLSPS_R60 | 14.48 | 0 | 1.0833 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, FCSPS unavailable. DS Only | NIL | FCAS | FCAS
CA_BRIS_542A114F_1 | 14.4753 | 0 | 0.16667 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage | Thermal | Constraint Automation
F_S_DLBAT-G_R60 | 14.34 | 2195.4457 | 2.3333 | 22.1667 | Out= NIL, Dalrymple Battery (Generation Component) R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_N_WALGR_BAT_L_LREG | 14.2 | 0 | 0.25 | 0 | Out= Nil, Wallgrove BESS (load component) Lower Regulation Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN++BIP_ML_L60 | 14.1812 | 2.01 | 2.0833 | 1.1667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_T++BL_650_R60_2 | 13.84 | 0 | 0.91667 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage | FCAS | FCAS
SVML_060 | 12.8235 | 0 | 0.083333 | 0 | SA to Vic on ML upper transfer limit of 60 MW | Outage | Discretionary | SA
F_T+NIL_TL_L60_DS | 12.0779 | 0 | 0.5 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_S_DLBAT-G_R5 | 10.82 | 173.54 | 2.3333 | 21.9167 | Out= NIL, Dalrymple Battery (Generation Component) R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q>N-MUTE_757 | 10.7151 | 1483.2135 | 0.58333 | 9.0833 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
Q>N_LSLS_9U8 | 10.7039 | 0 | 0.083333 | 0 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 Directlink cable O/S. | Outage | Thermal | Qld
F_ESTN++HYTR_L5 | 10.55 | 0 | 1.5 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_S_DLBAT-L_L6 | 10.27 | 558.712 | 2.25 | 18.5 | Out= NIL, Dalrymple Battery (Load Component) L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>>NIL_8E_8C_S | 9.9249 | 0 | 0.25 | 0 | Out = Nil, avoid O/L Sapphire to Armidale (8E) using 15 min rating on trip of Dumaresq to Armidale (8C) line, Feedback | NIL | Thermal | NSW
F_Q++8E_L5 | 9.7266 | 390.8095 | 0.58333 | 1.5833 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
F_S_DLBAT-L_L5 | 9.66 | 202.9232 | 2.1667 | 18.3333 | Out= NIL, Dalrymple Battery (Load Component) L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V::N_WBHO_xxx | 9.2011 | 0 | 0.083333 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_QNV++HYTR_L5 | 9.1 | 0 | 1.0833 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S>>NIL_TBTU_TBTU_1 | 9.0859 | 0 | 0.083333 | 0 | Out= NIL, avoid O/L Tailem Bend-Tungkillo 275kV line 1 or 2 on trip of parallel Tailem Bend-Tungkillo 275 kV line 2 or 1, Feedback | NIL | Thermal | SA
S>>X_RBTU+RBTX_16 | 8.7119 | 19830.7441 | 0.91667 | 4.25 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage | Thermal | SA
F_T++COGT_TL_L60 | 8.46 | 0 | 1.1667 | 0 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_ESTN+MCSH_TG_R5 | 8.367 | 21.11 | 2 | 4.75 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line | Outage | FCAS | FCAS
F_QNV++HYTR_L6 | 8.0151 | 18.89 | 0.66667 | 0.83333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
QNTE_090 | 7.8484 | 0 | 0.16667 | 0 | Qld to NSW on Terranora Interconnector upper transfer limit of 90 MW | Outage | Discretionary | Qld
N>>V_SMDD6 | 7.7958 | 1240.5915 | 0.083333 | 1.4167 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
F_T+BL_650_R60_1 | 7.62 | 0 | 0.83333 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage | FCAS | FCAS
VSML_025 | 7.0976 | 0 | 0.5 | 0 | Vic to SA on ML upper transfer limit of 25 MW | Outage | Discretionary | Vic
F_QNV+HYTR_L5 | 6.96 | 0 | 0.75 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
N>96L_967_89 | 6.7819 | 0 | 0.33333 | 0 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), TG formulation in PD/ST(Noted: Swamped out when 967 O/S) | Outage | Thermal | NSW
F_MAIN+BIP_ML_L5 | 6.6 | 0.12 | 1.6667 | 0.16667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL | FCAS | FCAS
V>>KMRC_DPTX_KGBE | 6.5932 | 0 | 0.16667 | 0 | Out= Kiamal to Red Cliffs 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
N>>11_39_17 | 6.2421 | 0 | 0.083333 | 0 | Out = Dapto-Sydney South (11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage | Thermal | NSW
F_N_WALGR_BAT_G_R5 | 6.21 | 1.28 | 0.33333 | 0.25 | Out= Nil, Wallgrove BESS (generation component) Raise 5 min Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S^DVPL_CRK_VCS | 6 | 0 | 0.25 | 0 | Out= Any line between Davenport, Cultana and Port Lincoln, Upper limit for Cathedral Rocks WF based on Mt Millar Voltage Control System (VCS) availability, (Note: CRK <=45 MW when VCS OFF; CRK<= 53 MW when VCS ON) | Outage | Voltage Stability | SA
F_T++NIL_TL_L60_DS | 5.56 | 0 | 0.25 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_T++FASH_1_TG_R60 | 5.519 | 0 | 1.4167 | 0 | Out=Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_N_WALGR_BAT_L_L60 | 5.43 | 0 | 0.66667 | 0 | Out= Nil, Wallgrove BESS (load component) Lower 60 sec Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_QNV++MLMO_L60 | 5.27 | 0 | 0.41667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_S+MLMO_TL_L5 | 5.25 | 0 | 3.25 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 5 min requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage | FCAS | FCAS
F_T++NIL_TL_L5_DS | 4.89 | 0 | 0.083333 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_T++BLSPS_IMP_R6_1 | 4.84 | 0 | 0.66667 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS | FCAS
F_T_FARC2_R6 | 4.52 | 7.19 | 0.083333 | 0.25 | Out=Farrell-Reece 2 220KV line. R6 <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_N_WALGR_BAT_L_L5 | 4.24 | 0 | 0.66667 | 0 | Out= Nil, Wallgrove BESS (load component) Lower 5 min Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T++BLSPS_IMP_R60_1 | 3.8869 | 0 | 0.83333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS | FCAS
F_T+GTTE_TL_L6 | 3.42 | 2826.1678 | 0.75 | 117.3333 | Out = one George Town to Temco 110 kV line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T+GTTE_TL_L60 | 3.42 | 2115.8649 | 0.75 | 112.9167 | Out = one George Town to Temco 110 kV line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
SVML_000 | 3.4196 | 0 | 0.33333 | 0 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Discretionary | SA
F_MAIN++TTS_TG_R6 | 3.41 | 257.043 | 0.83333 | 18.8333 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_QNV+MLMO_L6 | 3.22 | 0 | 0.16667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T_JBUTTERS_L60 | 3.2011 | 0 | 2.0833 | 0 | Out= NIL, John Butters L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T_CETHANA_L60 | 3.0411 | 0 | 0.75 | 0 | Out= NIL, Cethana L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T_DG_0_L60 | 3.0411 | 0 | 0.75 | 0 | Devils Gate = 0MW L60 <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_ESTN++MLMO_L5 | 3.03 | 0 | 0.41667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_T++FASH_1_TG_R5 | 2.99 | 0 | 1.4167 | 0 | Out= Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_ESTN+MCSH_TG_R6 | 2.93 | 3.16 | 0.58333 | 0.41667 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line | Outage | FCAS | FCAS
F_T+CO_752_TL_L60 | 2.8258 | 0 | 0.25 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S^DVPPL_CRK+MTM_109 | 2.25 | 0 | 0.083333 | 0 | Out= Any line between Davenport, Cultana and Port Lincoln, Upper limit for Cathedral Rocks WF + Mt Millar WF <= 109 MW to maintain voltage stability limits | Outage | Voltage Stability | SA
F_T++NIL_BLSPS_R5 | 2.18 | 0 | 1 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS unavailable. DS Only | NIL | FCAS | FCAS
N^^V_MSUT_1 | 2.0748 | 0 | 0.16667 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
QNI_SOUTH_1100_DYN | 1.9844 | 0 | 0.083333 | 0 | QLD to NSW on QNI upper transfer limit of 1100 MW, dynamic headroom with Max calc on the QNI, DS formulation only. | Outage | Transient Stability | Qld
F_T+CO_752_TL_L5 | 1.9 | 0 | 0.41667 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T++BL_650_R6_2 | 1.74 | 0 | 0.41667 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage | FCAS | FCAS
F_T+NIL_TL_L5_DS | 1.52 | 6411.5 | 0.33333 | 0.083333 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N_DARL_BAT_L_ZERO | 1.4909 | 0 | 0.083333 | 0 | Darlington Point Battery (Load Component) upper limit of 0 MW | Outage | Unit Zero | NSW
F_T++NIL_BL_R60_4 | 1.45 | 0 | 0.083333 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 4, FCSPS available | NIL | FCAS | FCAS
F_T++BLSPS_IMP_R6_2 | 1.43 | 0 | 0.083333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 2 | Outage | FCAS | FCAS
F_T_CETHANA_RREG | 1.3678 | 0 | 0.083333 | 0 | Out= NIL, Cethana RREG Requirement <= 0MW | Outage | Unit Zero | FCAS
F_T_DG_0_RREG | 1.3678 | 0 | 0.083333 | 0 | Devils Gate = 0MW. RREG <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T_JBUTTERS_RREG | 1.3678 | 0 | 0.083333 | 0 | Out= NIL, John Butters RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N::Q_LDTM_KC | 1.2809 | 0 | 0.083333 | 0 | Out= Liddell-Tomago (82), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
F_QNV++MCSH_TG_R60 | 1.24 | 62.3758 | 0.25 | 3.8333 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV+MCSH_TG_R60 | 1.04 | 59.14 | 0.083333 | 2.9167 | Out= Heywood to Tarrone OR Haunted Gully to Moorabool 500kV line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS or HYTS-TRTS line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T+BL_650_R6_1 | 0.92 | 0 | 0.5 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage | FCAS | FCAS
F_T_REECE1_R6 | 0.65 | 0 | 4.4167 | 0 | Out= NIL, Reece 1 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T_REECE2_R6 | 0.65 | 0 | 4.4167 | 0 | Out= NIL, Reece 2 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN++ST1_ML_L6 | 0.63 | 2.02 | 0.16667 | 0.66667 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T++FA_B_N-2_TG_R5 | 0.6 | 0 | 0.5 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 5 min requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_S_LBBG1_R5 | 0.49 | 218922.6993 | 0.083333 | 16.25 | Out= NIL, Lake Bonney Battery (Generation Component) R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN+ST1_ML_L6 | 0.39 | 19.39 | 0.083333 | 0.33333 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_N_WALGR_BAT_L_L6 | 0.39 | 0 | 0.75 | 0 | Out= Nil, Wallgrove BESS (load component) Lower 6 sec Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LBBL1_L60 | 0.39 | 102218.2148 | 0.083333 | 15.75 | Out= NIL, Lake Bonney Battery (Load Component) L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LBBL1_L5 | 0.38 | 73297.9823 | 0.083333 | 14.75 | Out= NIL, Lake Bonney Battery (Load Component) L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LBBL1_L6 | 0.38 | 102270.7308 | 0.083333 | 15.5 | Out= NIL, Lake Bonney Battery (Load Component) L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T++BLSPS_IMP_R5 | 0.38 | 0 | 0.083333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 5 min Requirement for loss of Basslink | Outage | FCAS | FCAS
F_T++BLSPS_IMP_R60_2 | 0.38 | 0 | 0.083333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 2 | Outage | FCAS | FCAS
T>T_GTHA_IMP_4L | 0.19826 | 0 | 0.083333 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
F_Q++86_R60 | 0.19167 | 0 | 0.083333 | 0 | Out = Armidale to Tamworth (86) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_T_CETHANA_R60 | 0.16 | 0 | 0.41667 | 0 | Out= NIL, Cethana R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>>LDTM_964_81_CL | 0.15282 | 0 | 0.083333 | 0 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV closed, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage | Thermal | NSW
F_T_REECE2_R60 | 0.12 | 0 | 0.083333 | 0 | Out= NIL, Reece 2 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T_FAJB_RREG | 0.11 | 0 | 0.083333 | 0 | Out=Farrell-John Butters 220KV line. RREG <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q^^N_TW_SVC_SRAR | 0.10384 | 0 | 0.083333 | 0 | Out = Tamworth SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
F_MAIN+APD_TL_L1 | 0.07 | 0 | 0.58333 | 0 | Out = Nil, Lower 1 sec requirement for Mainland Network event, simultaneous loss of both APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS. Requirement capped at 125 MW | Outage | FCAS | FCAS
F_T_JBUTTERS_L5 | 0.07 | 0 | 0.58333 | 0 | Out= NIL, John Butters L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LBBG1_R6 | 0.05 | 96868.626 | 0.083333 | 14.9167 | Out= NIL, Lake Bonney Battery (Generation Component) R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LBBG1_R60 | 0.05 | 428225.7202 | 0.083333 | 16.9167 | Out= NIL, Lake Bonney Battery (Generation Component) R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T_LEM_WIL_R60 | 0.02 | 0 | 0.16667 | 0 | Out= NIL, Lemonthyme + Wilmot R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>>NIL_5_3P_N | 0.0015 | 0 | 0.16667 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) using 15 mins rating on trip of Rye Park to Gullen Range (3P) line, Feedback | NIL | Thermal | NSW
Q-WHTSF_MVAR | 0.00076 | 0 | 0.083333 | 0 | Constraint to violate if Reactive power output of Whitsundays Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld

## Summary By Region
Binding Hours
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Ad-Hoc |  |  | 0 | 0 | 0 | 0
Constraint Automation | 1.3333 | 8.5833 | 22.75 | 14.4167 | 13 | 26.6667
Direction | 8190.0833 | 4093.5833 | 6243.5 | 10937 | 8580.4167 | 7192.75
FCAS | 95124.9167 | 105057.75 | 103359.8333 | 108605.1667 | 116665.9167 | 106431.8333
NSW | 3057.8333 | 4993.6667 | 5560.75 | 9057.9167 | 18965.6667 | 18127.4167
Negative Residue | 10.4167 | 24.1667 | 31.25 | 126.0833 | 135.9167 | 243.5833
Non-Conformance | 61.0833 | 93.75 | 110.5833 | 75.5 | 999 | 385.1667
Other | 115.25 | 64.3333 | 48.4167 | 7.25 | 14.1667 | 43.5
Outage Ramping | 174.4167 | 475.0833 | 645.8333 | 912.5 | 656.3333 | 813.9167
Qld | 511.3333 | 3120.5833 | 8015.5 | 4006.25 | 8083.5833 | 4827.0833
Quick | 12617.6667 | 10994.8333 | 9862.0833 | 11963.75 | 11952.1667 | 10949.25
SA | 3285.75 | 3935.6667 | 4110 | 6565.9167 | 8702.3333 | 7092.75
Tas | 1027.6667 | 966.5833 | 1886.6667 | 3197.8333 | 3445.25 | 2426.4167
Vic | 1914.5 | 5095.75 | 6439.6667 | 8030.75 | 9178.4167 | 9057.6667
Binding Impact
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Ad-Hoc | 0 | 0 | 0 | 0 | 0 | 0
Constraint Automation | 4494.9703 | 59181.5539 | 14369.9689 | 44668.7651 | 163091.1969 | 118260.3323
FCAS | 11563905.7935 | 14750181.9392 | 28959781.4212 | 22909324.6631 | 52721054.5674 | 8848301.7442
NSW | 4130424.9984 | 20853119.0897 | 20558572.6087 | 70853460.552 | 170481451.2232 | 126632826.0614
Negative Residue | 190929.9383 | 357086.6257 | 778063.9302 | 5915845.9777 | 3211345.7111 | 1212709.4364
Other | 11515.5764 | 31229.546 | 199098.2389 | 13605.2418 | 24345.9237 | 30853.343
Qld | 1092572.6105 | 14405785.5151 | 58969747.1872 | 29235595.5037 | 61043423.9559 | 20808223.8548
SA | 49743082.8304 | 23177002.4614 | 19911748.8298 | 32002902.6706 | 133245974.3113 | 51288161.2616
Tas | 2671514.9731 | 5630711.8908 | 7676693.2707 | 5526650.8229 | 17849391.7548 | 1699201.6972
Vic | 3495766.3104 | 19701434.9435 | 29835220.6476 | 46172027.4914 | 82285810.649 | 48190678.5135
Total | 72904208.0013 | 98965733.5652 | 166903296.1032 | 212674081.6883 | 521025889.2934 | 258829216.2445
Note on A6: FCAS excluded as it will swamp the graph

## NIL vs Outage
Binding Hours
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Commissioning | 12116 | 10389.25 | 7565 | 10437.3333 | 8298.6667 | 10841.3333
FCAS - NIL | 89035.8333 | 86275.9167 | 87403.0833 | 97807.5 | 100439.9167 | 99822.5
FCAS - Outage | 6087.5833 | 18781.8333 | 15954.5833 | 10797.6667 | 16226 | 6607.1667
System Normal | 4947.25 | 8902 | 12236.5 | 17536.9167 | 19035.9167 | 22704.3333
Network Support | 210.3333 | 74.25 | 123.4167 | 49.4167 | 547.3333 | 515.3333
Negative Residues | 10.4167 | 24.1667 | 31.25 | 126.0833 | 135.9167 | 243.5833
Outage | 4817.0833 | 9302.6667 | 13833.9167 | 13369.5 | 29818.1667 | 18765
Total (non-FCAS) | 22101.0833 | 28692.3333 | 33790.0833 | 41519.25 | 57836 | 53069.5833
Binding Impact
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Commissioning | 48442546.0203 | 68138620.5509 | 20610054.6861 | 29730094.3355 | 12546266.9298 | 2194509.3174
FCAS - NIL | 8309289.3932 | 10234061.3339 | 8943329.8904 | 9672529.6493 | 22163892.499 | 7194067.6289
FCAS - Outage | 3254616.4004 | 4516120.6054 | 20016451.5307 | 13236795.0138 | 31903432.4496 | 1654234.1154
System Normal | 20382744.3293 | 37998718.3151 | 76132971.008 | 98704424.3792 | 189629359.6493 | 145065771.5209
Network Support | 30414067.7368 | 683796.7041 | 243610.7044 | 1310271.1961 | 51806950.8047 | 23221155.9163
Negative Residues | 190929.9383 | 357086.6257 | 778063.9302 | 5915845.9777 | 3236834.8784 | 1212709.4364
Outage | 10352560.2034 | 45175949.9811 | 60788869.0394 | 83834215.4721 | 249239553.245 | 80481277.6267
Total | 121346754.0216 | 167104354.1161 | 187513350.7893 | 242404176.0239 | 560526290.4558 | 261023725.5619

## Interconnector Binding
Interconnector Direction | Constraint Equation ID | 2023 Hours | 2022 Hours | Description | Type
N-Q-MNSP1 Export | N^N-LS_SVC | 3028.1667 | 4283.1667 | Out= Lismore SVC O/S or reactive power control mode,avoid Voltage collapse on TL 87/89 trip;[Swamped for 3 DLK cables are O/S Or when ECS is enabled with DLK is exporting to QLD,sets DLK to -29 MW for -29< DLK FLOW<0, checks ETS status & unswamps if O/S) | Outage
N-Q-MNSP1 Export | N_X_MBTE_3A | 171 | 298.1667 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Export | N>NIL_LSDU | 139.8333 | 0.58333 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Export | N^^Q_LS_SVC_KPP_1 | 64.5833 | 0.91667 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage Collapse on loss of Kogan Creek MW | Outage
N-Q-MNSP1 Export | N>Q-NIL_757_758 | 54.6667 | 58.9167 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL
N-Q-MNSP1 Export | NQTE_ROC | 38.5 | 31.6667 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Export | N>>NIL_33_34 | 30.9167 | 0 | Out= Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL
N-Q-MNSP1 Export | N^^Q_DM_TW_SVC_B1 | 24.5833 | 0 | Out = Dumaresq or Tamworth SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N^N-X_LS_SVC+96R | 20.25 | 0 | Out= Lismore SVC + 96R/96L O/S, avoid Voltage collapse on TL (87) trip; [Swamped for 3 DLK cables are O/S Or when ECS is enabled with DLK is exporting to QLD,sets DLK to -29 MW for -29< DLK FLOW<0, checks ETS status & unswamps if O/S) | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 16.5 | 4.8333 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | N^N_KKLS_1 | 16 | 0 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage
N-Q-MNSP1 Export | N_X_MBTE2_A | 14.9167 | 0.25 | Out= two Directlink cables, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N::Q_8C8J_KC_N-2 | 8.8333 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage
N-Q-MNSP1 Export | N>GITN-96R_967_89 | 6.8333 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89),(Noted: Swamped out when 967 O/S) | Outage
N-Q-MNSP1 Export | N::Q_NIL_KC | 6.6667 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL
N-Q-MNSP1 Export | N::Q_DM_TW_SVC_KC | 5.5 | 0 | Out = Dumaresq or Tamworth SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
N-Q-MNSP1 Export | Q>>BCRG_BCCP_CLWU | 4.5 | 1.9167 | Out= Bouldercombe to Raglan (811), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
N-Q-MNSP1 Export | N>N-BAMB_132_OPEN_A | 2.75 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage
N-Q-MNSP1 Export | N::Q_MUTW_1 | 1.75 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
N-Q-MNSP1 Export | N^^Q_ARTW_B1 | 1.75 | 6.1667 | Out = Armidale to Tamworth (85 or 86 or 8U), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
N-Q-MNSP1 Export | QNTE_OSCILLATE | 1.0833 | 1.6667 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage
N-Q-MNSP1 Export | N::Q_AR_VC_KC | 1 | 0 | Out= Armidale SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
N-Q-MNSP1 Export | N::Q_ARSR_1 | 0.91667 | 0 | Out= Armidale - Saphhire (8E) 330kV line, NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 0.83333 | 0.66667 | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Export | Q>>LCCP_BCCP_CLWU | 0.75 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
N-Q-MNSP1 Export | #R026958_005_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 19/04/2022, Version: 1 | Other
N-Q-MNSP1 Export | #R027255_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R028534_005_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 11/08/2023, Version: 1 | Other
N-Q-MNSP1 Export | F_Q++MUTW_R6 | 0.66667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | F_Q++MUTW_R60 | 0.5 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N^^Q_MIMR_TWO_B1 | 0.5 | 0 | Out = Two parallel feeders between R4 Millmerran to H14 Middle Ridge (9914+9915 or 9908+9907), avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | #R026818_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R027110_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^N-X_LS_SVC+96R, Effective Date: 02/03/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R026824_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R026863_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R027921_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N::Q_AR_VC_KC, Effective Date: 12/12/2022, Version: 1 | Other
N-Q-MNSP1 Export | #R028225_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R028306_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R029298_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R029298_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R029309_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 11/08/2023, Version: 1 | Other
N-Q-MNSP1 Export | F_Q++MUTW_R5 | 0.33333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | N::Q_BWTX_KC | 0.33333 | 0 | Out= Bayswater 500/330kV tie Tx, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
N-Q-MNSP1 Export | N>96L_967_89 | 0.33333 | 0 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), TG formulation in PD/ST(Noted: Swamped out when 967 O/S) | Outage
N-Q-MNSP1 Export | NQTE_090 | 0.33333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of 90 MW | Outage
N-Q-MNSP1 Export | #R027074_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R027921_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N::Q_AR_VC_KC, Effective Date: 12/12/2022, Version: 1 | Other
N-Q-MNSP1 Export | #R028078_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N::Q_MUTW_1, Effective Date: 27/04/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R028099_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R028099_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R028306_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R028703_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N::Q_ARSR_1, Effective Date: 27/04/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R028897_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R029169_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 11/08/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R029309_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 11/08/2023, Version: 1 | Other
N-Q-MNSP1 Export | N::Q_TW_SVC_TNT | 0.25 | 0 | Out = Tamworth SVC, NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage
N-Q-MNSP1 Export | N>BWLD33_BWLD34 | 0.25 | 0 | Constraint Automation, O/L 34:LN34:Z:330@BAYSWATR@NSW for CTG LNPI on trip of BAYSWATR-LIDDELL 33 330KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | NRM_NSW1_QLD1 | 0.25 | 0.58333 | Negative Residue Management constraint for NSW to QLD flow. | NIL
N-Q-MNSP1 Export | #R026863_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R027207_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q^^TR_TRBK_-400, Effective Date: 08/03/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R027255_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R027936_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N::Q_LDTM_LDTW, Effective Date: 26/09/2022, Version: 2 | Other
N-Q-MNSP1 Export | #R028078_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>>88_84_QGEN_N, Effective Date: 09/11/2022, Version: 1 | Other
N-Q-MNSP1 Export | #R028703_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N::Q_ARSR_1, Effective Date: 27/04/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R029185_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | F_Q++8U_R60 | 0.16667 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N>>NIL_84_83_OPEN | 0.16667 | 0 | Out = Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
N-Q-MNSP1 Export | NQTE_-090 | 0.16667 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -90 MW | Outage
N-Q-MNSP1 Export | Q>>BCCP_BCRG_CLWU | 0.16667 | 0 | Out= Bouldercombe to Calliope River (812), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
N-Q-MNSP1 Export | #R027936_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::Q_LDTM_LDTW, Effective Date: 26/09/2022, Version: 2 | Other
N-Q-MNSP1 Export | #R028038_007_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 27/04/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R028225_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R028265_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::Q_LDTW_1, Effective Date: 27/04/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R028265_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N::Q_LDTW_1, Effective Date: 27/04/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R028756_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R029080_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q>>BCRG_BCCP_CLWU, Effective Date: 06/10/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R029169_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_LS_SVC_KPP_1, Effective Date: 30/01/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R029206_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R029308_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 11/08/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R029308_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_LS_SVC_KPP_1, Effective Date: 30/01/2023, Version: 1 | Other
N-Q-MNSP1 Export | #R029309_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_LS_SVC_KPP_1, Effective Date: 30/01/2023, Version: 1 | Other
N-Q-MNSP1 Export | N::Q_8C8J_LDTW_N-2 | 0.083333 | 0 | Out = Nil, NSW to Qld Transient Stability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage
N-Q-MNSP1 Export | N::Q_LDTM_KC | 0.083333 | 0 | Out= Liddell-Tomago (82), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
N-Q-MNSP1 Import | N>>NIL_964_84_S | 777 | 0 | Out= NIL, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Liddell (84) line, Feedback | NIL
N-Q-MNSP1 Import | N_X_MBTE_3B | 220.8333 | 141.9167 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Import | N_MBTE1_B | 208.4167 | 102.4167 | Out= one Directlink cable, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N>NIL_MBDU | 108.5833 | 42.3333 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Import | N>>NIL_84_88_S | 65.4167 | 33.9167 | Out= NIL, avoid O/L Tamworth to Liddell (84) using 15 min rating on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL
N-Q-MNSP1 Import | N_NIL_TE_B | 59.5 | 92.75 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL
N-Q-MNSP1 Import | N>>NIL_86_85_S | 45.5 | 0 | Out= NIL, avoid O/L Armidale to Tamworth (86) on trip of Uralla to Tamworth (85) line, Feedback | NIL
N-Q-MNSP1 Import | QNTE_ROC | 44.3333 | 34.4167 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | N>>964_86_85_S | 43.6667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Armidale to Tamworth (86) on trip of Uralla to Tamworth (85) line, Feedback | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 34.5 | 0.25 | Out= two Directlink cables, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N>>NIL_86_8U_S | 23.1667 | 49.5 | Out= NIL, avoid O/L Armidale to Tamworth (86) using 15 min rating on trip of the other Armidale to Uralla line (8U), Feedback | NIL
N-Q-MNSP1 Import | N>>NIL_88_84_S | 22.4167 | 9.25 | Out= NIL, avoid O/L Tamworth to Muswellbrook (88) using 15 min rating on trip of Tamworth to Liddell (84) line, Feedback | NIL
N-Q-MNSP1 Import | N>>NIL_85_86_S | 22.0833 | 0 | Out= NIL, avoid O/L Uralla to Tamworth (85) on trip of Armidale to Tamworth (86) line, Feedback | NIL
N-Q-MNSP1 Import | F_Q++86_L6 | 20.6667 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N>>964_85_86_S | 15.9167 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Uralla to Tamworth (85) on trip of Armidale to Tamworth (86) line, Feedback | Outage
N-Q-MNSP1 Import | N>>17_39_11 | 12.9167 | 0 | Out = Avon-Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 10.8333 | 33.1667 | Negative Residue Management constraint for QLD to NSW flow | NIL
N-Q-MNSP1 Import | N>>LDTM_964_81_OPEN | 10.5 | 5.25 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage
N-Q-MNSP1 Import | N>>81_964_82 | 10.25 | 3.25 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, (Note: Swamps if 964 O/S) | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L6 | 9.5833 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N>>964_8U_86_S | 8.5833 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Armidale to Uralla (8U) on trip of Armidale to Tamworth (86) line, Feedback | Outage
N-Q-MNSP1 Import | N>>NIL_8U_86_S | 7.75 | 0 | Out= NIL, avoid O/L Armidale to Uralla (8U) on trip of Armidale to Tamworth (86) line, Feedback | NIL
N-Q-MNSP1 Import | F_Q++MUTW_L5 | 6.1667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | Q>NIL_757_758_ECS | 6.1667 | 40 | Out= Nil, ECS for managing Mudgeeraba to Terranora (757 or 758) 110kV lines, Summer and Winter ECS ratings selected by SCADA status | NIL
N-Q-MNSP1 Import | F_Q++85_L6 | 5.8333 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L6 | 5.4167 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | Q>N-MUTE_758 | 4.9167 | 6.0833 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | N>N-BAMB_132_OPEN_B | 4.6667 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 Directlink cables O/S, feedback | Outage
N-Q-MNSP1 Import | N>96L/96R_967_89_S | 4.5 | 0 | Out= Lismore to Tenterfield (96L) or Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Lismore to Koolkhan (967) 132kV line on trip of Lismore to Coffs Harbour (89) 330kV line, Feedback | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L5 | 4 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | CA_BRIS_542A136B_1 | 3.8333 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage
N-Q-MNSP1 Import | N>N_LSDU_9U6_2 | 3.25 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage
N-Q-MNSP1 Import | F_Q++86_L5 | 2.75 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N>N-X_9U6_9G2_2 | 2.75 | 0 | Out = one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 132kV line between Mullumbimby and Ballina (9G2, 9G3, 9G4 or 9G5), avoid O/L remaining 132kV line, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N>>NIL_39_17 | 2.5833 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL
N-Q-MNSP1 Import | N>9U6/9U7_8507_9U7 | 1.9167 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L Balina to Astonville (8507) 66kV line on trip of other 9U7 or 9U6 132kV line, Feedback | Outage
N-Q-MNSP1 Import | N>>NIL_39_11 | 1.9167 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
N-Q-MNSP1 Import | I_CTRL_ISSUE_TE | 1.5 | 2.0833 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Import | N>>14_39_12 | 1.25 | 0 | Out = Kemps Creek to Sydney North (14), avoid O/L Bannaby to Sydney West (39) on trip of Sydney South to Liverpool (12) line, Feedback | Outage
N-Q-MNSP1 Import | N>>964_88_84_S | 1 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | Outage
N-Q-MNSP1 Import | CA_SYDS_549FBEF5_1 | 0.91667 | 0 | Constraint Automation, O/L XFMR 1_H4@H4_MUGBA@QLD for CTG TQHQ on trip of H4_MUGBA #5 TRANS. Generated by STNET[BNECR3] Host NORREGEEMP7(EMPSYD) | Outage
N-Q-MNSP1 Import | N>>81_964_84 | 0.83333 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tamworth (84) line,(Note: Swamps if 964 O/S) | Outage
N-Q-MNSP1 Import | F_Q++8U_L6 | 0.75 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | F_Q++85_L5 | 0.66667 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N>>NIL_964_88_S | 0.66667 | 0 | Out= NIL, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL
N-Q-MNSP1 Import | #R029063_015_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N>>81_964_82, Effective Date: 10/11/2023, Version: 1 | Other
N-Q-MNSP1 Import | Q>N-MUTE_757 | 0.58333 | 9.1667 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | #R026861_015_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N>>LDTM_964_81_OPEN, Effective Date: 12/01/2023, Version: 1 | Other
N-Q-MNSP1 Import | #R028897_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R026824_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R028756_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R029051_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R029185_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R029201_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R029206_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R026818_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R027074_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R027553_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_MBTE1_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | Q>GBMO_BLYTA_GBMO | 0.33333 | 0 | Out= 8824 or 8825 (S3 Greenbank to H4 Molendinar) 275kV line, avoid OL on 704 (T108 Beenleigh to Yatala) 132kV line on trip of remaining feeder 8824 or 8825, feedback | Outage
N-Q-MNSP1 Import | #R026818_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R028099_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R028640_018_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q:N_ARDM_A, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R029051_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | F_Q++8U_L5 | 0.25 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N>>NIL_966/1_87_S | 0.25 | 0 | Out=Nil, avoid O/L Metz Tee to Armidale (966/1) kV line on trip of Coffs Harbour to Armidale (87) 330kV line, Feedback | NIL
N-Q-MNSP1 Import | #R026824_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R027074_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R027934_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R028225_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R028756_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R029185_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R029201_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R029206_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | CA_BRIS_542A0DC2_1 | 0.16667 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage
N-Q-MNSP1 Import | CA_BRIS_542A114F_1 | 0.16667 | 0 | Constraint Automation, O/L 967:L967:I:132@LISMORE@NSW for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP5(EMPBRI) | Outage
N-Q-MNSP1 Import | QNTE_090 | 0.16667 | 0 | Qld to NSW on Terranora Interconnector upper transfer limit of 90 MW | Outage
N-Q-MNSP1 Import | QNTE_ZERO | 0.16667 | 0 | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW | Outage
N-Q-MNSP1 Import | #R026863_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R027934_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | F_Q++85_L60 | 0.083333 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | N>>11_39_17 | 0.083333 | 0 | Out = Dapto-Sydney South (11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage
N-Q-MNSP1 Import | N>>LDTM_964_81_CL | 0.083333 | 0 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV closed, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage
N-Q-MNSP1 Import | N>>LDTM_964_84_OPEN | 0.083333 | 0 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Liddell (84) line, Feedback | Outage
N-Q-MNSP1 Import | Q>N_LSLS_9U8 | 0.083333 | 0 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd, Swamp out when all 3 Directlink cable O/S. | Outage
NSW1-QLD1 Export | N^^Q_LS_SVC_KPP_1 | 121.8333 | 1.1667 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage Collapse on loss of Kogan Creek MW | Outage
NSW1-QLD1 Export | Q>>BCRG_CLWU_BCCP | 87.5833 | 34.9167 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | N>>NIL_33_34 | 72.4167 | 0 | Out= Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL
NSW1-QLD1 Export | N::Q_8C8J_KC_N-2 | 56.5833 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage
NSW1-QLD1 Export | N^^Q_DM_TW_SVC_B1 | 39.8333 | 0 | Out = Dumaresq or Tamworth SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | Q>>LCCP_CLWU_BCCP | 25.6667 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | N::Q_NIL_KC | 24.9167 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL
NSW1-QLD1 Export | NQ_750_DYN_TEST | 12.8333 | 0 | NSW to QLD on QNI upper transfer limit of 750 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage
NSW1-QLD1 Export | N::Q_DM_TW_SVC_KC | 9.3333 | 0 | Out = Dumaresq or Tamworth SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | N>>NIL_84_83_OPEN | 8.9167 | 5.8333 | Out = Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
NSW1-QLD1 Export | N::Q_ARSR_1 | 6.25 | 0 | Out= Armidale - Saphhire (8E) 330kV line, NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
NSW1-QLD1 Export | Q>>BCRG_BCCP_CLWU | 5.9167 | 2.25 | Out= Bouldercombe to Raglan (811), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
NSW1-QLD1 Export | F_Q++BCDM_R6 | 3.6667 | 0.16667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | F_Q++8E_R6 | 3.3333 | 1.1667 | Out = Sapphire to Armidale (8E) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N::Q_MUTW_1 | 2.75 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
NSW1-QLD1 Export | N::Q_BWTX_KC | 2.5 | 0 | Out= Bayswater 500/330kV tie Tx, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | N^^Q_ARTW_B1 | 2.3333 | 16.3333 | Out = Armidale to Tamworth (85 or 86 or 8U), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
NSW1-QLD1 Export | N::Q_AR_VC_KC | 1.5 | 0 | Out= Armidale SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | Q>>LCCP_BCCP_CLWU | 1.3333 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
NSW1-QLD1 Export | F_Q++MUTW_R60 | 1.25 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | Q>>NIL_BCCP_RGLC | 1.25 | 25.5 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL
NSW1-QLD1 Export | N::Q_8C8J_TNT_N-2 | 1.1667 | 0 | Out = Nil, NSW to Qld Transient Stability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage
NSW1-QLD1 Export | N^^Q_MIMR_TWO_B1 | 0.91667 | 0 | Out = Two parallel feeders between R4 Millmerran to H14 Middle Ridge (9914+9915 or 9908+9907), avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | F_Q++MUTW_R6 | 0.83333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | #R029309_004_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint N^^Q_LS_SVC_KPP_1, Effective Date: 30/01/2023, Version: 1 | Other
NSW1-QLD1 Export | NRM_NSW1_QLD1 | 0.75 | 2.3333 | Negative Residue Management constraint for NSW to QLD flow. | NIL
NSW1-QLD1 Export | F_Q++8U_R60 | 0.58333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | #NSW1-QLD1_RAMP_I_F | 0.5 | 0 | NSW1-QLD1 >= MIN(-122, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Export | #R027744_007_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^Q_DM_TW_SVC_B1, Effective Date: 27/04/2023, Version: 1 | Other
NSW1-QLD1 Export | #R029167_003_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^Q_LS_SVC_KPP_1, Effective Date: 30/01/2023, Version: 1 | Other
NSW1-QLD1 Export | N::Q_MIMR_TWO_KC | 0.5 | 0 | Out = Two parallel feeders between R4 Millmerran to H14 Middle Ridge (9914+9915 or 9908+9907), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | N>BWLD33_BWLD34 | 0.5 | 0 | Constraint Automation, O/L 34:LN34:Z:330@BAYSWATR@NSW for CTG LNPI on trip of BAYSWATR-LIDDELL 33 330KV LINE. Generated by RTCA[EMS] | Outage
NSW1-QLD1 Export | F_Q++MUTW_R5 | 0.41667 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | #R027921_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N::Q_AR_VC_KC, Effective Date: 12/12/2022, Version: 1 | Other
NSW1-QLD1 Export | #R028703_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N::Q_ARSR_1, Effective Date: 27/04/2023, Version: 1 | Other
NSW1-QLD1 Export | #R029081_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint Q>>BCCP_CLWU_RGLC, Effective Date: 06/10/2023, Version: 1 | Other
NSW1-QLD1 Export | NQ_700_DYN_TEST | 0.33333 | 15.5833 | NSW to QLD on QNI upper transfer limit of 700 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage
NSW1-QLD1 Export | #R027911_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N::Q_AR_VC_KC, Effective Date: 12/12/2022, Version: 1 | Other
NSW1-QLD1 Export | #R027921_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N::Q_AR_VC_KC, Effective Date: 12/12/2022, Version: 1 | Other
NSW1-QLD1 Export | #R028078_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N::Q_MUTW_1, Effective Date: 27/04/2023, Version: 1 | Other
NSW1-QLD1 Export | N::Q_TW_SVC_TNT | 0.25 | 0 | Out = Tamworth SVC, NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage
NSW1-QLD1 Export | Q>>BCCP_CLWU_RGLC | 0.25 | 0 | Out= Bouldercombe to Calliope River (812), avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | #R027232_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 13/12/2022, Version: 1 | Other
NSW1-QLD1 Export | #R027936_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N::Q_LDTM_LDTW, Effective Date: 26/09/2022, Version: 2 | Other
NSW1-QLD1 Export | #R027936_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N::Q_LDTM_LDTW, Effective Date: 26/09/2022, Version: 2 | Other
NSW1-QLD1 Export | #R028065_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>>88_84_QGEN_N, Effective Date: 09/11/2022, Version: 1 | Other
NSW1-QLD1 Export | #R028078_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>>88_84_QGEN_N, Effective Date: 09/11/2022, Version: 1 | Other
NSW1-QLD1 Export | #R028703_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N::Q_ARSR_1, Effective Date: 27/04/2023, Version: 1 | Other
NSW1-QLD1 Export | #R029080_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q>>BCRG_BCCP_CLWU, Effective Date: 06/10/2023, Version: 1 | Other
NSW1-QLD1 Export | #R029167_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_LS_SVC_KPP_1, Effective Date: 30/01/2023, Version: 1 | Other
NSW1-QLD1 Export | #R029169_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_LS_SVC_KPP_1, Effective Date: 30/01/2023, Version: 1 | Other
NSW1-QLD1 Export | N>>24_93_90 | 0.16667 | 0 | Out = Eraring to Vales Point (24), avoid O/L Eraring to Newcastle (93) on trip of Eraring to Newcastle (90) line, Feedback | Outage
NSW1-QLD1 Export | Q>>BCCP_BCRG_CLWU | 0.16667 | 0 | Out= Bouldercombe to Calliope River (812), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
NSW1-QLD1 Export | #R027207_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q^^TR_TRBK_-400, Effective Date: 08/03/2023, Version: 1 | Other
NSW1-QLD1 Export | #R028038_007_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 27/04/2023, Version: 1 | Other
NSW1-QLD1 Export | #R028052_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>88_84_QGEN_N, Effective Date: 09/11/2022, Version: 1 | Other
NSW1-QLD1 Export | #R028078_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::Q_MUTW_1, Effective Date: 27/04/2023, Version: 1 | Other
NSW1-QLD1 Export | #R028265_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::Q_LDTW_1, Effective Date: 27/04/2023, Version: 1 | Other
NSW1-QLD1 Export | #R028265_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N::Q_LDTW_1, Effective Date: 27/04/2023, Version: 1 | Other
NSW1-QLD1 Export | F_Q++86_R60 | 0.083333 | 0 | Out = Armidale to Tamworth (86) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | F_Q++BCDM_R60 | 0.083333 | 0.16667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N::Q_8C8J_LDTW_N-2 | 0.083333 | 0 | Out = Nil, NSW to Qld Transient Stability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage
NSW1-QLD1 Export | N::Q_LDTM_KC | 0.083333 | 0 | Out= Liddell-Tomago (82), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Import | N>>NIL_964_84_S | 770.4167 | 0 | Out= NIL, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Liddell (84) line, Feedback | NIL
NSW1-QLD1 Import | N>>964_86_85_S | 79.6667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Armidale to Tamworth (86) on trip of Uralla to Tamworth (85) line, Feedback | Outage
NSW1-QLD1 Import | N>>NIL_84_88_S | 73.9167 | 41.75 | Out= NIL, avoid O/L Tamworth to Liddell (84) using 15 min rating on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL
NSW1-QLD1 Import | N>>NIL_86_85_S | 57.75 | 0 | Out= NIL, avoid O/L Armidale to Tamworth (86) on trip of Uralla to Tamworth (85) line, Feedback | NIL
NSW1-QLD1 Import | F_Q++BCDM_L6 | 37.3333 | 23.9167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | N>>NIL_85_86_S | 32.25 | 0 | Out= NIL, avoid O/L Uralla to Tamworth (85) on trip of Armidale to Tamworth (86) line, Feedback | NIL
NSW1-QLD1 Import | F_Q++86_L6 | 32.0833 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | N>>964_85_86_S | 30 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Uralla to Tamworth (85) on trip of Armidale to Tamworth (86) line, Feedback | Outage
NSW1-QLD1 Import | Q:N_1078 | 26.75 | 9.25 | QNI oscillatory stability limit of 1078 MW | Outage
NSW1-QLD1 Import | N>>NIL_88_84_S | 25.5833 | 11 | Out= NIL, avoid O/L Tamworth to Muswellbrook (88) using 15 min rating on trip of Tamworth to Liddell (84) line, Feedback | NIL
NSW1-QLD1 Import | N>>NIL_86_8U_S | 23.3333 | 61.25 | Out= NIL, avoid O/L Armidale to Tamworth (86) using 15 min rating on trip of the other Armidale to Uralla line (8U), Feedback | NIL
NSW1-QLD1 Import | Q::N_8C8J_AR_2LG_N-2 | 16.8333 | 2.8333 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage
NSW1-QLD1 Import | F_Q++8E_L6 | 14.0833 | 23.75 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | QN_1200_DYN_TEST | 13.3333 | 3.1667 | QLD to NSW on QNI upper transfer limit of 1200 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage
NSW1-QLD1 Import | N>>17_39_11 | 13.25 | 0 | Out = Avon-Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
NSW1-QLD1 Import | N>>LDTM_964_81_OPEN | 12.4167 | 5.25 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 12.0833 | 33.9167 | Negative Residue Management constraint for QLD to NSW flow | NIL
NSW1-QLD1 Import | N>>81_964_82 | 10.9167 | 3.25 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, (Note: Swamps if 964 O/S) | Outage
NSW1-QLD1 Import | N>>964_8U_86_S | 10.5 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Armidale to Uralla (8U) on trip of Armidale to Tamworth (86) line, Feedback | Outage
NSW1-QLD1 Import | Q^^N_TW+LS_SVC_SRAR | 10.1667 | 0 | Out = Tamworth SVC and Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage
NSW1-QLD1 Import | F_Q++MUTW_L6 | 9.8333 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | N>>NIL_8U_86_S | 9.1667 | 0 | Out= NIL, avoid O/L Armidale to Uralla (8U) on trip of Armidale to Tamworth (86) line, Feedback | NIL
NSW1-QLD1 Import | F_Q++85_L6 | 7.4167 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | Q^^N_LS_SVC_SRAR | 6.75 | 0 | Out = Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage
NSW1-QLD1 Import | F_Q++MUTW_L5 | 6.25 | 0 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++LDTW_L6 | 5.5 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++86_L5 | 4.6667 | 0 | Out = Armidale to Tamworth (86) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | QNI_SOUTH_1000_DYN | 4.25 | 0 | QLD to NSW on QNI upper transfer limit of 1000 MW, dynamic headroom with Max calc on the QNI, DS formulation only. | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 4.1667 | 4 | NSW1-QLD1 >= MIN(-122, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Import | F_Q++8C_L6 | 4 | 20.0833 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++LDTW_L5 | 4 | 0 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q^^N_AR+LS_SVC_SRAR | 3.5833 | 0 | Out = Lismore SVC + Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage
NSW1-QLD1 Import | Q^^N_NIL_SRAR | 3.1667 | 0.58333 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL
NSW1-QLD1 Import | N>>NIL_39_17 | 2.8333 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL
NSW1-QLD1 Import | F_Q++BCDM_L5 | 2.75 | 0.5 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q:N_1150 | 2.1667 | 0 | QNI oscillatory stability limit of 1150 MW | Outage
NSW1-QLD1 Import | N>>NIL_39_11 | 2 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
NSW1-QLD1 Import | N>>14_39_12 | 1.5833 | 0 | Out = Kemps Creek to Sydney North (14), avoid O/L Bannaby to Sydney West (39) on trip of Sydney South to Liverpool (12) line, Feedback | Outage
NSW1-QLD1 Import | N>>964_88_84_S | 1.4167 | 0.5 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | Outage
NSW1-QLD1 Import | Q:N_1110 | 1 | 0 | QNI oscillatory stability limit of 1110 MW | Outage
NSW1-QLD1 Import | N>>81_964_84 | 0.83333 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tamworth (84) line,(Note: Swamps if 964 O/S) | Outage
NSW1-QLD1 Import | F_Q++8U_L6 | 0.75 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | N>>NIL_964_88_S | 0.75 | 0 | Out= NIL, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL
NSW1-QLD1 Import | F_Q++85_L5 | 0.66667 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++NIL_R5 | 0.66667 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | #R029063_015_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N>>81_964_82, Effective Date: 10/11/2023, Version: 1 | Other
NSW1-QLD1 Import | #R026861_015_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N>>LDTM_964_81_OPEN, Effective Date: 12/01/2023, Version: 1 | Other
NSW1-QLD1 Import | #R027983_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint Q:N_1078, Effective Date: 24/07/2013, Version: 1 | Other
NSW1-QLD1 Import | F_Q++NIL_R60 | 0.41667 | 0.66667 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | #R027172_013_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint Q^^N_AR+LS_SVC_SRAR, Effective Date: 16/12/2022, Version: 1 | Other
NSW1-QLD1 Import | #R029049_015_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>>81_964_82, Effective Date: 10/11/2023, Version: 1 | Other
NSW1-QLD1 Import | F_Q++8E_L5 | 0.33333 | 1 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++NIL_R6 | 0.33333 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 6 sec requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | Q^^N_DM+LS_SVC_SRAR | 0.33333 | 0 | Out = Dumaresq SVC + Lismore SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage
NSW1-QLD1 Import | #R028640_018_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q:N_ARDM_A, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | F_Q++8U_L5 | 0.25 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | N>>NIL_8E_8C_S | 0.25 | 0 | Out = Nil, avoid O/L Sapphire to Armidale (8E) using 15 min rating on trip of Dumaresq to Armidale (8C) line, Feedback | NIL
NSW1-QLD1 Import | Q::N_30+38_AR_2L-G | 0.25 | 0 | Out = Liverpool to Sydney West (30) + Regentville to Sydney West (38) 330 kV lines, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | #R027983_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q:N_1078, Effective Date: 24/07/2013, Version: 1 | Other
NSW1-QLD1 Import | #R028073_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q^^N_88+LS_SVC_SRAR, Effective Date: 14/04/2023, Version: 1 | Other
NSW1-QLD1 Import | F_Q++8C_L5 | 0.16667 | 4.75 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | N>>LDTM_964_84_OPEN | 0.16667 | 0 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Tamworth to Liddell (84) line, Feedback | Outage
NSW1-QLD1 Import | #R027063_023_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q::N_30+38_AR_2L-G, Effective Date: 30/01/2023, Version: 1 | Other
NSW1-QLD1 Import | #R027394_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q:N_1110, Effective Date: 02-04-2020, Version: 1 | Other
NSW1-QLD1 Import | #R027781_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q:N_1078, Effective Date: 24/07/2013, Version: 1 | Other
NSW1-QLD1 Import | #R027876_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q^^N_AR+LS_SVC_SRAR, Effective Date: 24/05/2023, Version: 1 | Other
NSW1-QLD1 Import | #R028601_016_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q:N_790, Effective Date: 02/04/2020, Version: 1 | Other
NSW1-QLD1 Import | F_Q++85_L60 | 0.083333 | 0 | Out = Uralla to Tamworth (85) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++BCDM_L60 | 0.083333 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | N>>11_39_17 | 0.083333 | 0 | Out = Dapto-Sydney South (11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage
NSW1-QLD1 Import | N>>LDTM_964_81_CL | 0.083333 | 0 | Out = Liddell to Tomago (82) with Singleton-Kurri 132kV closed, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage
NSW1-QLD1 Import | QNI_SOUTH_1100_DYN | 0.083333 | 0 | QLD to NSW on QNI upper transfer limit of 1100 MW, dynamic headroom with Max calc on the QNI, DS formulation only. | Outage
NSW1-QLD1 Import | QN_1300_DYN_TEST | 0.083333 | 0 | QLD to NSW on QNI upper transfer limit of 1300 MW, dynamic headroom with Max calc on the QNI, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 863.5 | 358.4167 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 596.5833 | 906.9167 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 431.25 | 469.9167 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 311.6667 | 12.3333 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++RREG_0220 | 264.1667 | 75.5 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 111 | 11.1667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++GFT_TG_R60 | 57.4167 | 79.1667 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++GFT_TG_R5 | 53.9167 | 33.5 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L5 | 28.75 | 2.6667 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | T^V_NIL_9 | 23.8333 | 3.5 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | T_V_NIL_BL1 | 13.3333 | 12.3333 | Out=Nil, Basslink no go zone limits Tas to Vic. Limit Basslink upper limit to 125 MW on 1st DI out of no go zone. i.e. BL <= 125 MW | NIL
T-V-MNSP1 Export | F_T++LREG_0050 | 11.1667 | 44.75 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++TTS_TG_R60 | 9.5 | 42.5833 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | V>>NIL_SMTX_SMTX_R5 | 9.4167 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 500kV mode, Feedback | NIL
T-V-MNSP1 Export | TVBL_ROC | 9.1667 | 5.5 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Export | F_MAIN++TTS_TG_R5 | 7.8333 | 7.5 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++GFT_TG_R6 | 5.75 | 21.5833 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | V>>NIL_SMTX_SMTX_R2 | 5.1667 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 220kV mode, Feedback | NIL
T-V-MNSP1 Export | V>>NIL_MLGT_MLGT_A | 4.0833 | 0 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | NIL
T-V-MNSP1 Export | V>>XGTML2_KTTX2_1_R2 | 2.8333 | 0 | Out= Geelong to Moorabool No.2 220kV line and Keilor A2 500/220kV transformer, avoid O/L Moorabool to Geelong No.1 220kV line on trip of Sydenham to Keilor 500kV line (offloading Keilor A4 500/220kV transformer), radial mode, YWPS1 on 220kV mode, Feedback | Outage
T-V-MNSP1 Export | T^V_NIL_8 | 2.4167 | 4.3333 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | T^V_HAPM_220_1 | 2.25 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage
T-V-MNSP1 Export | T^^V_GTHA_1 | 0.91667 | 0 | Out = George Town to Hadspen 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining George Town to Hadspen 220 kV line. | Outage
T-V-MNSP1 Export | #R027281_029_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | T^^V_GTSH_1 | 0.66667 | 0 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage
T-V-MNSP1 Export | #R027189_029_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R028735_027_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint T^^V_GTHA_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | F_MAIN++NIL_MG_R1 | 0.41667 | 0 | Out = Nil, Raise 1 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS. Requirement capped at 225 MW | Outage
T-V-MNSP1 Export | #R027139_009_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint T^^V_PMSH_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R028735_027_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint T^^V_GTHA_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | F_MAIN++TTS_TG_R6 | 0.33333 | 7.75 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++COGT_TL_L6 | 0.33333 | 0 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | #R027157_027_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint T^^V_GTHA_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R027157_027_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint T^^V_GTHA_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R027189_029_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R027329_029_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R027329_029_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | F_T++COGT_TL_L5 | 0.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T_BLINK_VT_NGZ | 0.25 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow < 0, Basslink Target MW <= 0, swamped if Basslink Metered Flow > -0.1 DS only. | NIL
T-V-MNSP1 Export | #R027090_019_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 10/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R028855_029_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | F_T++COGT_TL_L60 | 0.16667 | 0 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++CO_752_TL_L6 | 0.16667 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>MLSY_KTTX_SYML_5R | 0.16667 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | #R027281_029_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R027963_027_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint T^^V_GTHA_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R028631_027_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint T^^V_GTHA_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R028715_029_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R028755_027_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint T^^V_GTHA_1, Effective Date: 11/12/2018, Version: 1 | Other
T-V-MNSP1 Export | #R028883_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>SMF1_SMF2_NIL_R2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Export | F_T++CO_752_TL_L60 | 0.083333 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T::T_HA_GT_PM_6 | 0.083333 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 1000.3333 | 572.3333 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0210 | 459.5833 | 91.75 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 394.8333 | 522.0833 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V_T_NIL_FCSPS | 351.4167 | 159.8333 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL
T-V-MNSP1 Import | V::N_NILxxx | 237.1667 | 19.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L6 | 183.3333 | 301.6667 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++BIP_ML_L1 | 176.8333 | 0 | Out = Nil, Lower 1 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS. Requirement capped at 125 MW | Outage
T-V-MNSP1 Import | VT_ZERO | 131.25 | 91.25 | Vic to Tas on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R6 | 109.4167 | 20.8333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++BIP_ML_L6 | 105.3333 | 0.75 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 103.0833 | 134.9167 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | F_T++RREG_0050 | 101.6667 | 44.0833 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T+NIL_BL_R60_1 & F_T++NIL_BL_R60_x | 97.1667 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 400ms | NIL
T-V-MNSP1 Import | T::T_NIL_3 | 58.4167 | 118.1667 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL
T-V-MNSP1 Import | F_T+NIL_BL_R6_1 & F_T++NIL_BL_R6_x | 56.5 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 400ms | NIL
T-V-MNSP1 Import | T_ROCOF_3 | 52.6667 | 6.4167 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL
T-V-MNSP1 Import | T::T_HA_GT_PM_4 | 47.5 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 44.9167 | 2.3333 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_DDSM_V1 | 42.6667 | 179.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_X_SMSC_O1 | 40.5833 | 85.6667 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_HYSE_V2 | 37.8333 | 5.9167 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R60 | 35.4167 | 26.0833 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R5 | 33.75 | 27.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T_BLINK_TV_NGZ | 29.5833 | 37.4167 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 27.9167 | 9 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 25.5833 | 9 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 21.0833 | 8 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_HWSM_V1 | 16.5833 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | VTBL_ROC | 16.25 | 11.8333 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Import | V::N_JNWG_S2 | 14.75 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 13.9167 | 2.8333 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_X_SMSC_V1 | 12.9167 | 76.9167 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V_T_NIL_BL1 | 11.25 | 9.4167 | Out=Nil, Basslink no go zone limits Vic to Tas. Limit Basslink lower limit to -125 MW on 1st DI out of no go zone. i.e. BL >= -125 MW | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_APD_LD | 8.5 | 8.9167 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_SETB_O1 | 8 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_HYSE_S2 | 6.8333 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 6.3333 | 10.3333 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V^T_NIL_9 | 6.3333 | 23.9167 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL
T-V-MNSP1 Import | VT_250 | 6.0833 | 0 | Vic to Tas on Basslink upper limit of 250 MW | Outage
T-V-MNSP1 Import | V::N_MLTX_V1 | 5.5 | 0 | Out = Moorabool Transformer 500/220kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | T::T_GTHA_2 | 5.0833 | 0 | Out = George Town to Hadspen 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 3.9167 | 0.16667 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HYSE_V1 | 3.9167 | 2.75 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_HWSM_S1 | 3.6667 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
T-V-MNSP1 Import | V::N_JNWG_V2 | 3.6667 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++BIP_ML_L5 | 3.1667 | 0.083333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_HYTR_O1 | 3 | 1.4167 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_X_ARWBBA_S1 | 2.5 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 2.3333 | 14.3333 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_HYSE_S1 | 2.25 | 0.58333 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V:T_HAPM_BL_1 | 2 | 0 | Out = Hadspen to Palmerston 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to Palmerston 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | F_T++FA_B_N-2_TG_R6 | 1.75 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R60 | 1.6667 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HWSM_SD | 1.6667 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V:T_HAGT_BL_1 | 1.6667 | 0 | Out = Hadspen to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to George Town 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | V::N_X_ARWBBA_V1 | 1.5 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V_T_FCSPS_RAMP | 1.25 | 0 | Ramp down (200 MW per DI) Basslink (Vic to Tas) to 144 MW for outage of FCSPS | Outage
T-V-MNSP1 Import | F_T++FA_B_N-2_TG_R60 | 1.0833 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FASH_1_TG_R6 | 1 | 0 | Out= Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_X_ARWBBA_SD | 1 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V:T_SHGT_BL_1 | 1 | 0 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | F_QNV++HYTR_L60 | 0.91667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_ROSM_O1 | 0.91667 | 1.0833 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | F_T++BL_650_R60_2 | 0.83333 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage
T-V-MNSP1 Import | #R027271_028_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V:T_HAGT_BL_1, Effective Date: 20/01/2022, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++BIP_ML_L60 | 0.75 | 0.25 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R5 | 0.75 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, TAS Raise 5 min requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FASH_1_TG_R60 | 0.75 | 0 | Out=Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_MLMO_V2 | 0.75 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_MLTX_S1 | 0.75 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R028920_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint VT_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
T-V-MNSP1 Import | V::N_HYTR_V1 | 0.66667 | 0.66667 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | T_ROCOF_2 | 0.58333 | 0 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of TAS largest unit with Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL
T-V-MNSP1 Import | #R027313_004_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R029116_004_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | F_T++BL_650_R6_3 | 0.5 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage
T-V-MNSP1 Import | V::N_KGRC_O2 | 0.5 | 0 | Out = Kerang to Red Cliffs 220kV line (or any section in between), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | #R028070_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HYSE_S2, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028323_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028341_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028455_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028796_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R029116_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R029306_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++HYTR_L5 | 0.41667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_KMRC_O2 | 0.41667 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | #R027504_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027604_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027604_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027681_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_S1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027817_012_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027817_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028070_013_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_HYSE_S2, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028323_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028428_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KMRC_V1, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028665_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028724_028_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V:T_HAGT_BL_1, Effective Date: 20/01/2022, Version: 1 | Other
T-V-MNSP1 Import | #R028824_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_O2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028920_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VT_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++NIL_BL_L6 | 0.33333 | 10.5833 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | V::N_KMRC_O1 | 0.33333 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | #R027271_028_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V:T_HAGT_BL_1, Effective Date: 20/01/2022, Version: 1 | Other
T-V-MNSP1 Import | #R027313_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R027511_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HYTR_O1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027681_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028087_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028428_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KMRC_V1, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028494_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HYMO_O1, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028654_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 07/09/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028779_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028796_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R029217_009_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint VT_250, Effective Date: 08/01/2014, Version: 1 | Other
T-V-MNSP1 Import | #R029306_004_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | F_T++NIL_BLSPS_R6 | 0.25 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, FCSPS unavailable. DS Only | NIL
T-V-MNSP1 Import | V::N_SMTT_O2 | 0.25 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | VT_350 | 0.25 | 0 | Vic to Tas on Basslink upper limit of 350 MW | Outage
T-V-MNSP1 Import | #R027400_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R027511_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HYTR_O1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027919_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027923_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028209_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028217_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028338_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028710_039_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWG_SD, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028724_028_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V:T_HAGT_BL_1, Effective Date: 20/01/2022, Version: 1 | Other
T-V-MNSP1 Import | #R028741_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028779_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028807_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KMRC_V2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028869_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028871_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028874_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_SD, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R029014_020_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V:T_SHGT_BL_1, Effective Date: 20/01/2022, Version: 1 | Other
T-V-MNSP1 Import | #R029228_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint VT_250, Effective Date: 08/01/2014, Version: 1 | Other
T-V-MNSP1 Import | #T-V-MNSP1_RAMP_I_F | 0.16667 | 0 | T-V-MNSP1 >= MIN(-250, InitialFlow + 100) (Wt=35) | Other
T-V-MNSP1 Import | F_QNV++MLMO_L60 | 0.16667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++BL_650_R60_3 | 0.16667 | 0 | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage
T-V-MNSP1 Import | F_T++BL_650_R6_2 | 0.16667 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage
T-V-MNSP1 Import | F_T++FASH_1_TG_R5 | 0.16667 | 0 | Out= Farrell to Sheffield No.1 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tas Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDSM_S1 | 0.16667 | 21.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_ROSM_O2 | 0.16667 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | V_T_FCSPS_DS | 0.16667 | 0 | Basslink limit from Vic to Tas for FCSPS scheme outage, DS only. Swamped when FCSPS scheme in service and load available for arming | NIL
T-V-MNSP1 Import | #R027271_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R027333_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027586_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_V1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027681_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HYSE_S1, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R027923_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028087_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028087_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_SD, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028338_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028338_013_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_V1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028338_013_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_V1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028455_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028654_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028665_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028723_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028727_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028788_028_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V:T_HAGT_BL_1, Effective Date: 20/01/2022, Version: 1 | Other
T-V-MNSP1 Import | #R028807_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028812_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
T-V-MNSP1 Import | #R028869_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S1, Effective Date: 15/06/2023, Version: 1 | Other
T-V-MNSP1 Import | #R029217_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VT_250, Effective Date: 08/01/2014, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++HYTR_L6 | 0.083333 | 0.083333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++BLSPS_IMP_R60_1 | 0.083333 | 0 | Limit Basslink import to levels where no FCSPS action is required for loss of Basslink, Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Import | F_T++FA_B_N-2_TG_R5 | 0.083333 | 0 | Out = FA 2220kV Bus B, loss of FA 220kV Bus A declared credible, TAS Raise 5 min requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_BL_R6_4 | 0.083333 | 0 | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 4, FCSPS available | NIL
T-V-MNSP1 Import | V::N_MLMO_V1 | 0.083333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>NIL_MHNW1_MHNW2 | 1258.9167 | 1465 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL
V-S-MNSP1 Export | V^^N_NIL_1 | 468.6667 | 72.5833 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
V-S-MNSP1 Export | S>NIL_NWRB2_NWRB1 | 372 | 211.6667 | Out= NIL, avoid O/L North West Bend-Roberstown #1 132kV line on trip of North West Bend-Robertstown #2 132kV line (this trips MWP1-3 SFs), Feedback | NIL
V-S-MNSP1 Export | V^^N_LTUT_1 | 205.5 | 0 | Out = Lower to Upper Tumut (64) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V::N_NILxxx | 187.5833 | 21.75 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL
V-S-MNSP1 Export | V^SML_BUDP_3 | 153.1667 | 16.5833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V^^N_DTKV_1 | 99.4167 | 30.3333 | Out = Dapto - Kangaroo Valley (18) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | VSML_ROC_80 | 73.8333 | 72.5 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Export | V>>NIL_BABE_HOMRKM | 60.25 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Export | V::N_DDSM_V1 | 46.6667 | 158.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_X_SMSC_O1 | 43.0833 | 73.9167 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V^^SML_NIL_3 | 41.0833 | 0.083333 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL
V-S-MNSP1 Export | S>>RBTU_RBPA_WTTP | 38.1667 | 1.0833 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>RBTX_WEWT_RBTX | 35.5833 | 70.4167 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage
V-S-MNSP1 Export | V>>N_NIL_65_66 | 31.25 | 75.9167 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
V-S-MNSP1 Export | V>>NIL_MBDD_MBDD | 26.5833 | 0 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Export | S>>NIL_TWPA_TPRS | 24.8333 | 14.0833 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_HYSE_V2 | 24.75 | 3.5 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>RBTU_N-2_WEWT | 24.1667 | 0 | Out= Nil, avoid O/L Waterloo East to Waterloo #1 132kV line on trip of Robertstown - Tungkillo 275kV line 1 and 2, Feedback | Outage
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 21.25 | 5.0833 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | S>>BWMP_TWPA_TPRS | 20 | 42.0833 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V^SML_HORC_3 | 19.8333 | 0 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | N>>DPTX1-2_TX_NIL | 19.1667 | 0 | Out= one Darlington Pt 132/330kV TX1 or TX2, avoid O/L remaining Darlington Pt 132/330kV TX on trip of Nil, Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_TWPA_TPRS | 18.6667 | 0.25 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+RBTX_13 | 18.25 | 13.8333 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Waterloo-Templers 132kV line on trip of remaining Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_N-2_WTTP | 18.0833 | 0 | Out= Nil, avoid O/L Waterloo to Templers 132kV line on trip of Robertstown - Tungkillo 275kV line 1 and 2, Feedback | Outage
V-S-MNSP1 Export | V^^SML_ARWBBA_1 | 17.75 | 0 | Out = Ballarat to Waubra to Ararat 220kV line (or any line section between Ballarat and Ararat), avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | VSML_030 | 17.3333 | 0 | Vic to SA on ML upper transfer limit of 30 MW | Outage
V-S-MNSP1 Export | V^^SML_NSWRB_2 | 16.25 | 78.5 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL
V-S-MNSP1 Export | V::N_HWSM_V1 | 16.1667 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WTTP | 15.9167 | 15.1667 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_JNWG_S2 | 15.5833 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>PA6509_BWPA_WTTP | 14.6667 | 0 | Out= Para 275kV CB6509, avoid O/L Waterloo-Templers 132kV line on trip of Munno Para-Para 275kV line (this offloads Tungkillo-Para 275kV line 2 & Blyth West-Munno Para 275kV line & Munno Para TX), Feedback | Outage
V-S-MNSP1 Export | V^^N_DPWG_X5_1 | 13.8333 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V::N_X_SMSC_V1 | 12.8333 | 52.3333 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | S>>X_CNRB+RBTX_22 | 12.25 | 0 | Out= One Robertstown TX + Canowie-Robertstown 275kV line O/S, avoid O/L Templers-Roseworthy 275kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>MKRB_TWPA_TPRS | 11.6667 | 33.5 | Out= Mokota-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V^^N_DTSS_1 | 11.5833 | 0 | Out = Dapto-Sydney South(11), avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V^^N_UTRV_1 | 10.4167 | 3.75 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | S>>RBTU_RBTU_WTTP | 9.6667 | 0 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Waterloo to Templers 132kV line on trip of Robertstown to Tungkillo 275kV line 1 or 2, Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_RBPA_WEWT | 9.5 | 14.1667 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>SMLMHNW1 | 9.4167 | 0 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-S-MNSP1 Export | VSML_110 | 9.4167 | 1.6667 | Vic to SA on ML upper transfer limit of 110 MW | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WEWT | 9.1667 | 23.3333 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>S_WERB_TWPA_TPRS | 9.0833 | 0 | Out= Robertstown - MWP4 - Waterloo East O/S(offloads MWP4 SF), avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_5 | 9 | 16.9167 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Export | S>>X_RBTU+RBTX_10 | 8.3333 | 11.4167 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Templers- Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTX+MNWT_24 | 7.6667 | 0 | Out= One Robertstown 275/132 kV TX + Mintaro-Waterloo 132 kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX2 on trip of Waterloo East-Waterloo 132 kV line, Feedback | Outage
V-S-MNSP1 Export | V>>NIL_SMTX_SMTX_R5 | 7.3333 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 500kV mode, Feedback | NIL
V-S-MNSP1 Export | S>>RBTX1_RBTX2_WEWT | 6.8333 | 0 | Out= one Robertstown 275/132kV TX, avoid O/L Waterloo East-Waterloo 132kV line on trip of remaining Robertstown 132/275kV TX, Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_25 | 6.75 | 93.6667 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Export | VSML_020 | 6.6667 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage
V-S-MNSP1 Export | VSML_165 | 6.5833 | 6.1667 | Vic to SA on ML upper transfer limit of 165 MW | Outage
V-S-MNSP1 Export | V^^N_SDUT_1 | 6.3333 | 0 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V::N_SETB_O1 | 6.25 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V^^N_HWSM_1 | 5.5833 | 0 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | S>>WEWT_BWPA_WTTP | 5.4167 | 0 | Out= Waterloo East-Waterloo 132kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_MLTX_V1 | 5.4167 | 0 | Out = Moorabool Transformer 500/220kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V^^N_CRGR_1 | 5.4167 | 0 | Out = Crookwell to Gullen Range (3H), avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V>>V_DDSM_1 | 5.25 | 124.6667 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WTTP | 5 | 12.75 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of one Robertstown - Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | VSML_100 | 4.8333 | 0 | Vic to SA on ML upper transfer limit of 100 MW | Outage
V-S-MNSP1 Export | V>>NIL_SMTX_SMTX_R2 | 4.3333 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 220kV mode, Feedback | NIL
V-S-MNSP1 Export | V::N_JNWG_V2 | 4 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>X_RBPA+RBTX2_22 | 3.75 | 33.4167 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo-Templers 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HWSM_S1 | 3.5833 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-S-MNSP1 Export | S>>X_CR+RBTX+TPRS_13 | 3.5 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Export | S>>BWMP_BRTW_WTTP | 3.3333 | 1.6667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage
V-S-MNSP1 Export | N>>V_NIL_0X1_60 | 3.25 | 0.33333 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL
V-S-MNSP1 Export | V>>ARWB_X3_BEKG | 3.25 | 0 | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V::N_HYTR_O1 | 3.0833 | 0.33333 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V^SML_KGRC_4 | 3.0833 | 0 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage
V-S-MNSP1 Export | S>>RBTU_RBTU_WEWT | 2.8333 | 0 | Out= Robertstown-Tungkillo 275kV line 1 or 2, avoid O/L Waterloo East to Waterloo #1 132kV line on trip of Robertstown to Tungkillo 275kV line 1 or 2, Feedback | Outage
V-S-MNSP1 Export | VSML_ZERO | 2.75 | 2.5833 | Vic to SA on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | S>>X_RBPA+RBTX2_16 | 2.6667 | 20.0833 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo East-Waterloo 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage
V-S-MNSP1 Export | VSML_060 | 2.6667 | 0 | Vic to SA on ML upper transfer limit of 60 MW | Outage
V-S-MNSP1 Export | V::N_HYSE_S2 | 2.5833 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HYSE_V1 | 2.5833 | 3.25 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>N_NIL_65 | 2.5833 | 5.6667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | S>>PA6509_BWPA_RBTU | 2.5 | 0 | Out= Para 275kV CB6509, avoid O/L Robertstown-Tungkillo 275kV line 1 or 2 on trip of Munno Para-Para 275kV line (this offloads Tungkillo-Para 275kV line 2 & Blyth West-Munno Para 275kV line & Munno Para TX), Feedback | Outage
V-S-MNSP1 Export | V>>NIL_ARTSTL_ARCW | 2.5 | 0 | Out = Nil, avoid O/L Ararat to Stawell 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service, Feedback | NIL
V-S-MNSP1 Export | V::N_X_ARWBBA_S1 | 2.25 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>RBTX_TWPA_TPRS | 2.0833 | 16.0833 | Out= one Robertstown 275/132kV transformed, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_CNRB+RBTX1_07 | 1.5833 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line O/S, avoid O/L of remaining Robertstown 132/275kV TX on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Export | V::N_HYSE_S1 | 1.5833 | 0.58333 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_X_ARWBBA_V1 | 1.5 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>NIL_BABE_KMRC | 1.4167 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL
V-S-MNSP1 Export | V^^N_2_6X_3J_1 | 1.4167 | 0 | Out = Ravine-Yass or Upper Tumut to Ravine (2 or 6X) 330kV line and Gullen Range to Yass (3J), avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | #R028387_006_RAMP_F | 1.3333 | 0 | Hard Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | S>>BRTW_BWPA_WTTP | 1.3333 | 1.3333 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HWSM_SD | 1.3333 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | S>>NIL_RBTX_RBTX_2 | 1.25 | 0.083333 | Out= Nil, avoid O/L of one Robertstown 132/275kV TX on trip of other Robertstown 132/275kV TX, Feedback | NIL
V-S-MNSP1 Export | S>>RBTX1_RBTX2_WTTP | 1.25 | 0 | Out= one Robertstown 275/132kV TX, avoid O/L Waterloo-Templers 132kV line on trip of remaining Robertstown 132/275kV TX, Feedback | Outage
V-S-MNSP1 Export | V>>DDTX2_DDTX3_DDTX1 | 1.25 | 0 | Out= Dederang H2 txfmr, avoid O/L Dederang H3 330/220kV txfmr on trip of Dederang H1 330/220kV txfmr, Feedback | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_RBMWP4 | 1.1667 | 0.41667 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+RBTX_14 | 1.0833 | 24.4167 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of remaining Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_ROSM_O1 | 1.0833 | 1 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | #R027988_014_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint S>>RBTU_RBPA_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | VSML_FLT_150 | 0.91667 | 0 | Vic to SA on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to voltage oscillation | Outage
V-S-MNSP1 Export | #R027148_019_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint S>>BWMP_TWPA_TPRS, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R027778_004_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028238_011_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint S>S_WERB_TWPA_TPRS, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028807_021_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | S>>X_CR+RBTX+TPRS_04 | 0.83333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTX+MNWT_18 | 0.83333 | 0 | Out= One Robertstown 275/132 kV TX + Mintaro-Waterloo 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage
V-S-MNSP1 Export | V::N_MLTX_S1 | 0.83333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>SML_NIL_7B | 0.83333 | 0.16667 | Out = Nil, avoid O/L Buangor to Ararat 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL
V-S-MNSP1 Export | VSML_085 | 0.83333 | 0 | Vic to SA on ML upper transfer limit of 85 MW | Outage
V-S-MNSP1 Export | #R028984_031_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R029255_001_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | V::N_MLMO_V2 | 0.75 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | #R028128_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S>>PA6509_BWPA_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028860_021_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | S>>NIL_BWMP_WTTP | 0.66667 | 0.16667 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_HYTR_V1 | 0.66667 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V^^N_JNWG_1 | 0.66667 | 0 | Out = Jindera to Wagga (62) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | #R026783_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026820_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R027210_018_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 20/09/2022, Version: 1 | Other
V-S-MNSP1 Export | #R027918_004_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint S>>X_CR+RBTX+TPRS_04, Effective Date: 02/06/2023, Version: 1 | Other
V-S-MNSP1 Export | V::N_KMRC_O1 | 0.58333 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | #R026816_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026850_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint VSML_085, Effective Date: 13/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R026851_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint VSML_110, Effective Date: 24/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R027402_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S>>WEWT_BRTW_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R029249_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | S>>NIL_RBTU_RBTU | 0.5 | 0 | Out= NIL, avoid O/L Robertstown-Tungkillo 275kV line 1 or 2 on trip of parallel Robertstown-Tungkillo 275kV line 2 or 1, Feedback | NIL
V-S-MNSP1 Export | VSML_010 | 0.5 | 0 | Vic to SA on ML upper transfer limit of 10 MW | Outage
V-S-MNSP1 Export | VSML_025 | 0.5 | 0 | Vic to SA on ML upper transfer limit of 25 MW | Outage
V-S-MNSP1 Export | V^^N_BADP_1 | 0.5 | 0 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | #R026783_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026804_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026827_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint VSML_110, Effective Date: 24/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026827_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_110, Effective Date: 24/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026851_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_110, Effective Date: 24/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R027019_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint VSML_110, Effective Date: 24/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R027019_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_110, Effective Date: 24/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R027057_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_135, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R027216_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_135, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R027217_019_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027615_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R027923_011_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027970_073_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028070_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HYSE_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028128_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>>PA6509_BWPA_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028215_022_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S>>BWMP_TWPA_TPRS, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028226_021_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 20/02/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028323_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028341_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028380_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V>>DDSM_BABE_SMDD, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028421_021_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028435_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R028455_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028480_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R028886_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R029249_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | S>>WERB_BWPA_WTTP | 0.41667 | 0 | Out= Robertstown - MWP4 - Waterloo East O/S(offloads MWP4 SF), avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_KGRC_O2 | 0.41667 | 0 | Out = Kerang to Red Cliffs 220kV line (or any section in between), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | V::N_KMRC_O2 | 0.41667 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | V>>CWHO_X3_BEKG | 0.41667 | 0 | Out = Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | #R026804_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026820_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R027366_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R027413_026_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^N_LTUT_1, Effective Date: 21/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027504_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027547_031_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027604_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027681_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027790_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027817_012_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027817_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027992_078_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028170_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint S>>BWMP_BRTW_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028215_022_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>BWMP_TWPA_TPRS, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028323_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028380_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>DDSM_BABE_SMDD, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028428_021_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028654_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 07/09/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028710_055_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028796_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028824_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028846_021_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028846_021_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R029231_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^N_DTSS_1, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | S>>BWMP_RBTU_RBPA | 0.33333 | 0.66667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Robertstown-Para 275kV line on trip of Robertstown -Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>MLSY_KTDPT_SYML | 0.33333 | 0 | Out = Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid O/L Keilor to Deer Park 220 kV line on trip of remaining Moorabool to Sydenham 500 kV line, feedback | Outage
V-S-MNSP1 Export | V>>S_MWP3RB_NWRB1 | 0.33333 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L North West Bend-Roberstown #1 132kV line on Nil trip, Feedback | Outage
V-S-MNSP1 Export | VSML_195 | 0.33333 | 1.0833 | Vic to SA on ML upper transfer limit of 195 MW | Outage
V-S-MNSP1 Export | #R027210_018_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 20/09/2022, Version: 1 | Other
V-S-MNSP1 Export | #R027227_018_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^^N_2_6X_3J_1, Effective Date: 06/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027333_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027511_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HYTR_O1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027547_031_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027604_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027681_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027753_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027790_004_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027923_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027992_078_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028087_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028215_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>BWMP_BRTW_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028238_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S>S_WERB_TWPA_TPRS, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028239_021_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 20/02/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028387_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028428_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KMRC_V1, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028494_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HYMO_O1, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028665_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028696_023_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>RBTX_WEWT_RBTX, Effective Date: 22/09/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028710_055_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028723_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028779_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028796_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028801_010_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028860_021_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | N>>NIL_DPTX_HV | 0.25 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL
V-S-MNSP1 Export | S>>NIL_RBTU_WEWT | 0.25 | 5 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of one Robertstown-Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>WEWT_TWPA_TPRS | 0.25 | 0 | Out= Waterloo East-Waterloo 132kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_ROSM_O2 | 0.25 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | V::N_SMTT_O2 | 0.25 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | #R026850_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VSML_085, Effective Date: 13/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027106_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R027217_019_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027227_018_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_2_6X_3J_1, Effective Date: 06/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027413_026_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_LTUT_1, Effective Date: 21/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027449_024_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>X_RBTX+MNWT_24, Effective Date: 06/04/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027586_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_V1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027753_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027881_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_DTSS_1, Effective Date: 01/05/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027919_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027988_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>>RBTU_RBPA_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028209_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028226_021_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 20/02/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028338_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028341_023_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>ARWB_X3_BEKG, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028421_021_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028428_021_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028479_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R028503_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_DTSS_1, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028710_039_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWG_SD, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028741_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028779_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028796_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028807_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KMRC_V2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028869_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028871_015_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028871_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028874_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_SD, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028874_026_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>ARCW_X3_BEKG, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | S>>RBTU_RBPA_BWMP | 0.16667 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Blyth West-Munno Para 275kV line on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_DDSM_S1 | 0.16667 | 21.8333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_X_ARWBBA_SD | 0.16667 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V>>KMCB_BABE_KMRC | 0.16667 | 0 | Out= Kiamal 220kV CB (one or more MR2B or 7422A or 7422B), avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | Outage
V-S-MNSP1 Export | V>>NIL_SMDD_SMDD | 0.16667 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Export | #R026935_020_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>RBTX_WEWT_RBTX, Effective Date: 27/10/2021, Version: 2 | Other
V-S-MNSP1 Export | #R027146_019_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>BWMP_TWPA_TPRS, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R027148_019_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>BWMP_TWPA_TPRS, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R027504_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027586_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027586_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027681_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HYSE_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R027923_024_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^SML_ARWBBA_1, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028087_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028215_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>BWMP_BRTW_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028338_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028338_013_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028338_013_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028341_026_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^SML_ARWBBA_1, Effective Date: 31/01/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028374_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>DDSM_BABE_SMDD, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028487_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | #R028527_026_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_LTUT_1, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028582_013_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>X_RBTU+RBTX_14, Effective Date: 15/09/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028665_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028665_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 07/09/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028727_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028807_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028812_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Export | #R028869_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-S-MNSP1 Export | #R029159_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>>S_MWP3RB_NWRB1, Effective Date: 15/10/2020, Version: 2 | Other
V-S-MNSP1 Export | S>>MKRB_BRTW_WTTP | 0.083333 | 0.16667 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>MKRB_BWMP_WTTP | 0.083333 | 0.16667 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_CR+RBTX+TPRS_15 | 0.083333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L Templers West-Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+RBTX_01 | 0.083333 | 0 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown-Tungkillo 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>NIL_NIL_MHNW2 | 0.083333 | 0 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on Nil trip, Feedback | NIL
V-S-MNSP1 Export | V>>DBT_DDTX3_DDTX | 0.083333 | 0 | Out = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage Schemes), avoid O/L Dederang H3 330/220kV transformer for loss of Dederang H1 or H2 330/220kV transformer, feedback | Outage
V-S-MNSP1 Export | V>>MLSY_KTTX_SYML_5R | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage
V-S-MNSP1 Export | V>>NIL_BANBGR_ARCW | 0.083333 | 0 | Out = Nil, avoid O/L Ballarat North to Buangor 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service, Feedback | NIL
V-S-MNSP1 Export | V>>N_64_66_65_N | 0.083333 | 0 | Out = LowerTumut-UpperTumut (64), avoid Murray to Lower Tumut (66) O/L on Murray to Upper Tumut (65) trip; Feedback | Outage
V-S-MNSP1 Export | V>>N_NIL_66_65 | 0.083333 | 0.25 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL
V-S-MNSP1 Export | VSML_150 | 0.083333 | 0 | Vic to SA on ML upper transfer limit of 150 MW | Outage
V-S-MNSP1 Import | SVML_ZERO | 848.4167 | 543.5833 | SA to Vic on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Import | V^^V_NIL_KGTS | 757.25 | 496.9167 | Out= Nil, avoid voltage collapse for loss of Horsham - Murra Warra - Kiamal 220kV line. Murraylink VFRB disabled. Swamp if Murraylink VFRB enabled. | NIL
V-S-MNSP1 Import | SVML^NIL_MH-CAP_ON | 498.1667 | 463.5 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL
V-S-MNSP1 Import | N^^N_NIL_X5_BEKG | 280.9167 | 0 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of Bendigo to Kerang 220kV line and other nearby lines in NW Victoria | NIL
V-S-MNSP1 Import | N^^N_NIL_3 | 246.25 | 986.8333 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL
V-S-MNSP1 Import | V^^V_MLNK_KGTS | 138.6667 | 61.5 | Out= Murraylink, avoid voltage collapse for loss of Horsham - Murra Warra - Kiamal 220kV line | Outage
V-S-MNSP1 Import | V>>NIL_ELML_BAML2 | 128.75 | 11.0833 | Out= Nil, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | NIL
V-S-MNSP1 Import | N^^N_NIL_X5_BESH | 92.75 | 0 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of Bendigo to Shepparton 220kV line in NW Victoria | NIL
V-S-MNSP1 Import | N>>NIL_990_051 | 90.5833 | 0 | Out= NIL, avoid O/L Wagga to Yass (990) on trip of Wagga to Lower Tumut (051) line, Feedback | NIL
V-S-MNSP1 Import | SVML_ROC_80 | 82.3333 | 74.0833 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Import | V>>NIL_WBBA_RCWEKG | 77.3333 | 0 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_18 | 73.5833 | 270.1667 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | N^^V_NIL_1 | 58.6667 | 16.8333 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
V-S-MNSP1 Import | V>>NIL_ARWB_RCWEKG | 56.8333 | 0 | Out = Nil, avoid O/L Ararat to Waubra 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL
V-S-MNSP1 Import | V>>NIL_ARWB_KGBE | 52.3333 | 0 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | V>>NIL_WBBA_KGBE | 50.4167 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | N^^V_SM_SCAP_R & N^^V_SM_SCAP_P | 42.1667 | 112.1667 | Out = both South Morang 330 kV series capacitor banks, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | N::N_NIL_63 | 34.5833 | 38.8333 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL
V-S-MNSP1 Import | N^^V_CNCW_1 | 31.5833 | 36.1667 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W) or Dapto-Kangaroo Valley (18), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | N>>NIL_991_051 | 29.75 | 0 | Out= NIL, avoid O/L Wagga North 132 to Murrumburrah 132 (991) on trip of Wagga to Lower Tumut (051) line, Feedback | NIL
V-S-MNSP1 Import | S>X_CNRB+RBTX1_23 | 26.6667 | 0 | Out= Robertstown TX1 + Canowie-Robertstown 275kV line O/S, avoid O/L Robertstown 275/132kV TX2 on trip of Robertstown-Waterloo East 132kV line (This trip MWP4 SF) line, Feedback | Outage
V-S-MNSP1 Import | SVML_FLT_125 | 26.5833 | 0.16667 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage
V-S-MNSP1 Import | V>>NIL_WBBA_RCBSS | 23.3333 | 0 | Out= NIL, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Buronga (0X1) 220kV line, Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_27 | 21.5833 | 78.4167 | Out = Nil, avoid O/L Ararat to Waubra 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL
V-S-MNSP1 Import | N>>DP_TIETX_D | 20.6667 | 0 | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (220 KV to 330 kV) on Kerang-Bendigo trip; Feedback | Outage
V-S-MNSP1 Import | S>>X_RBTU+RBTX_15 | 20.5833 | 54.3333 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Import | SVML_FLT_150 | 20.5833 | 2.0833 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage
V-S-MNSP1 Import | SVML_FLT_130 | 18.5 | 25.8333 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage
V-S-MNSP1 Import | S>RBTX1_RBTX2_WEMWP4 | 16.4167 | 75.4167 | Out= one Robertstown 275/132kV TX, avoid O/L MWP4-Robertstown 132kV line on trip of remaining Robertstown 275/132kV TX | Outage
V-S-MNSP1 Import | V>>ARCW_DPTX_KGBE | 15.75 | 0 | Out= Ararat to Crowlands 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | N^^V_DDSM1 | 13.5833 | 18.8333 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage
V-S-MNSP1 Import | V>>V_NIL_24 | 13.25 | 15 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | N^^V_2_6X_3J_1 | 10.6667 | 0 | Out = Ravine-Yass or Upper Tumut to Ravine (2 or 6X) 330kV line and Gullen Range to Yass (3J), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | V>>V_NIL_7 | 9.3333 | 101.8333 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL
V-S-MNSP1 Import | S>NIL_RBMWP3_RBNW1 | 7.5 | 15.1667 | Out= Nil, avoid O/L Robertstown-North West Bend #1 132kV line on trip of Robertstown-Morgan Pipeline 3-Morgan Pipeline 2-Morgan Pipeline 1-North West Bend 132kV #2 line, Feedback | NIL
V-S-MNSP1 Import | V^^V_NIL_KGTS_2 | 5.9167 | 0 | Out= Nil, avoid voltage collapse for loss of Horsham - Murra Warra - Kiamal 220kV line. Murraylink VFRB enabled. Swamp if Murraylink VFRB disabled. | NIL
V-S-MNSP1 Import | V>>V_NIL_9 | 5.75 | 77.3333 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | N^^V_JNWG_63_X5_1 | 5.6667 | 0.75 | Out = Jindera to Wagga(62) 330kV line, 63 + X5 open, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | V>>V_NIL_23 | 5.5 | 12.1667 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | S>VMLMHNW1 | 5.25 | 0 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-S-MNSP1 Import | S>V_RBNW_RBMWP3 | 4.9167 | 0.33333 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage
V-S-MNSP1 Import | S>RBTX2_RBTX1_WEMWP4 | 4.6667 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage
V-S-MNSP1 Import | S>>V_MWP3RB_RBNW1 | 4.5833 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L Roberstown-North West Bend 132kV line on trip of Nil trip, Feedback | Outage
V-S-MNSP1 Import | V>>RCWE_DPTX_ARWB | 4.25 | 0 | Out= Any 220kV line section between Red Cliffs and Wemen, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Ararat to Waubra to Ballarat 220kV line, Feedback | Outage
V-S-MNSP1 Import | N^^V_BADP_1 | 4 | 0.5 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | I_CTRL_ISSUE_ML | 3.25 | 0.66667 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Import | N>>NIL_996_62 | 3.0833 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback (Note: constraint swamped when 996 is O/S) | NIL
V-S-MNSP1 Import | V>>BUCW_DPTX_KGBE | 3.0833 | 0 | Out= Bulgana to Crowlands 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | N>>994_99F_63 | 3 | 9.1667 | Out= Narrandera to Wagga (994) 132kV line, avoid O/L Yanco to Uranquinty (99F) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,(Note: Option C on OM521) | Outage
V-S-MNSP1 Import | S>>X_RBPA+RBTX_06 | 2.8333 | 0 | Out=Robertstown-Para 275 kV line + one Robertstown TX 275/132 kV, avoid O/L remaining Robertstown 275/132kV TX on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage
V-S-MNSP1 Import | V>>NIL_RCWE_HOMRKM | 2.5833 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | S:VS_PA_SVC_620 | 2.4167 | 2.75 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murraylink upper transfer limit of 620 MW | Outage
V-S-MNSP1 Import | V>>ARWB_DPTX_KGBE | 2.1667 | 0 | Out= Any 220kV line section between Ararat and Ballarat, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | CA_SYDS_53C9C000_1 | 2.0833 | 0 | Constraint Automation, O/L XFMR 4H@DARL_PT@NSW for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP7(EMPSYD) | Outage
V-S-MNSP1 Import | S>>NIL_RBTX_RBTX_1 | 2.0833 | 0 | Out= Nil, avoid O/L of one Robertstown 275/132kV TX on trip of other Robertstown 275/132kV TX, Feedback | NIL
V-S-MNSP1 Import | V>>X5_WBBA_KGBE | 2.0833 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | V>>NIL_MLGT_MLGT_A | 1.5833 | 0 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | NIL
V-S-MNSP1 Import | N^^V_DTSS_1 | 1.5 | 0 | Out = Dapto-Sydney South(11), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | V>>V_NIL_4_SIPS | 1.5 | 0 | Out= Nil, avoid O/L Eildon to Thomastown 220kV line on trip of one Dederang to South Morang 330kV line, 5 min line rating, Feedback. Swamp if SIPS not available | NIL
V-S-MNSP1 Import | S>>MKRB_CNRB_WEMWP4 | 1.25 | 3 | Out= Mokota-Robertstown 275kV line, avoid O/L Morgan Whyalla 4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage
V-S-MNSP1 Import | S>>V_NIL_NIL_RBMW3 | 1.1667 | 0.5 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | #R027387_001_RAMP_F | 1.0833 | 0 | Hard Ramping constraint for constraint SVML_000, Effective Date: 05/08/2008, Version: 1 | Other
V-S-MNSP1 Import | S>>X_RBTU+RBTX_16 | 0.91667 | 3.1667 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage
V-S-MNSP1 Import | V>>XGTML2_KTTX2_1_R2 | 0.91667 | 0 | Out= Geelong to Moorabool No.2 220kV line and Keilor A2 500/220kV transformer, avoid O/L Moorabool to Geelong No.1 220kV line on trip of Sydenham to Keilor 500kV line (offloading Keilor A4 500/220kV transformer), radial mode, YWPS1 on 220kV mode, Feedback | Outage
V-S-MNSP1 Import | #R027366_003_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R027407_008_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R028043_003_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | N>>NIL_DPTX_LV | 0.75 | 0.33333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
V-S-MNSP1 Import | SVML_000 | 0.75 | 0 | SA to Vic on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Import | #R027615_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R028323_009_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R028435_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R028480_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | N^^V_LTUT_1 | 0.66667 | 0 | Out = Lower to Upper Tumut (64) 330kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | V>>EPTT_DDSM_DDSM | 0.66667 | 0 | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to South) for loss of the parallel line, 15 min rating, feedback. Swamp if VBB/SIPS available | Outage
V-S-MNSP1 Import | N>>99J_99D_63 | 0.58333 | 0 | Out= Griffith to Yanco (99J) 132kV line, avoid O/L Darlington Point to Yanco (99D) 132kV line on trip of Darlington Point to Wagga (63) 330kV line, (Note:X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521) | Outage
V-S-MNSP1 Import | SVML_030 | 0.58333 | 0 | SA to Vic on ML upper transfer limit of 30 MW | Outage
V-S-MNSP1 Import | V>>BAML1_ELML_BAML2 | 0.58333 | 0 | Out= Ballarat to Moorabool No.1 220kV line, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | Outage
V-S-MNSP1 Import | #R027949_008_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R028338_009_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | S>>X_RBPA+RBTX2_06 | 0.5 | 43.6667 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage
V-S-MNSP1 Import | V>>NIL_WEKG_HOMRKM | 0.41667 | 0 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_14 | 0.41667 | 0.25 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | #R028043_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | N^^V_2+3J+DDSM_1 | 0.33333 | 0 | Out = Ravine-Yass (2)/Upper Tumut-Ravine (6X) + Yass-Gullen Range (3J) + one Dederang-South Morang line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S>>X_CR+RBTX+TPRS_12 | 0.33333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | #R026997_006_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_DTSS_1, Effective Date: 02/02/2023, Version: 1 | Other
V-S-MNSP1 Import | #R027082_017_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 22/08/2022, Version: 2 | Other
V-S-MNSP1 Import | #R027106_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R028479_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R028871_019_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>ARCW_DPTX_KGBE, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Import | #R028886_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | N>>99K_99D_63 | 0.25 | 0 | Out= Darlington Point to Griffith (99K) 132kV line, avoid O/L Darlington Pt to Yanco (99D) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,(Note: assumed X5 trip scheme disarmed & Wagga to Darlington Point network solid, option C on OM521) | Outage
V-S-MNSP1 Import | N>>V_NIL_65_66 | 0.25 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; (Note: constraint is swamped out if TL 64 is O/S) | NIL
V-S-MNSP1 Import | S>>V_NIL_NIL_RBNW1 | 0.25 | 0 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | S>NIL_NIL_NWMH2 | 0.25 | 0 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL
V-S-MNSP1 Import | V>>ARWB_X5DP_KGBE | 0.25 | 0 | Out= Any 220kV line section between Ararat and Ballarat, avoid O/L Balranald to Darlington Point (X5) on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | #R027418_029_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 22/08/2022, Version: 2 | Other
V-S-MNSP1 Import | #R028239_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | N>>9R3_99D_63 | 0.16667 | 0 | Out= Finley to Deniliquin (9R3), avoid O/L Darlington Point to Yanco (99D) 132kV line on trip of Darling Point to Wagga (63) 330kV line, X5 trip scheme disarmed, Feedback | Outage
V-S-MNSP1 Import | V>>KMRC_DPTX_KGBE | 0.16667 | 0 | Out= Kiamal to Red Cliffs 220kV line, avoid O/L Darlington Point TX3/TX4 (220 to 330kV) on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | #R027970_021_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_BADP_1, Effective Date: 16/08/2022, Version: 1 | Other
V-S-MNSP1 Import | #R027970_021_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_BADP_1, Effective Date: 16/08/2022, Version: 1 | Other
V-S-MNSP1 Import | #R027992_049_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SVML_FLT_125, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | #R028239_016_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>>RCWE_WBBA_X3, Effective Date: 11/07/2023, Version: 1 | Other
V-S-MNSP1 Import | #R028710_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_JNWG_63_X5_1, Effective Date: 10/08/2023, Version: 1 | Other
V-S-MNSP1 Import | CA_SYDS_52F01146_1 | 0.083333 | 0 | Constraint Automation, O/L BATS_WBTS_220:LBAT:Z:220@WBTS@VIC for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP3(EMPSYD) | Outage
V-S-MNSP1 Import | N>>V_SMDD6 | 0.083333 | 1.25 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage
V-S-MNSP1 Import | S:VS_700_HY_TEST | 0.083333 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-S-MNSP1 Import | S>>X_CNRB+RBTX_13 | 0.083333 | 0 | Out= One Robertstown TX + Canowie-Robertstown 275kV line O/S, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Import | S>>X_CR+RBTX+TPRS_21 | 0.083333 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of MWP4-Robertstown 132kV line (This trip MWP4 SF) line, Feedback | Outage
V-S-MNSP1 Import | SVML_060 | 0.083333 | 0 | SA to Vic on ML upper transfer limit of 60 MW | Outage
V-SA Export | V::N_NILxxx | 215.5833 | 16 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL
V-SA Export | V:S_600_HY_TEST | 171.75 | 64 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL
V-SA Export | V::S_SETB_TBSE_2 | 136.0833 | 60.75 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V:S_600_HY_TEST_DYN | 96 | 31.6667 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-SA Export | VS_050_DYN | 62.75 | 27.3333 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage
V-SA Export | V::N_X_SMSC_O1 | 46.1667 | 90.6667 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::S_NIL_MAXG_xxx | 34.5833 | 54.6667 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V_S_NIL_ROCOF | 29.5 | 20.6667 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL
V-SA Export | VS_050 | 26.4167 | 0.33333 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage
V-SA Export | V_S_HEYWOOD_UFLS | 22.75 | 23.25 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC. Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL
V-SA Export | V::N_JNWG_S2 | 14.5833 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_X_SMSC_V1 | 13.9167 | 72.3333 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::N_HWSM_V1 | 13.4167 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V_VS_MLMO_NETT | 12.5833 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage
V-SA Export | V^^S_TBCB94_35_SETB | 11.3333 | 0 | Out= Tailem Bend 275kV CB6594 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | V^^S_PAVC1_SETB | 10.9167 | 1.9167 | Out= Para one SVC(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage
V-SA Export | V::N_HYSE_V2 | 10.3333 | 3.5833 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_PAVC1_SETB | 7.75 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage
V-SA Export | V::N_SETB_O1 | 6.3333 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::N_MLTX_V1 | 5.9167 | 0 | Out = Moorabool Transformer 500/220kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V^^S_PAVC1_MAXG | 5.3333 | 1.75 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | F_ESTN++HYTR_L60 | 5.1667 | 2.75 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::S_TBCP1_MAXG | 4.6667 | 0.083333 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage
V-SA Export | S>>TBTU_TBTU_TBMO | 4.5 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of remaining Tailem Bend-Tungkillo 275kV line, Feedback | Outage
V-SA Export | V::S_SEVC1_MAXG | 4.3333 | 1 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V::N_JNWG_V2 | 4 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V^^S_TBEBUS_MAXG | 3.9167 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA | Outage
V-SA Export | V::N_HWSM_S1 | 3.4167 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-SA Export | V^^S_MLSY_3 | 3.4167 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage
V-SA Export | VS_250 | 2.8333 | 4 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage
V-SA Export | V::N_HYTR_O1 | 2.75 | 1.6667 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V^^S_NIL_MAXG_xxx | 2.4167 | 1.1667 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V::N_X_ARWBBA_S1 | 2.3333 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_TBEBUS_SETB | 2.3333 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage
V-SA Export | V^^S_SETB_TBSE_2 | 2.3333 | 4.75 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V^^S_SEVC1_MAXG | 1.8333 | 0.41667 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V::N_HWSM_SD | 1.75 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::N_X_ARWBBA_V1 | 1.6667 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_RBTU_MAXG_2 | 1.6667 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V::S_RBTU_SETB | 1.6667 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | V::S_PAVC1_MAXG | 1.5833 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage
V-SA Export | V::S_NIL_TBSE_1 | 1.25 | 2.6667 | Out = Nil(Both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (Both South East Capacitors (61 and 62) Available). | NIL
V-SA Export | V::N_ROSM_O1 | 1.0833 | 1.0833 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | #R029025_022_RAMP_F | 1 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | F_ESTN++HYTR_L6 | 1 | 2.5833 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | V^S_HYCP | 1 | 14.5833 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL
V-SA Export | F_ESTN++MLMO_L60 | 0.91667 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | VS_250_DYN | 0.91667 | 2.5 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage
V-SA Export | V>S_460 | 0.83333 | 14.4167 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage
V-SA Export | V::N_MLTX_S1 | 0.83333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_NIL_SETB_SECP_1 | 0.83333 | 3.3333 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | #R028973_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S>>TBTU_TBTU_TBMO, Effective Date: 05/06/2023, Version: 1 | Other
V-SA Export | V::N_HYTR_V1 | 0.66667 | 0.66667 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::N_MLMO_V2 | 0.66667 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_QNV++HYTR_L60 | 0.58333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_KMRC_O1 | 0.58333 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | #R028914_021_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | V::N_KGRC_O2 | 0.5 | 0 | Out = Kerang to Red Cliffs 220kV line (or any section in between), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | #R027509_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R027534_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R027538_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R027594_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R027830_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R027923_011_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R028069_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R028323_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028341_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028455_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028796_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | F_QNV+HYTR_L60 | 0.41667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_KMRC_O2 | 0.41667 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | V::N_X_ARWBBA_SD | 0.41667 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::S_TBEBUS_MAXG | 0.41667 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailem Bend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage
V-SA Export | V^^S_RBPA_SETB | 0.41667 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | V>S_460_DYN | 0.33333 | 5.25 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Export | #R027504_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027542_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R027604_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027752_020_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_VS_MLMO_NETT, Effective Date: 12/03/2021, Version: 1 | Other
V-SA Export | #R027817_012_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027817_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R028274_024_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028323_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028345_024_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028428_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KMRC_V1, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028665_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
V-SA Export | #R028796_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028824_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028928_021_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | F_QNV++HYTR_L5 | 0.33333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::S_SEVC1_SETB | 0.33333 | 0.91667 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage
V-SA Export | V>>MLSY_KTDPT_SYML | 0.33333 | 0 | Out = Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid O/L Keilor to Deer Park 220 kV line on trip of remaining Moorabool to Sydenham 500 kV line, feedback | Outage
V-SA Export | #R027333_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027604_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027682_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R027923_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R028044_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::S_TBCP1_MAXG, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028070_013_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HYSE_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028087_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028091_020_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::S_RBTU_MAXG_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028274_024_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028453_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 28/06/2023, Version: 2 | Other
V-SA Export | #R028494_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HYMO_O1, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028502_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 28/06/2023, Version: 2 | Other
V-SA Export | #R028654_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 07/09/2023, Version: 1 | Other
V-SA Export | #R028723_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028779_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028928_021_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R029008_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 28/06/2023, Version: 2 | Other
V-SA Export | #R029017_022_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R029221_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 28/06/2023, Version: 2 | Other
V-SA Export | #R029238_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 28/06/2023, Version: 2 | Other
V-SA Export | S>>NIL_TBCG_TBTU_1 | 0.25 | 0.33333 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL
V-SA Export | V::N_ROSM_O2 | 0.25 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | V::S_NIL_MG_PS_N-2_1 | 0.25 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA with loss of Pelican Point + Snapper Point PS declared as credible.( Note: South East Capacitor Available) | Outage
V-SA Export | #R027586_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_V1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027626_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R027681_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYSE_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027752_020_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_MLMO_NETT, Effective Date: 12/03/2021, Version: 1 | Other
V-SA Export | #R027919_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R028044_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::S_TBCP1_MAXG, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028161_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | #R028166_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^S_TBEBUS_SETB, Effective Date: 17/05/2023, Version: 1 | Other
V-SA Export | #R028209_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028217_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028338_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028345_024_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028499_022_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_V_HYMO_1, Effective Date: 01/09/2020, Version: 1 | Other
V-SA Export | #R028710_039_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWG_SD, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028741_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028779_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028807_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KMRC_V2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028869_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028871_015_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028871_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028874_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_SD, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | F_ESTN++HYTR_L5 | 0.16667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | F_QNV+HYTR_L6 | 0.16667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_SMTT_O2 | 0.16667 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | V::S_RBPA_SETB | 0.16667 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | V>>MLSY_KTTX_SYML_5R | 0.16667 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage
V-SA Export | #R027504_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027586_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027586_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R027604_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V1, Effective Date: 06/01/2023, Version: 1 | Other
V-SA Export | #R028044_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_TBCP1_SETB, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028070_013_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HYSE_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028087_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028087_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_SD, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028091_020_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::S_RBTU_MAXG_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028168_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_TBEBUS_MAXG, Effective Date: 17/05/2023, Version: 1 | Other
V-SA Export | #R028168_007_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::S_TBEBUS_MAXG, Effective Date: 17/05/2023, Version: 1 | Other
V-SA Export | #R028274_026_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R028338_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028338_013_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028338_013_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028428_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_V1, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028455_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028654_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
V-SA Export | #R028665_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
V-SA Export | #R028727_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028807_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028812_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Export | #R028869_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S1, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Export | #R028906_021_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Export | #R029016_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 28/06/2023, Version: 2 | Other
V-SA Export | #R029238_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint VS_050, Effective Date: 28/06/2023, Version: 2 | Other
V-SA Export | F_QNV++MLMO_L60 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+HYTR_L5 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+MLMO_L60 | 0.083333 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | S>>NIL_TBTU_TBTU_1 | 0.083333 | 0 | Out= NIL, avoid O/L Tailem Bend-Tungkillo 275kV line 1 or 2 on trip of parallel Tailem Bend-Tungkillo 275 kV line 2 or 1, Feedback | NIL
V-SA Export | V::N_MLMO_V1 | 0.083333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V:S_570_OSC_AUTO | 0.083333 | 0.083333 | Out = NIL (Note: with both Black Range series capacitors I/S), Upper transfer limit of 570 MW on VIC to SA on Heywood, Active only when I25 mode cannot be monitored. | NIL
V-SA Export | V:S_PA_SVC_550 | 0.083333 | 0 | Out= one Para SVC (Note: with both Black Range series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 550 MW | Outage
V-SA Export | V^^S_MLSY_2 | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage
V-SA Export | V^^S_PAVC_MAXG | 0.083333 | 0 | Out= Para one SVC (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V^^S_XPAVC_SETB | 0.083333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage
V-SA Import | S:V_PA_SVC_470 | 196.5833 | 217.6667 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 470 MW | Outage
V-SA Import | V^^V_NIL_SWVIC | 185.5 | 19.1667 | Out = Nil, manage flow towards Moorabool across Haunted Gully to Moorabool and Mortlake to Moorabool 500kV lines to avoid voltage instability for the loss of Haunted Gully to Moorabool 500kV line and both APD potlines | NIL
V-SA Import | SV_470_DYN | 117.6667 | 132.5 | SA to Victoria on Heywood upper transfer limit of 470 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 50 MW | Outage
V-SA Import | S:V_550_HY_TEST_DYN | 99.8333 | 4.5 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | S:V_550_HY_TEST | 87.5 | 5.6667 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | S^^V_SETB_1 | 80.5 | 8.75 | Out= one South East to Tailem Bend 275kV line, voltage collapse equation Tailem Bend-Keith #2 132kV Line <=135 MW on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage
V-SA Import | V::N_DDSM_V1 | 47.5833 | 187.8333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Import | F_S++HYSE_L60 | 41.5 | 121.75 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
V-SA Import | S>>TBTU_TUTB_MOTB | 29.1667 | 0 | Out= One Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of remaining Tungkillo-Tailem Bend 275kV line, Feedback | Outage
V-SA Import | F_S++HYSE_L6_1 | 21.75 | 92.8333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
V-SA Import | F_S++HYSE_L5 | 11.1667 | 10.5 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
V-SA Import | V>>NIL_SMTX_SMTX_R5 | 10.25 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 500kV mode, Feedback | NIL
V-SA Import | S:V_XPAVC_310 | 8.8333 | 26 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage
V-SA Import | S::V_TBSE_TBSE_2 | 6.25 | 1.0833 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | S>V_460 | 6.0833 | 1.5 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage
V-SA Import | V>>NIL_SMTX_SMTX_R2 | 4.5 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 220kV mode, Feedback | NIL
V-SA Import | S>V_460_DYN | 4.4167 | 0.66667 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Import | V>>NIL_MLGT_MLGT_A | 3.8333 | 0 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | NIL
V-SA Import | F_S+MLMO_TL_L60 | 3.0833 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
V-SA Import | V>>XGTML2_KTTX2_1_R2 | 2.5 | 0 | Out= Geelong to Moorabool No.2 220kV line and Keilor A2 500/220kV transformer, avoid O/L Moorabool to Geelong No.1 220kV line on trip of Sydenham to Keilor 500kV line (offloading Keilor A4 500/220kV transformer), radial mode, YWPS1 on 220kV mode, Feedback | Outage
V-SA Import | S::V_TBSE_TBSE | 2.4167 | 92.25 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | S:VS_PA_SVC_620 | 1.8333 | 6.6667 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murraylink upper transfer limit of 620 MW | Outage
V-SA Import | S>>CGTB1_TUTB_MOTB | 1.75 | 0.91667 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage
V-SA Import | S:V_PASVC_420OSC_AT | 1.6667 | 0 | Out = one Para SVC, Upper transfer limit of 420 MW on SA to VIC on Heywood, Active only when I25 mode cannot be monitored. | Outage
V-SA Import | #V-SA_RAMP_I_F | 1.5833 | 8.1667 | V-SA >= MIN(-119, InitialFlow + 50) (Wt=35) | Other
V-SA Import | F_S+MLMO_TL_L6_1 | 1.25 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage
V-SA Import | V_SV_MLMO_NETT | 1.25 | 0 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit nett MW contingency size out of SA to be < 150 MW | Outage
V-SA Import | F_S+MLMO_TL_L6_2 | 1.1667 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage
V-SA Import | F_S++HYSE_L6_2 | 1.0833 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage
V-SA Import | #R028511_008_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S^^V_SETB_1, Effective Date: 07/08/2023, Version: 1 | Other
V-SA Import | S:V_460 | 0.66667 | 0 | Maintain maximum transfer limit of 460 MW on Heywood IC from SA to VIC to avoid oscillatory instability | Outage
V-SA Import | #R028801_010_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 15/06/2023, Version: 1 | Other
V-SA Import | F_S+MLMO_TL_L5 | 0.5 | 0 | Out= Moorabool to Mortlake 500kV line, SA Lower 5 min requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
V-SA Import | S:V_PA_SVC_420 | 0.5 | 88.1667 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage
V-SA Import | #R028876_005_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S^^V_SETB_1, Effective Date: 07/08/2023, Version: 1 | Other
V-SA Import | #R028876_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S^^V_SETB_1, Effective Date: 07/08/2023, Version: 1 | Other
V-SA Import | S:VS_700_HY_TEST_DYN | 0.41667 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | #R027983_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S::V_TBSE_TBSE, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Import | #R028511_008_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S^^V_SETB_1, Effective Date: 07/08/2023, Version: 1 | Other
V-SA Import | SV_420_DYN | 0.33333 | 97.5833 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 50 MW | Outage
V-SA Import | #R029015_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R029017_005_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S^^V_SETB_1, Effective Date: 07/08/2023, Version: 1 | Other
V-SA Import | #R029103_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_470, Effective Date: 24/06/2022, Version: 1 | Other
V-SA Import | #R029103_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S:V_PA_SVC_470, Effective Date: 24/06/2022, Version: 1 | Other
V-SA Import | S:VS_700_HY_TEST | 0.25 | 0 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 700 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | #R027983_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S::V_TBSE_TBSE, Effective Date: 12/12/2022, Version: 1 | Other
V-SA Import | #R028906_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S^^V_SETB_1, Effective Date: 07/08/2023, Version: 1 | Other
V-SA Import | #R029015_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R027636_007_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R027983_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S^^V_SETB_1, Effective Date: 22/11/2022, Version: 3 | Other
V-SA Import | #R028471_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R028471_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R028484_016_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_MOPS_SH_NETT_600, Effective Date: 14/08/2023, Version: 1 | Other
V-SA Import | #R028883_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>SMF1_SMF2_NIL_R2, Effective Date: 10/08/2023, Version: 1 | Other
V-SA Import | S>>NIL_CGTB_TUTB_1 | 0.083333 | 0 | Out= Nil, avoid O/L Tungkillo - Tailem Bend 275kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | NIL
V-SA Import | S>>NIL_TUTB_TUTB_1 | 0.083333 | 0 | Out= NIL, avoid O/L Tungkillo-Tailem Bend 275kV line 1 or 2 on trip of parallel Tungkillo-Tailem Bend 275 kV line 2 or 1, Feedback | NIL
VIC1-NSW1 Export | V^^N_NIL_1 | 526.3333 | 333.6667 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
VIC1-NSW1 Export | N>>NIL_970_051 | 385.25 | 0 | Out= NIL, avoid O/L Burrinjuck to Yass (970) on trip of Wagga to Lower Tumut (051) line, Feedback | NIL
VIC1-NSW1 Export | N^^N_NIL_X5_BEKG | 378.25 | 0 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of Bendigo to Kerang 220kV line and other nearby lines in NW Victoria | NIL
VIC1-NSW1 Export | N^^N_NIL_3 | 328.3333 | 1311.25 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL
VIC1-NSW1 Export | V^^N_LTUT_1 | 239.4167 | 0 | Out = Lower to Upper Tumut (64) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_NILxxx | 235.0833 | 20.3333 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL
VIC1-NSW1 Export | N>>NIL_990_051 | 175.6667 | 0 | Out= NIL, avoid O/L Wagga to Yass (990) on trip of Wagga to Lower Tumut (051) line, Feedback | NIL
VIC1-NSW1 Export | N>>NIL_YSTX_051 | 137 | 0 | Out = NIL, avoid O/L of either Yass 132/330kV on trip of Wagga to Lower Tumut (051) line, Feedback | NIL
VIC1-NSW1 Export | N^^N_NIL_X5_BESH | 129.3333 | 0 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of Bendigo to Shepparton 220kV line in NW Victoria | NIL
VIC1-NSW1 Export | V^^N_DTKV_1 | 102.75 | 125.4167 | Out = Dapto - Kangaroo Valley (18) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>NIL_BABE_HOMRKM | 76.3333 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
VIC1-NSW1 Export | N::N_DTKV_2 | 72.8333 | 0 | Out = Dapto - Kangaroo Valley (18) 330kV line, transient stability limit (Snowy-NSW) for loss of one 330kV line between Yass and Bannaby/Marulan with summated flow on 4+5+61 <=1500 | Outage
VIC1-NSW1 Export | N>>YSTX_TX_051 | 64.25 | 0 | Out= One Yass 330/132kV TX, avoid O/L of other Yass 132/330kV TX on trip of Wagga to Lower Tumut (051) line, Feedback | Outage
VIC1-NSW1 Export | N>>NIL_33_34 | 55.0833 | 0 | Out= Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL
VIC1-NSW1 Export | V::N_DDSM_V1 | 46.9167 | 157 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_X_SMSC_O1 | 45.25 | 84.0833 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | N>>NIL_991_051 | 43.5833 | 0 | Out= NIL, avoid O/L Wagga North 132 to Murrumburrah 132 (991) on trip of Wagga to Lower Tumut (051) line, Feedback | NIL
VIC1-NSW1 Export | V::N_HYSE_V2 | 35.4167 | 5.9167 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | N::N_UTRV_2 | 35.25 | 241.1667 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | V>>N-62_66_65_RADIAL | 34.8333 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service - OM521) | Outage
VIC1-NSW1 Export | V>>N_NIL_65_66 | 30.75 | 79.25 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
VIC1-NSW1 Export | V>>NIL_MBDD_MBDD | 26.9167 | 0 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | N::X_2+3J_2 | 20.75 | 0 | Out = Upper Tumut-Ravine (6X) 330kV line/Ravine-Yass (2) 330kV line + Yass-Gullen Range (3J) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | N>>NIL_998 | 20.4167 | 0.83333 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | V^^N_DTMN_1 | 16.9167 | 49.8333 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_JNWG_S2 | 15.0833 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_HWSM_V1 | 14.4167 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_X_SMSC_V1 | 14.0833 | 72.75 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V^^N_DPWG_X5_1 | 13.6667 | 7.3333 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>V_NIL_25 | 12.0833 | 91.75 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
VIC1-NSW1 Export | N::N_SDUT_2 | 11.9167 | 14.1667 | Out = Upper Tumut-Stockdill (1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V^^N_DTSS_1 | 11.8333 | 0 | Out = Dapto-Sydney South(11), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N>>17_39_11 | 11.5833 | 0 | Out = Avon-Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
VIC1-NSW1 Export | V^^N_BURC_1 | 11.5 | 0 | Out = Buronga to Red Cliffs (0X1) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N::N_CNSD_2 | 11 | 1.25 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V^^N_UTRV_1 | 11 | 16.5833 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>NIL_SMTX_SMTX_R5 | 9.3333 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 500kV mode, Feedback | NIL
VIC1-NSW1 Export | V>>V_NIL_5 | 9 | 17.3333 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | V::N_SETB_O1 | 7.8333 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V^^N_CRGR_1 | 6.8333 | 0 | Out = Crookwell to Gullen Range (3H), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_HYSE_S2 | 6.6667 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V^^N_LTMS_1 | 6.5833 | 0 | Out = Murray to Lower Tumut 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_MLTX_V1 | 6.3333 | 0 | Out = Moorabool Transformer 500/220kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V^^N_SDUT_1 | 6.1667 | 0.083333 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V^^N_HWSM_1 | 5.6667 | 0 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N>>3H_998_4 | 5.25 | 0 | Out = Crookwell to Gullen Range(3H) 330kV line, avoid O/L Cowra to Forbes (998) 132kV line on trip of Collector to Marulan (4) 330kV line, Feedback | Outage
VIC1-NSW1 Export | V>>V_DDSM_1 | 5.0833 | 117.0833 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
VIC1-NSW1 Export | V>>NIL_SMTX_SMTX_R2 | 4.6667 | 0 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 220kV mode, Feedback | NIL
VIC1-NSW1 Export | N>>NIL_4 | 4.3333 | 0.16667 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | V::N_HYSE_V1 | 4 | 3.25 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | N::N_CRGR_2 | 3.8333 | 0 | Out = Crookwell to Gullen Range (3H), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage
VIC1-NSW1 Export | N>>NIL_5_61_N | 3.5 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) 330kV line on trip of Crookwell to Bannaby (61) 330kV line, Feedback | NIL
VIC1-NSW1 Export | V::N_HYTR_O1 | 3.4167 | 1.25 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | N::N_CNCW_2 | 3.25 | 5.5833 | Out = Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line | Outage
VIC1-NSW1 Export | V::N_JNWG_V2 | 3.1667 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | CA_SYDS_544A2F7F_2 | 2.5833 | 0 | Constraint Automation, O/L 998:L998:I:132@COWRA@NSW for CTG LNQT on trip of COLLECWF-MARULAN 4 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP7(EMPSYD) | Outage
VIC1-NSW1 Export | V::N_HYSE_S1 | 2.5833 | 0.58333 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HWSM_S1 | 2.5 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
VIC1-NSW1 Export | V>>N_NIL_65 | 2.5 | 6 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | V::N_X_ARWBBA_S1 | 2.4167 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V^^N_CNCW_1 | 2.3333 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N>>3H_5_4_N | 1.9167 | 0 | Out = Crookwell to Gullen Range (3H), avoid O/L Yass to Marulan (5) 330kV line on trip of Collector to Marulan (4) 330kV line, Feedback | Outage
VIC1-NSW1 Export | V>>N-62_65_66_RADIAL | 1.75 | 0 | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service - OM521) | Outage
VIC1-NSW1 Export | CA_SYDS_52C88A79_1 | 1.6667 | 0 | Constraint Automation, O/L 65:LSM1:I:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP3(EMPSYD) | Outage
VIC1-NSW1 Export | V>>NIL_BABE_KMRC | 1.6667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL
VIC1-NSW1 Export | N>>14_39_12 | 1.5833 | 0 | Out = Kemps Creek to Sydney North (14), avoid O/L Bannaby to Sydney West (39) on trip of Sydney South to Liverpool (12) line, Feedback | Outage
VIC1-NSW1 Export | V::N_HWSM_SD | 1.5833 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_X_ARWBBA_V1 | 1.5 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V^^N_2_6X_3J_1 | 1.4167 | 0 | Out = Ravine-Yass or Upper Tumut to Ravine (2 or 6X) 330kV line and Gullen Range to Yass (3J), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_ROSM_O1 | 1.0833 | 1.0833 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_X_ARWBBA_SD | 1.0833 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines (complete circuit O/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | N::N_CNLT_2 | 1 | 0 | Out = Lower Tumut-Canberra (07), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | NRM_VIC1_NSW1 | 1 | 3.3333 | Negative Residue Management constraint for VIC to NSW flow | NIL
VIC1-NSW1 Export | N^^N_NIL_1 | 1 | 1.6667 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL
VIC1-NSW1 Export | N>>NIL_39_11 | 0.91667 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
VIC1-NSW1 Export | N>>NIL_39_17 | 0.91667 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL
VIC1-NSW1 Export | #R029231_006_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V^^N_DTSS_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | V::N_MLTX_S1 | 0.83333 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-BUDP_2N | 0.83333 | 0 | Out= Buronga-(X5), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, (Note: assumed Darlington-Wagga 132kV mesh operated CLOSED) | Outage
VIC1-NSW1 Export | N>>NIL_7_3 | 0.75 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, [Note: unswamped when both 1 & 2 LSC disabled] | NIL
VIC1-NSW1 Export | V::N_MLMO_V2 | 0.75 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V^^N_JNWG_1 | 0.66667 | 0 | Out = Jindera to Wagga (62) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | #R027210_018_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 20/09/2022, Version: 1 | Other
VIC1-NSW1 Export | N>>NIL_5_3L_N | 0.58333 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) using 15 mins rating on trip of Yass to Collector (3L) line, Feedback | NIL
VIC1-NSW1 Export | V::N_HYTR_V1 | 0.58333 | 0.5 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_KMRC_O1 | 0.58333 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | N>>NIL_DPTX_LV | 0.5 | 0.33333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
VIC1-NSW1 Export | V::N_KGRC_O2 | 0.5 | 0 | Out = Kerang to Red Cliffs 220kV line (or any section in between), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
VIC1-NSW1 Export | V>>MLSY_KTDPT_SYML | 0.5 | 0 | Out = Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid O/L Keilor to Deer Park 220 kV line on trip of remaining Moorabool to Sydenham 500 kV line, feedback | Outage
VIC1-NSW1 Export | V^^N_BADP_1 | 0.5 | 4.4167 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | #R027910_023_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_CNCW_1, Effective Date: 24/02/2021, Version: 1 | Other
VIC1-NSW1 Export | #R027923_011_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028070_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HYSE_S2, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028323_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028341_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028380_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V>>DDSM_BABE_SMDD, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028402_029_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_BURC_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028455_011_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028983_029_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_BURC_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | N>>NIL_9_18_N | 0.41667 | 0 | Out= Nil, avoid O/L Canberra to Yass (9) using 15 mins rating on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL
VIC1-NSW1 Export | N>BWLD33_BWLD34 | 0.41667 | 0 | Constraint Automation, O/L 34:LN34:Z:330@BAYSWATR@NSW for CTG LNPI on trip of BAYSWATR-LIDDELL 33 330KV LINE. Generated by RTCA[EMS] | Outage
VIC1-NSW1 Export | V::N_KMRC_O2 | 0.41667 | 0 | Out = Kiamal to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
VIC1-NSW1 Export | #R027413_026_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^N_LTUT_1, Effective Date: 21/03/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027504_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027604_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027604_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027681_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_S1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027817_012_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027817_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028070_013_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_HYSE_S2, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028323_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028380_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>DDSM_BABE_SMDD, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028428_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KMRC_V1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028503_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^N_DTSS_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028654_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 07/09/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028665_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028796_011_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028801_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028824_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_O2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R029215_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N::N_SDUT_2, Effective Date: 30/11/2023, Version: 1 | Other
VIC1-NSW1 Export | CA_SYDS_52C76ACC_1 | 0.33333 | 0 | Constraint Automation, O/L 65:LSM1:I:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR2] Host NORREGEEMP3(EMPSYD) | Outage
VIC1-NSW1 Export | N>>NIL_YSTX_LV | 0.33333 | 0 | Out= Nil, avoid O/L Either of Yass 132/330 Transformers on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | #R027210_018_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 20/09/2022, Version: 1 | Other
VIC1-NSW1 Export | #R027333_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027511_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HYTR_O1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027511_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HYTR_O1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027681_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HYSE_S1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027681_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027923_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028087_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028428_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_KMRC_V1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028494_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_HYMO_O1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028723_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028779_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028796_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | N>>NIL_4_61_N | 0.25 | 0 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Crookwell to Bannaby (61) line, Feedback | NIL
VIC1-NSW1 Export | V::N_SMTT_O2 | 0.25 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
VIC1-NSW1 Export | V>>N_051_66_65_R | 0.25 | 1.5 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line,(Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage
VIC1-NSW1 Export | #R027227_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_2_6X_3J_1, Effective Date: 06/03/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027227_018_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_2_6X_3J_1, Effective Date: 06/03/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027413_026_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_LTUT_1, Effective Date: 21/03/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027586_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_V1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027881_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_DTSS_1, Effective Date: 01/05/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027919_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S2, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028209_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028217_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028245_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_DTMN_1, Effective Date: 09/12/2021, Version: 1 | Other
VIC1-NSW1 Export | #R028245_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_DTMN_1, Effective Date: 09/12/2021, Version: 1 | Other
VIC1-NSW1 Export | #R028338_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028402_029_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_BURC_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028455_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028503_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_DTSS_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028710_039_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWG_SD, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028741_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028779_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028796_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028807_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_KMRC_V2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028869_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028871_015_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028871_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028874_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_SD, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028983_029_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_BURC_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | V::N_DDSM_S1 | 0.16667 | 21.1667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | #R027504_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_O1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027586_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027586_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S1, Effective Date: 06/01/2023, Version: 1 | Other
VIC1-NSW1 Export | #R027910_023_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_CNCW_1, Effective Date: 24/02/2021, Version: 1 | Other
VIC1-NSW1 Export | #R028046_021_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R028087_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028087_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_SD, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028271_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::N_CNCW_2, Effective Date: 04/07/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028338_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028338_013_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_X_ARWBBA_V1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028338_013_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_V1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028374_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>DDSM_BABE_SMDD, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028527_026_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_LTUT_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028527_026_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_LTUT_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028665_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_O2, Effective Date: 07/09/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028727_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HWSM_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028807_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028812_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KMRC_O2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028869_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S1, Effective Date: 15/06/2023, Version: 1 | Other
VIC1-NSW1 Export | #R028883_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>SMF1_SMF2_NIL_R2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Export | #R029214_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::N_UTRV_2, Effective Date: 30/11/2023, Version: 1 | Other
VIC1-NSW1 Export | N>>64_07_03 | 0.083333 | 0 | Out = LowerTumut-UpperTumut (64), avoid O/L Lower Tumut to Canberra (07) on trip of Lower Tumut to Yass (03) line, Feedback | Outage
VIC1-NSW1 Export | N>>NIL_5_3J_N | 0.083333 | 0 | Out= Nil, avoid O/L Yass to Marulan (5) using 15 mins rating on trip of Yass to Gullen Range (3J) line, Feedback | NIL
VIC1-NSW1 Export | N>>NIL_61_4 | 0.083333 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) on trip of Collector to Marulan (4) line, Feedback | NIL
VIC1-NSW1 Export | N>>NIL_64_65 | 0.083333 | 0 | Out = Nil, avoid Lower Tumut to Upper Tumut(64) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL
VIC1-NSW1 Export | V::N_MLMO_V1 | 0.083333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>KMCB_BABE_KMRC | 0.083333 | 0 | Out= Kiamal 220kV CB (one or more MR2B or 7422A or 7422B), avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | Outage
VIC1-NSW1 Export | V>>N-DPWG_X5_A | 0.083333 | 0 | Out = to Wagga (63) and Darlington Point to Balranald (X5), avoid Murray to Upper Tumut (65) O/L on Murray to Lower Tumut (66) trip; Feedback | Outage
VIC1-NSW1 Export | V>>NIL_SMDD_SMDD | 0.083333 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | V>>N_64_66_65_N | 0.083333 | 0 | Out = LowerTumut-UpperTumut (64), avoid Murray to Lower Tumut (66) O/L on Murray to Upper Tumut (65) trip; Feedback | Outage
VIC1-NSW1 Export | V>>N_NIL_66_65 | 0.083333 | 0.66667 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 228.75 | 80.25 | Negative Residue Management constraint for NSW to VIC flow | NIL
VIC1-NSW1 Import | V>>NIL_ELML_BAML2 | 217.5833 | 26 | Out= Nil, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | NIL
VIC1-NSW1 Import | N^^V_NIL_1 | 65.0833 | 17.75 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
VIC1-NSW1 Import | N^^V_SM_SCAP_R & N^^V_SM_SCAP_P | 48.8333 | 122.6667 | Out = both South Morang 330 kV series capacitor banks, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_NIL_ARWBBA | 37.4167 | 30.6667 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL
VIC1-NSW1 Import | N^^V_CNCW_1 | 35.1667 | 40 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W) or Dapto-Kangaroo Valley (18), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_MLNK_1 | 29.5833 | 0.66667 | Out = Murraylink, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N>>V_NIL_0X1_60 | 14.6667 | 3.25 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL
VIC1-NSW1 Import | N^^V_DDSM1 | 14.5833 | 22.5833 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage
VIC1-NSW1 Import | N^^V_2_6X_3J_1 | 10.8333 | 0 | Out = Ravine-Yass or Upper Tumut to Ravine (2 or 6X) 330kV line and Gullen Range to Yass (3J), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_JNWG_63_X5_1 | 5.6667 | 0.75 | Out = Jindera to Wagga(62) 330kV line, 63 + X5 open, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N>>NIL_996_62 | 5.0833 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback (Note: constraint swamped when 996 is O/S) | NIL
VIC1-NSW1 Import | N^^V_BADP_1 | 4 | 4.75 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>NIL_MLGT_MLGT_A | 3.8333 | 0 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | NIL
VIC1-NSW1 Import | V>>XGTML2_KTTX2_1_R2 | 2.9167 | 0 | Out= Geelong to Moorabool No.2 220kV line and Keilor A2 500/220kV transformer, avoid O/L Moorabool to Geelong No.1 220kV line on trip of Sydenham to Keilor 500kV line (offloading Keilor A4 500/220kV transformer), radial mode, YWPS1 on 220kV mode, Feedback | Outage
VIC1-NSW1 Import | N^^V_DTSS_1 | 2.5833 | 0 | Out = Dapto-Sydney South(11), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>BAML1_ELML_BAML2 | 2.4167 | 0 | Out= Ballarat to Moorabool No.1 220kV line, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | Outage
VIC1-NSW1 Import | N^^V_LTWG_1 | 2.0833 | 2.25 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_2+3J+DDSM_1 | 1.75 | 0 | Out = Ravine-Yass (2)/Upper Tumut-Ravine (6X) + Yass-Gullen Range (3J) + one Dederang-South Morang line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_MLNK_ARWBBA | 1.6667 | 1.3333 | Out = Murraylink, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | Outage
VIC1-NSW1 Import | V>>V_NIL_4_SIPS | 1.5 | 0 | Out= Nil, avoid O/L Eildon to Thomastown 220kV line on trip of one Dederang to South Morang 330kV line, 5 min line rating, Feedback. Swamp if SIPS not available | NIL
VIC1-NSW1 Import | V>>DDTX2_DDTX3_DDTX1 | 1.25 | 0 | Out= Dederang H2 txfmr, avoid O/L Dederang H3 330/220kV txfmr on trip of Dederang H1 330/220kV txfmr, Feedback | Outage
VIC1-NSW1 Import | N>>NIL_DPTX_HV | 1.1667 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL
VIC1-NSW1 Import | #R027778_004_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
VIC1-NSW1 Import | V>>EPTT_DDSM_DDSM | 0.75 | 0 | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to South) for loss of the parallel line, 15 min rating, feedback. Swamp if VBB/SIPS available | Outage
VIC1-NSW1 Import | N^^V_LTUT_1 | 0.66667 | 0 | Out = Lower to Upper Tumut (64) 330kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | #R028524_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_MSDD2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Import | V>>DBT_DDTX3_DDTX | 0.41667 | 0 | Out = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage Schemes), avoid O/L Dederang H3 330/220kV transformer for loss of Dederang H1 or H2 330/220kV transformer, feedback | Outage
VIC1-NSW1 Import | #R026997_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_DTSS_1, Effective Date: 02/02/2023, Version: 1 | Other
VIC1-NSW1 Import | #R027753_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
VIC1-NSW1 Import | #R027790_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
VIC1-NSW1 Import | #R028435_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^V_MLNK_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Import | N>>V_NIL_65_66 | 0.33333 | 0.083333 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; (Note: constraint is swamped out if TL 64 is O/S) | NIL
VIC1-NSW1 Import | #R027082_017_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 22/08/2022, Version: 2 | Other
VIC1-NSW1 Import | #R027552_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_LTWG_1, Effective Date: 16/08/2022, Version: 1 | Other
VIC1-NSW1 Import | N::V_DDSM_UTMS | 0.25 | 0.41667 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit for trip of Upper Tumut - Murray (65) line | Outage
VIC1-NSW1 Import | V::V_1900 | 0.25 | 0.25 | Out=Nil, upper limit into Vic of 1900 MW | NIL
VIC1-NSW1 Import | #R027418_029_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 22/08/2022, Version: 2 | Other
VIC1-NSW1 Import | #R027753_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
VIC1-NSW1 Import | #R027790_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>DDTX1_DDTX3_DDTX2, Effective Date: 14/03/2023, Version: 1 | Other
VIC1-NSW1 Import | #R028524_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_MSDD2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Import | N>>V_051_65_66_R | 0.16667 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Upper Tumut to Murray (65) on trip of Lower Tumut to Murray (66) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage
VIC1-NSW1 Import | N^^V_MSUT_1 | 0.16667 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>051_68_67_R | 0.16667 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, (Note: Assumed Wagga-Yass 132kV network Split, X5, 63 & 9R4 opened, & with 2 Yass Transformer I/S; Swamped if SIPS ENABLED) | Outage
VIC1-NSW1 Import | #R027970_021_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_BADP_1, Effective Date: 16/08/2022, Version: 1 | Other
VIC1-NSW1 Import | #R027970_021_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_BADP_1, Effective Date: 16/08/2022, Version: 1 | Other
VIC1-NSW1 Import | #R028520_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_MSDD2, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Import | #R028710_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_JNWG_63_X5_1, Effective Date: 10/08/2023, Version: 1 | Other
VIC1-NSW1 Import | N>>NIL_X3_060 | 0.083333 | 0 | Out= Nil, avoid O/L Balranald to Buronga (X3) on trip of Jindera to Wodonga (060) line, Feedback | NIL
VIC1-NSW1 Import | N>>V_SMDD6 | 0.083333 | 1.4167 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage

## Outages
Constraint Set ID | 2023 Days | 2022 Days | Description
N-LS_VC1 | 364.6146 | 330.0208 | Out= Lismore SVC
S-PA_VC1 | 229.6111 | 323.0764 | Out= One Para SVC , (Note: with both Black Range Series caps I/S)
Q-KEP-HYB_50MW | 210.9618 | 0 | Kennedy Energy Park upper limit of 50MW
V-KIAMAL_SC | 201.8507 | 75.9236 | Outage = Kiamal Syncon, 7422B and RC2A closed
N-MBTE_1 | 168.309 | 153.1424 | Out= one Directlink cable
N-BDKV_19 | 114.7014 | 0 | Out= Bendeela - Kangaroo Valley (19) line
Q-KEP-HYB_38MW | 95.1979 | 0 | Kennedy Energy Park upper limit of 38MW
V-X_SMSC | 92.7674 | 304.7674 | Outage = Both South Morang 330kV series capacitors
V-KIAMAL_SC_220CB | 85.2708 | 110.4132 | Outage = Kiamal Syncon, 7422B and RC2A open
F-I_FFR_GLOBAL | 83.4549 | 0 | Global FFR dispatch constraints. Used for initial FFR market start
I-QN_1300_TEST | 82.5799 | 0 | Qld to NSW on QNI limited to 1300 MW for testing QNI minor augmentation
N-ERVP_24 | 76.809 | 0.81944 | Out = Eraring to Vales Point (24)
N-BANCO_999 | 74.8715 | 66.2292 | Out= Bango 999 WF to Cowra 132kV line (999)
N-PKWL_94K_2 | 74.0382 | 0 | Out = Parkes to Suntop (94K/2) 132kV line (Open at Parkes end only)
Q-WRWK_132S | 70.3403 | 0 | Out = 8902 (H39 Woree - H60 Walkamin) 275kV line with 132 kV network between Ross and Woree split
N-TW_SVC | 62.8542 | 0.53472 | Out = Tamworth SVC
N-LTUT_64_15M | 58.7812 | 0.28125 | Out = Lower to UpperTumut (64), 15/30_min ratings for 65, 66 lines auto-switch on prior loading
I-NQ_700_TEST | 57.5382 | 0 | NSW to QLD on QNI limited to 700 MW for testing QNI minor augmentation
Q-KEP-HYB_25MW | 52.8576 | 122.5972 | Kennedy Energy Park upper limit of 25MW
N-DPTX1-2 | 50.4201 | 0 | Out= one Darlington Pt 132/330kV TX1 or TX2
Q-MIMR_9907_9908 | 48.9965 | 27.5278 | Out= 9907 or 9908 R4 Millmerran to H14 Middle Ridge 330kV feeder, or H14 Middle Ridge 330/275 kV #4 or #5 transformer
N-X_LS+TW_SVC | 46.316 | 0 | Out = Tamworth SVC and Lismore SVC
N-KCSN_14 | 44.0625 | 0.68403 | Out = Kemps Creek to Sydney North (14) 330kV line
I-MURRAYLINK | 42.7431 | 25.7396 | Out = Murraylink, (NOTE: ONLY INVOKE when MLK is O/S on both SA & VIC ends OR when MLK is open on either ends)
F-T-GTTE | 42.566 | 17.3993 | Out = one George Town to Temco 110kV line OR loss of both Georgetown to Temco 110 kV lines or all Temco load declared credible
S-SE_VC1 | 41.4965 | 71.7986 | Out= Either one of South East SVC O/S (Note: with both Black Range series caps I/S)
Q-BCNE_821 | 39.0729 | 0.038194 | Out = 821 275kV fdr H10 Bouldercombe - H11 Nebo
Q-NESTM | 38.8819 | 37.5972 | Out = One H11 Nebo to H35 Strathmore 275KV line (822 / 878 / 8845)
V-DBUSS_T | 34.1319 | 59.1597 | Outage = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage schemes)
N-DTKV_18_WG_CLOSE | 32.6285 | 0 | Out= Dapto - Kangaroo Valley (18) [Note: Wagga-Yass 132kV parallel lines CLOSED]]
N-X_TWNR_MORNR | 31.6806 | 1.125 | Out= 968 (Tamworth to Narrabri) and 96M(Narrabri to Moree) 132kV line
T-HA_TX | 28.0694 | 1.559 | Out = one Hadspen 220/110kV transformer
S-TB_CB6596 | 24.4931 | 0.14931 | Out= Tailem Bend 275kV CB6596 ONLY O/S (Note: all other 275kV CBs and lines at Tailembend I/S),(Note: with both Black Range series caps I/S)
N-TAPM_964 | 24.4549 | 8.5451 | Out = Taree to Port Macquarie (964) 132kV line
Q-BCRG_811 | 24.4375 | 11.2222 | Out = 811 (H10 Bouldercombe to H73 Raglan) 275kV line
N-GOONSF1_ZERO | 24.1146 | 0 | Goonumbla solar farm upper limit of 0 MW
S-RBPA | 21.3854 | 4.3125 | Out= Robertstown - Para 275 kV line (Note: with both Black Range series caps I/S)
Q-SMRS | 21.0938 | 0.43403 | Out = 8857 or 8858 (H35 Strathmore to H13 Ross) 275kV line, CQ-NQ limits.
Q-CMTX | 20.3333 | 0.25 | Out = Clermont T1 or T2 132/66 kV transformer
Q-TLWR_132S | 18.7882 | 0.23611 | Out= 877 (H108 Tumoulin to H39 Woree) 275kV line with 132 kV network between Ross and Woree split
V-DDSM | 17.2986 | 52.2708 | Out = Dederang to South Morang (DDTS-SMTS) 330 kV line
S-PA_VC1_BC-2CP | 16.809 | 37.6979 | Out= One Para SVC (Note: with both Black Range series caps O/S)
N-X_MBTE_3 | 16.7778 | 18.9271 | Out= all three Directlink cables
S-TBCP1 | 16.7257 | 0.15625 | Out = Tailem Bend 275kV capacitor bank (Note: with both Black Range series Caps I/S);
N-AVMA_17 | 15.0521 | 42.0278 | Out = Avon to Macarthur (17) 330kV line
N-GFYC-99J-C | 14.6667 | 0.48264 | Out= Griffith to Yanco (99J) 132kV line. X5 trip scheme disarmed and Wagga to Darlington Point network solid, option C on OM521
Q-WDSF_8927 | 14.3264 | 0 | Out = 8927 (S5 Western downs to H014 Western Downs Solar Farm) 275kV feeder
I-VS_050 | 14.0729 | 23.1667 | Victoria to SA on VicSA upper transfer limit of 50 MW
Q-COLTX | 13.8576 | 5.4028 | Out = Collinsville North T1 or T2 132/33 kV transformer
N-UTRV_6X | 12.5139 | 0 | Out= Upper Tumut to Ravine (6X) 330kV line
N-WLWO_79 | 12.1771 | 9.0382 | Out= Wollar West to Wellington (79) 330kV line or Wollar 500/330kV TX or Wollar to Wollar West (75) 330kV line
S-RBTU | 12 | 3.8854 | Out= Robertstown - Tungkillo 275 kV line 1 or 2; (Both Black Range series caps I/S)
S-TBSE | 11.7153 | 11.2604 | Out = One South East-Tailembend 275kV line (One Black Range series cap I/S)
N-YSTX | 11.7083 | 0 | Out= One Yass 330/132kV TX
N-DP_TIETX | 11.6042 | 8.9375 | Out= DarlingtonPt 330/220/33 kV tie Tx (#3 or #4)
V-DDMB | 11.2431 | 1.4861 | Out=Dederang to Mount Beauty 220kV line
S-NWRB | 11.0764 | 1.5139 | Out= Robertstown-North West Bend #1 132kV line
Q-LVMIDSF | 10.7118 | 1.6875 | Out = 6065 (H15 Lilyvale to Middlemount SF) 66kV feeder
N-X_2+3J | 10.6285 | 0 | Out =Upper Tumut-Ravine (6X) 330kV line/Ravine-Yass (2) 330kV line + Yass-Gullen Range (3J) 330kV line O/S
S-RB_TX | 10.4514 | 0 | Out =One Robertstown 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
Q-WARTX | 10.3924 | 21.684 | Out= Warwick 110/33kV Transformer T1 or T2 O/S
V-HWSM | 9.8958 | 0 | Outage = Hazelwood to South Morang 500kV line
Q-OKYTX4 | 9.8056 | 0.27778 | Out= Oakey 110/33kV transformer (T4)
N-NYNGANSF_ZERO | 9.6736 | 0 | Nyngan Solar Farm upper limit of 0 MW
S-RB_TX2 | 9.441 | 0.17361 | Out = Robertstown #2 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
N-X_18_77/78_CLOSE | 9.3125 | 0 | Out = Dapto-Kangaroo Valley(18) + 77 (Ingleburn-Wallerawang) or 78 (Ingleburn- Sydney South), [Note: Wagga-Yass 132kV parallel lines CLOSED]]
N-BWTX | 9.1979 | 0.125 | Out = one of Bayswater 500/330kV tie Tx
Q-OKYTX3 | 9 | 0.21181 | Out= Oakey 110/33kV transformer (T3)
I-HYSE | 8.8333 | 5.691 | Out = Heywood to South East 275kV line (Both Black Range series caps I/S)
Q-HACL | 8.816 | 20.25 | Out= 8810 or 8811 H24 Calvale to S2 Halys 275 kV feeder
N-MORBOR | 8.75 | 11.7917 | Out= Any one 132kV feeder between Moree to Boggabri East (96M,9UH,9UJ) 132kV line. Applicable with or without 96M offloaded during 9UH or 9UJ outage.
S-X_RBTU+RBTX | 8.6389 | 0 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S (Both Black Range Series caps I/S)
N-DM_SVC | 8.6285 | 0.57639 | Out = Dumaresq SVC
N-X_LS_SVC+96R | 8.6111 | 0 | Out = Out= Lismore SVC + 96R (Glen Innes to Tenterfield) / 96L (Lismore to Tenterfield) 132kV line O/S
N-MNTX3 | 8.4236 | 19.934 | Out = Marulan 132/330kV TX3
N-X_MBTE_2 | 8.2917 | 1.6146 | Out= two Directlink cables
Q-SMCK | 8.2708 | 0 | Out = 8906 (H35 Strathmore to H87 Crush Creek) 275kV line
N-JNWG_RADIAL | 7.6875 | 0.375 | Outage = Jindera - Wagga (62) line, Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service
N-LSTN_96L | 7.6701 | 4.0729 | Out= Lismore to Tenterfield (96L)
N-BAMB_132_OPEN | 7.6319 | 0.60764 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path.
N-RVYS_2 | 7.5521 | 70.434 | Out= Ravine to Yass (2) 330kV line
Q-YL_CB4412 | 7.4097 | 0 | Out = T10 Yarranlea 110kV CB 4412
N-GITN_96R | 7.316 | 0.75694 | Out= Glen Innes to Tenterfield (96R) line
S-TBTU | 7.2257 | 0.26736 | Out= One Tailem Bend - Tungkillo 275kV line (Note: WITH/WITHOUT associated line CBs I/S), (Both Black Range series caps I/S)
S-SECB6161 | 7.1562 | 0.20139 | Out = South East 132kV CB6161 ONLY O/S
S-CRK_0 | 6.8924 | 0 | Discretionary upper limit for Cathedral Rocks windfarm generation of 0 MW
N-AR_VC1 | 6.6285 | 0 | Out = Armidale SVC
T-HAPM_220 | 6.5347 | 0 | Out = One Hadspen to Palmerston (No.1 or No.2) 220kV line
N-WNMR_991 | 6.5 | 5.75 | Out = Wagga North to Murrumburrah (991) 132kV line
S-RB_TX1 | 6.1875 | 22.6424 | Out =Robertstown #1 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
S-WP_0 | 6.0035 | 2.3924 | Discretionary upper limit for Wattle Point windfarm generation of 0 MW
Q-KEP-HYB_35MW | 5.9931 | 0 | Kennedy Energy Park upper limit of 35MW
Q-CPWU_818 | 5.8854 | 0 | Out= 818 H67 Calliope River to H40 Wurdong 275kV feeder, CQ-SQ voltage stability limit
N-X_AR+LS_SVC | 5.6076 | 0 | Out = Lismore SVC + Armidale SVC
I-BL_ZERO | 5.5208 | 4.1667 | Limit Basslink to zero in either direction
N-GNNDHSF1_ZERO_INV | 5.4479 | 4.4826 | Gunnedah solar farm upper limit of 0 MW and 0 Inverter
T-FAJB | 5.4306 | 0.48264 | Out=Farrell-John Butters 220KV line
Q-810_PARALLEL_CLOSE | 5.4201 | 70.2118 | Out= 810 H9 Palmwoods to H5 Woolooga 275 kV feeder with parallel 132 kV network intact
Q-KEP-HYB_20MW | 5.4132 | 75.7812 | Kennedy Energy Park upper limit of 20MW
Q-X_STM_BUS+BC_CB | 5.4062 | 0 | Out = one H35 Strathmore 275kV Bus and H10 Bouldercombe 275kV CB8112
Q-NQ_275BUS_CB | 5.3542 | 1.5 | Out = one 275kV Bus or one or more 275kV CB at north of Calvale and Calliope River resulting loss of two 275kV feeders in the next contingency.
N-WALGR_BAT_L_ZERO | 5.3125 | 4.5069 | Wallgrove Battery (Load Component) upper limit of 0 MW
N-WALGR_BAT_G_ZERO | 5.3125 | 4.5069 | Wallgrove Battery (Generation Component) upper limit of 0 MW
S-MKRB | 5.2431 | 13.8924 | Out= Mokota-Robertstown 275kV line (Note: with both Black Range series caps I/S)
N-LPSW30+RGSW38 | 5.1181 | 0 | Out = Liverpool to Sydney West (30) + Regentville to Sydney West (38)/ Bayswater to Regentville (31) 330 kV lines
S-X_RBTX+MNWT | 5.0868 | 0 | Out= One Robertstown 275/132 kV TX + Mintaro-Waterloo 132 kV line O/S
T-GTHA | 5.0139 | 0 | Out = One George Town to Hadspen 220kV line
N-X_18+76_CLOSE | 4.9688 | 0 | Out = Dapto-Kangaroo Valley(18)+ Sydney South-Wallerawang (76), [Note: Wagga-Yass 132kV parallel lines CLOSED]]
S-MAPS2-PV_0 | 4.9201 | 0 | Discretionary upper limit for SA WATER Mannum Adelaide Pumping Station No 2 PV (Palmer) generation of 0 MW
N-LDTM_82_OPEN | 4.8819 | 4.5625 | Out= Liddell to Tomago (82), Redbank to Kurri 132kV loop opened
N-DTSS_11 | 4.875 | 3.0174 | Out = Dapto to Sydney South (11) 330kV line
N-X_18+30_CLOSE | 4.8438 | 0 | Out = Dapto-Kangaroo Valley(18) + Liverpool to Sydney West (30), [Note: Wagga to Yass 132 kV Parallel lines Closed]
N-LSDU_9U6 | 4.7014 | 0.11458 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L on the remaining 132kV line, Feedback
N-BADP | 4.6319 | 1.2049 | Out = Balranald to Darlington Point (X5) 220kV line
N-MORIV | 4.5139 | 9.7882 | Out= Moree to Inverell (9U2) 132kV line
S-X_RBPA+RBTX | 4.4653 | 0 | Out= Robertstown-Para 275 kV line + one of the Robertstown TX 275/132 kV (Note: with both Black Range series caps I/S)
N-GOONSF1_ZERO_INV | 4.4583 | 2.6667 | Goonumbla solar farm upper limit of 0 MW and 0 Inverter
V-HYTR | 4.441 | 3.4896 | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line
V-SALTCREEK_ZERO | 4.4375 | 0 | Salt Creek wind farm upper limit of 0 MW
Q-BS_275BUS_CB | 4.2569 | 0 | Out = one 275kV Bus or one or more CB (CB8202, CB8342, CB88472, CB88312, CB8562, CB8332) at Broadsound (H20)
N-CRGR_3H | 4.2153 | 0 | Out = Crookwell to Gullen Range(3H) 330kV line.
Q-YARANSF1_37MW | 4.1701 | 3.5868 | Yarranlea Solar Farm upper limit of 37 MW
S-X_PA_VC_2 | 4.1493 | 1.2847 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S)
N-X_966+KK+CH_CB892A | 4.1215 | 0 | Out= 966 (Armidale to Koolkhan) 132kV line [NOTE: Open at Koolkan end ONLY, Armidale end remains closed] O/S and Coffs Harbour CB 892A opened - Arrangement 1 - see OM521
N-WLMO_945 | 4.1111 | 0 | Out= Wellington to Molong (945) 132kV line
V-HYTX_M12 | 4.0833 | 14.691 | Out = Heywood (HYTS) M1 or M2 500/275 kV txfmr
Q-KEP-HYB_ZERO | 3.9583 | 13.3646 | Kennedy Energy Park upper limit of 0MW
N-DPYC-99D-C | 3.9097 | 0 | Out = Darlington Point to Yanco (99D) 132kV line. NOTE: X5 trip scheme disarmed and Wagga to Darlington Point 132kV network solid, option C on OM521
S-X_RBTU+RBTX2 | 3.8125 | 9.6875 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S; (Note: with both Black Range Series caps I/S)
S-DVTX | 3.7396 | 12.0278 | Out= One Davenport 275/132kV TX O/S
Q-KEP-HYB_29MW | 3.7396 | 30.3368 | Kennedy Energy Park upper limit of 29MW
S-PA_EAST_BUS_R | 3.691 | 0 | Out= Para 275kV East bus Right Section (i.e.Tx2,CB6509, CB6512,CB6543, CB6600, CB8034 O/S)
N-BU-SCON1 | 3.6181 | 8.6944 | Out= Buronga Syncon 1, SCON1 is associated with Finley SF
N-DPWG_63_X5 | 3.6076 | 2.4062 | Out = Darlington Point to Wagga (63) 330kV line + line X5 opened
N-PKWL_94K | 3.5938 | 2.2396 | Out = Parkes to Wellington (94K) 132kV line (Note: Entire line segment between Parkes-Suntop T-Wellington O/S)
V-KMRC | 3.5382 | 0 | Out = Kiamal to Red Cliffs 220kV line
Q-MARYRSF1_10MW | 3.5035 | 3.6354 | Maryrorough Solar Farm upper limit of 10 MW
Q-H13RS_SVC | 3.3889 | 17.8924 | Out= H13 Ross 275 kV SVC
Q-X_TLWR_275_FDR | 3.3056 | 0 | Out = 877 (H108 Tumoulin to H39 Woree) 275 kV line and one 275kV NQ feeder
Q-GBMO_8824_8825 | 3.2951 | 1.0799 | Out = Greenbank to Molendinar 275kV feeder 8824 or 8825
S-X_CNRB+RBTX1 | 3.2396 | 0.017361 | Out=One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line O/S;(Both Black Range series cap I/S)
V-ARCW | 3.2257 | 0 | Out = Ararat to Crowlands 220kV line
N-BODWF1_ZERO_WT | 2.9965 | 2.3507 | Bodangora wind farm upper limit of 0 MW and 0 Wind Turbine
N-BEBO-94B | 2.9965 | 2.3507 | Out = Beryl to Bodangora WF 132kV line (94B/2)
T-PMPO_220 | 2.9688 | 38.1806 | Out=A single Palmerston-Poatina 220KV line. One line out of service only
V-ROSM | 2.9514 | 4.4236 | Outage = Rowville to South Morang 500kV line
N-MOON_94T | 2.9306 | 8.4271 | Out = Molong to Orange North (94T) 132kV line
Q-X_BC_275_FDR | 2.8194 | 0 | Out = Bouldercombe Bus 1 or 2 or one or more CB (8482,8122,8202,8112) and one 275kV NQ feeder
N-ARIV_96N | 2.75 | 1.4201 | Out = Armidale to Inverell (96N) 132kV line
V-MTGELIBRAND_66 | 2.7222 | 9.6528 | Mt Gelibrand wind farm upper limit of 66 MW
N-WLTX | 2.7049 | 26.5764 | Out = one of the Wellington 132/330kV Transformers
Q-WARWARSF1 | 2.7049 | 5.566 | Out = 33kV feeder from T58 Warwick to Warwick SF1
Q-SP_VC | 2.7014 | 3.2778 | Out= H2 South Pine SVC
N-AR_TX | 2.6944 | 1.2292 | Out= Armidale No.3 or 6 330/132kV transformer
V-MLTX_A2_R | 2.6389 | 0.48958 | Out= Moorabool A2 500/220kV transformer, Radial Mode
N-SDUT_1 | 2.6042 | 2.5243 | Out = Stockdill to Upper Tumut (1) 330kV line
N-KKLS_967 | 2.5312 | 0.51389 | Out= Koolkhan to Lismore (967) 132kV line
S-ACMA | 2.4931 | 9.9132 | Out= Angas Creek-Mannum 132kV line(Note: With/Without associated line CBs I/S); (Both Black Range series capacitors I/S); (Note: This offloads Mannum-Adelaide Pumping Station PVs 2 & 3)
N-LIMOSF21_ZERO | 2.4479 | 0 | Limondale 2 solar farm upper limit of 0 MW
S-BWMP | 2.4306 | 0 | Out = Blyth West- Munno Para 275kV line (i.e. with Blyth West CB8002 OPEN & Blyth West tripping scheme I/S)
S-BG_CB6246 | 2.4236 | 0.37153 | Out = Bungama 132kV CB6246
S-X_BWMP+MPPA | 2.4167 | 15.7049 | Out = Blyth West- Munno Para 275kV line and Munno Para-Para 275kV (i.e. with Blyth West CB8002 OPEN & Blyth West tripping scheme I/S)
Q-MARYRSF1_ZERO | 2.4028 | 1.1076 | Maryrorough Solar Farm upper limit of 0 MW
N-DPGF-99K-C | 2.3854 | 0 | Out= Darlington Point to Griffith (99K) 132kV line. X5 trip scheme Disarmed and Wagga to Darlington Point network Solid, option c on OM521
N-WGNA_994_C | 2.2986 | 0 | Out = 994 (Narrandera to Wagga) 132kV line O/S; X5 Trip Scheme Disarmed, 132 kV parallel Solid, option c OM521
N-DTKV_18_WG_OPEN | 2.2743 | 0 | Out = Dapto-Kangaroo Valley(18), [Note: Assumed Wagga-Yass OPEN (990 + 991 + 99P)]
S-X_RBPA+RBTX2 | 2.2708 | 11.2361 | Out= Robertstown-Para 275 kV line + one Robertstown TX 275/132 kV (Note: with both Black Range series caps I/S)
Q-X_MIMR_TWO | 2.2604 | 0 | Out = Two parallel feeders between R4 Millmerran to H14 Middle Ridge (9914+9915 or 9908+9907) 330kV line
T-GTSH | 2.2396 | 0.059028 | Out = One George Town to Sheffield 220kV line
S-EMTX1 | 2.2153 | 0 | Out = Emeroo 132/33kV TX1 transformer
Q-STBS_SIPS_OUT | 2.1736 | 0 | Out= 856 or 8831 H29 Stanwell to H20 Broadsound 275 kV line, Stanwell Broadsound SIPS disarmed or OOS.
S-DVBL | 2.0938 | 1.5035 | Out = Davenport - Belalie 275kV line (Both Black Range series caps I/S)
Q-LVDS_2 | 2.0903 | 1.0069 | Out =7150/2 (H15 Lilyvale to T35 Dysart tee Norwich Park) 132kV line section 2 open at Dysart end
S-CNRB | 2.0764 | 13.9062 | Out = Canowie-Robertstown 275kV line (Both Black Range series capacitors I/S)
S-PA_W_BUS_R | 2.0382 | 0 | Out= Para 275kV West bus Right section(i.e.CBs 6601,8033,6510,6514 6542,6541, TX8 O/S),(NOTE: BW-MP 275kV line will also be taken O/S as per Electranet's OI 5.17 issued 19/07/2017)
Q-X_BCNE_CPWU | 2.0278 | 0 | Out = 821 (H10 Bouldercombe - H11 Nebo) and 818 (H67 Calliope River to H40 Wurdong) 275kV line O/S
S-DVCL | 2.0208 | 0 | Out= Davenport-Cultana 275 kV line 2
F-I_ML_APD_LOAD | 1.9896 | 1.8958 | Out=Nil, Dynamic FCAS for APD Load Event, excluding Portland WF
N-BROKENH1_ZERO | 1.9236 | 0.40972 | Broken Hill Solar Farm upper limit of 0MW
T-FARC1 | 1.8924 | 10.7049 | Out=Farrell-Reece 1 220KV line
V-MLMO | 1.8819 | 0 | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line
N-BU-SCON2-3 | 1.8819 | 8.6806 | Out= Buronga Syncon 2-3, SCON2 and SCON3 are associated with Darlington Point SF
N-LDNC_81 | 1.8681 | 84.8924 | Out= Liddell to Newcastle (81)
S-MWP3RB | 1.8576 | 0 | Out = Morgan Whyalla Pipeline Pump No.3 - Robertstown 132kV line O/S, (Note: for Murraylink runback I/S or O/S).
V-AR_WB_BA | 1.8229 | 0 | Out = Ararat to Waubra to Ballarat 220kV lines OR any 220kV line section between Ballarat and Ararat. Waubra wind farm disconnected/off
S-BIPS_ZERO | 1.7847 | 0.22222 | Barker Inlet upper limit of 0 MW
Q-X_RS_TX_TX_O | 1.7743 | 0 | Out = Two Ross 275/132 kV transformer with 132 kV network between Ross and Woree open
N-ARTW_86 | 1.7569 | 1.5868 | Out = Armidale to Tamworth (86) line
N-DBWL-94J | 1.6944 | 0 | Out = Dubbo132 to Wellington (94J) 132 kV line
I-BCDM_ONE | 1.684 | 0.36458 | Out = one Bulli Creek to Dumaresq (8L or 8M) line
T-FISH | 1.6285 | 0 | Out= Fisher - Sheffield 220KV line
T-FARC2 | 1.6042 | 0.14583 | Out=Farrell-Reece 2 220KV line
N-BANYS_9GM | 1.5833 | 90.6424 | Out = Bango 999 WF to Yass 132kV line(9GM)
N-X_9U6_9G2 | 1.5625 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 132kV line between Mullumbimby and Ballina (9G2, 9G3, 9G4 or 9G5)
N-LTWG_RADIAL | 1.5174 | 1.5382 | Out= Lower Tumut - Wagga (051) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service)
N-WLMP_72 | 1.5069 | 0.64583 | Out = Mt_Piper to Wellington (72) 330 kV line
V-MOORBWF_ZERO | 1.4653 | 0 | Moorabool Wind Farm upper limit of 0 MW
S-WEWT | 1.4653 | 0.017361 | Out = Waterloo East - Waterloo132kV line
S-NWCB6021+6225 | 1.4583 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225(Note: this takes out North West Bend-Monash #1 132kV line).(Note: for Murraylink runback scheme I/S or O/S and Sever scheme I/S or O/S)
Q-CLBSF_7473 | 1.4201 | 1.4097 | Out = 7473 (T194 Columboola to T272 Columboola Solar Farm) 132kV feeder
V-BAML1_15M | 1.4167 | 0 | Out= Ballarat to Moorabool No.1 220kV line, Ballarat to Moorabool No.2 220kV line run to 15 min rating.
Q-LCCP_8859 | 1.3993 | 0 | Out= Larcom Creek to Calliope River (8859), thermal limit equations for 812 and 871.
N-BOMENSF1_ZERO | 1.3993 | 0 | Bomen SF upper limit of 0 MW
N-CNSD_3C | 1.3924 | 1.4826 | Out= Canberra to Stockdill (3C) line
S-BRTW | 1.3854 | 0.375 | Out= Brinkworth- Templers West 275kV line
T-PMSH | 1.3785 | 0 | Out = Palmerston to Sheffield 220kV line
N-ARSR_8E | 1.3785 | 1.5833 | Out= Armidale Sapphire (8E) line
Q-KEP-HYB_21MW | 1.3681 | 0.23611 | Kennedy Energy Park upper limit of 21MW
V-ELAINEWF_ZERO | 1.3646 | 8.2569 | Elaine Wind Farm upper limit of 0 MW
I-LTMS | 1.3611 | 0.65972 | Out= Lower Tumut - Murray (66) line
V-SMTT1 | 1.3542 | 0 | Out= South Morang to Thomastown No. 1 220 kV line
V-HYTX_M3 | 1.3438 | 11.3264 | Out = Heywood (HYTS) M3 500/275 kV txfmr
V-KG_WE_RC | 1.3229 | 0.38542 | Outage = Kerang to Wemen to Red Cliffs 220 kV line section, entire line section
N-KVCW_3W_WG_CLOSE | 1.3194 | 0 | Out = Kangaroo Valley to Capital (3W) 330kV line [Wagga-Yass 132kV parallel lines CLOSED]
I-MUTE_758 | 1.3194 | 12.9444 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line
Q-WARMR_736 | 1.2986 | 0.97569 | Out= Warwick to Middle Ridge 110kV feeder (736)
N-WRWSF1_ZERO_INV_WT | 1.2882 | 0.13542 | White Rock wind and solar farm upper limit of 0 MW, 0 Inverter, 0 wind turbine
S-TB275_E_BUS | 1.2847 | 0 | Out= Tailem Bend 275 kV East Bus(This offloads Tailembend 275/132kV #4 TX and C64 Cap Bank) (Both Black Range series Caps I/S)
S-WE_MWP4_RB | 1.2604 | 0 | Out = Robertstown - MWP4 - Waterloo East 132kV line (Note: MWP4 Solar Farm is offloaded) O/S
N-MUTW_88 | 1.2569 | 1.4792 | Out = Muswellbrook to Tamworth (88) line
S-WT_S_BUS | 1.2465 | 0.065972 | Out= Waterloo 132kV South bus O/S (Note: WITH/WITHOUT associated bus CBs I/S) Or Waterloo CB 7022 ONLY O/S
Q-CLBWS_8891_8892 | 1.2431 | 1.4201 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line
V-HOTS_SVC | 1.2049 | 0.54514 | Out = Horsham 220kV SVC
I-MUTE_757 | 1.2049 | 10.6319 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line
V-EL_BUS2 | 1.1979 | 0.54861 | Out = Elaine No.2 220kV bus
N-TWNR_968 | 1.1979 | 2.9201 | Out= 968 (Tamworth to Narrabri) 132 kV Line
S-X-MNWT+CB | 1.1806 | 0 | Out= Mintaro-Waterloo 132kV line with associated critical line CBs O/S (i.e. Waterloo CB 7021 & 7020 O/S)
N-X_DM+LS_SVC | 1.1215 | 0 | Out = Dumaresq SVC + Lismore SVC
I-BURC | 1.066 | 0.20486 | Out = Buronga to Red Cliffs (0X1) 220kV line
I-CTRL_ISSUE_ML | 1.0278 | 0.27431 | DC Link Control Issue Constraint for Murraylink
V-KGTS_SVC | 1.0069 | 0.39583 | Out = Kerang 220kV SVC
T-SH_TX_WCP_OPEN | 0.98611 | 0.34028 | Out = one Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open
N-PK_TX | 0.98264 | 0.28819 | Out = One Parkes 132/66kV Transformer
I-VS_250 | 0.91667 | 3.3333 | Victoria to SA on VicSA upper transfer limit of 250 MW
F-T-CO_CB752 | 0.89931 | 0 | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard
Q-SMSPL | 0.86111 | 5.0764 | Out = 7457 (H35 Strathmore to T242 Springlands) 132kV line O/S
Q-LVCM | 0.84722 | 0.24653 | Out =7153 (H15 Lilyvale to T71 Clermont) 132kV line
I-SVML_030 | 0.80903 | 0 | SA to Vic on ML upper transfer limit of 30 MW
N-DPYC-99D-A | 0.80208 | 0.32986 | Out = Darlington Point to Yanco (99D) 132kV line. X5 trip scheme Armed and Wagga to Darlington Point 132kV network solid, option A on OM521
I-OSC_STAB_MON | 0.79861 | 0.059028 | Out = Oscillatory Stability Monitoring
N-X_2+3J+DDSM | 0.79514 | 0 | Out = Ravine-Yass (2)/Upper Tumut-Ravine (6X) + Yass-Gullen Range (3J) + one Dederang-South Morang 330kV line O/S
Q-STBS | 0.75694 | 6.5903 | Out= 856 or 8831 H29 Stanwell to H20 Broadsound 275 kV line
S-X_RBTU+RTX_BC-2CP | 0.75694 | 0 | Out=Robertstown 275/132 TX 1 or 2 + Robertstown-Tungkillo 275kV line 1 or 2 O/S (Both Black Range Series caps O/S)
N-WELLSF1_ZERO | 0.73611 | 1.3785 | Wellington solar farm upper limit of 0 MW
S-PA_CB6509 | 0.73611 | 0.27778 | Out= Para 275kV CB6509
T-WCOAST_220G_144 | 0.73264 | 0 | Total generation of Bastyan, Granville Harbour, John Butters, Tribute, Reece 1 and 2 limited to <= 144 MW
I-CTRL_ISSUE_TE | 0.72569 | 0.26042 | DC Link Control Issue Constraint for Terranora
S-X_WTP+DALR_ISLAND | 0.71181 | 0.34375 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network) and disconnected from rest of SA network,(Note:Wattle Point Wind Farm and Dalrymple Battery operating in islanded mode)
T-GRANVH_060 | 0.71181 | 0 | Discretionary 60 MW upper limit on Granville Harbour Wind Farm
N-DEFI_9R3_C | 0.68056 | 3.3194 | Out= Finley to Deniliquin (9R3); X5 Trip Scheme Disarmed, 132 kV parallel Solid, option c OM521
S-NWRB2 | 0.67708 | 0.097222 | Out = North West Bend to Robertstown No.2 132kV line O/S
N-BABU | 0.65278 | 2.2535 | Out = Balranald to Buronga (X3) 220kV line
N-FBPK_94U | 0.64931 | 0 | Out = Forbes to Parkes (94U) 132kV line
T-TUNN3 | 0.63194 | 0 | Out = Tungatinah to New Norfolk No.3 110kV line
N-X_11+14 | 0.62153 | 0 | Out = Dapto-Sydney South (11) + Kemps Creek to Sydney North (14)
N-LSLS_9U8 | 0.61806 | 8.1007 | Outage= 9U8 or 9U9 or 9W1 132kV line
V-HYMO | 0.59722 | 2.9062 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line
Q-RGBYRSF1_ZERO | 0.59028 | 0.24653 | Rugby Run Solar Farm upper limit of 0 MW
N-ARGI_96T | 0.58681 | 0.57986 | Out= Armidale to Glen Innes (96T) line
S-X_RBTU+RTX2_BC-2CP | 0.57986 | 0 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S; (Note: with both Black Range Series caps O/S)
Q-LVDS | 0.57986 | 0 | Out =7150 (H15 Lilyvale to T35 Dysart tee Norwich Park) 132kV line or 7150/1 section 1 opened at Lilyvale ends
Q-ST_275BUS_CB | 0.56944 | 0 | Out = one 275kV Bus or one or more 275kV CB (88732,CB 88312,CB8492, CB8612, CB88742, CB8622, CB8632, CB8642, CB8562, CB8552) at Stanwell (H29)
N-MPWW_ONE | 0.53819 | 0.37153 | Out = Mt. Piper to Wallerawang (70 or 71) 330kV line
F-FFR_ZERO_UNITS | 0.53819 | 0 | Out=Nil, Set zero R1 and L1 FCAS dispatch for all FFR registered units.
F-I_BL_650 | 0.53472 | 0 | Out=Nil, FCAS requirements for NEM for loss of Basslink, Basslink LoL = 650 ms
Q-ISHW_M022 | 0.53125 | 1.4167 | Out = M022 (T131 Isis to Howard Tee Childer SF) 66kV feeder
S-LFPP_PELPT | 0.50347 | 0.44792 | Out = Pelican Point to Lefevre 275kV line outage(Note: with both Black Range series capacitors I/S), trip of Pelican Point - Parafield Gardens West 275kV line resulting in loss of Pelican Point and Snapper Point PS a credible event.
N-WNWGA_9R6 | 0.50347 | 0 | Out = Wagga North to Wagga 132 (9R6) 132kV line
Q-BSNE_834 | 0.48958 | 0.052083 | Out = 834 (H20 Broadsound -H11 Nebo) 275kV feeder
V-BA_EL_ML | 0.46875 | 0.034722 | Out = Ballarat to Elaine to Moorabool 220kV line
Q-BCST | 0.46528 | 24.2847 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line
V-CWHO | 0.46181 | 0 | Out = Crowlands to Horsham 220kV line
V-DDWO_RADIAL | 0.45486 | 0 | Out = Dederang to Wodonga 330kV line O/S. TL63 330kV line and X5 opened. See OM 526 and OM 608
N-X_18+30_OPEN | 0.45486 | 0 | Out = Dapto-Kangaroo Valley(18) + Liverpool to Sydney West (30), [Note: Assumed Wagga-Yass OPEN (990 + 991 + 99P)]
S-BRBG | 0.45139 | 2.125 | Out = Brinkworth to Redhill to Bungama 132kV lines (Note: outage also takes out Clements Gap Windfarm).
V-DDTX2_DBUSS_T | 0.44792 | 0 | Out= Dederang H2 330/220kV transformer. Prior outage DBUSS-T scheme disabled
N-FLUR-99A-C | 0.43403 | 0.22569 | Out = Finley to Uranquinty (99A), X5 trip scheme disarmed and Wagga - Darlington point parallel solid, option c on OM521
N-WLON_947 | 0.42708 | 0.020833 | Out= Wellington to Orange North (947) 132kV line
Q-WR_VC | 0.42708 | 6.8576 | Out= H39 Woree 132 kV SVC
N-NYNGANSF_010 | 0.40972 | 0 | Nyngan Solar Farm upper limit of 10 MW
N-TWUL_85 | 0.40972 | 0 | Out = Tamworth to Uralla (85) line
Q-YARANSF1_ZERO | 0.40625 | 0.65625 | Yarranlea Solar Farm upper limit of 0 MW
Q-X_NESM_SMRS | 0.40278 | 0 | Out = one 275kV feeder between H11 Nebo and H35 Strathmore (8845,878,822) + one 275KV feeder between H35 Strathmore and H13 Ross(8857,8858,879,8911)
S-X_WTTP+CB | 0.40278 | 0 | Out = Templers - Waterloo 132kV line with associated critical line CBs O/S (i.e. Waterloo CB 7025 & CB7024 O/S)
N-LDTW_84 | 0.39931 | 0.89236 | Out = Liddell to Tamworth (84) 330kV line
N-X-AR-LS_VC1 | 0.375 | 2.1736 | Out = Armidale SVC and Lismore SVC
S-MBPS2-PV_0 | 0.37153 | 0 | Discretionary upper limit for SA WATER Murray Bridge (Hahndorf ) - Onkaparinga Pipeline Pumping Station 2 PV of 0 MW
N-X_LS_VC1+96L+967 | 0.36458 | 0 | Out= Lismore SVC + 96L (Lismore to Tenterfield) + 967 (Koolkhan to Lismore)
N-CNLT_07 | 0.36458 | 1.0035 | Out = Canberra - Lower Tumut (07) 330kV line
S-MHNW_1 | 0.35417 | 0 | Out = Monash to North West Bend line 1, (Note: Murraylink runback scheme can be I/S or O/S)
Q-X_SRMB+PBMB | 0.34375 | 0 | Out = T015 (Susan River to T59 Maryborough) 66kV line and T014 (Pialba to T59 Maryborough) 66kV line
N-X_947+949 | 0.32292 | 0 | Out= Wellington to Orange North (947) 132kV line + Orange North to Mt Piper (949) 132kV line
N-X_947+94P | 0.27431 | 0 | Out= Wellington to Orange North (947) 132kV line + Manildra to Molong (94P) 132kV
Q-WSWANDB_7484 | 0.26736 | 0.3125 | Out = 7484 (H76 Wandoan South to T271 Wandoan South BESS) 132kV feeder
N-X_ARKK_CH_CB892A | 0.26389 | 0.61806 | Out=966 (Armidale to Koolkhan) 132kV line [Note: Assumed both ends of 966 OPEN OR only Armidale end OPEN with Koolhan end CLOSED] O/S and Coffs Harbour CB 892A opened - Arrangement 1 - see OM521
I-QN_1000 | 0.25694 | 0 | Qld to NSW on QNI limited to 1000 MW, includes constraint with dynamic headroom
V-MURRAWR2_ZERO | 0.25694 | 0.11458 | Murra Warra 2 wind farm upper limit of 0 MW
V-BRYBWF_ZERO | 0.25347 | 24.1632 | Berrybank Wind Farm upper limit of 0 MW
S-X_CNRB+RBTX+TPRS | 0.25347 | 0 | Out= One Robertstown 275/132 kV TX + Canowie-Robertstown 275kV line + Templers-Roseworthy 132kV line O/S;(Both Black Range series cap I/S)
T-NWSD | 0.24653 | 0.086806 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752
I-MSUT | 0.23611 | 0 | Out= Murray - Upper Tumut (65) line
Q-STR_SMSF_ZERO | 0.23611 | 0 | Limit Sun Metals Solar farm to zero MW and disconnect inverter for system strength requirement
N-LDTM_82_CL | 0.23264 | 0 | Out= Liddell to Tomago (82), Redbank to Kurri 132kV loop closed
N-ARUL_8U | 0.22569 | 0 | Out = Armidale to Uralla (8U) line
Q-X_NQ_275_FDR_THREE | 0.22569 | 0 | Out = two or more 275kV feeders in North Queensland
I-ML_ZERO | 0.22569 | 0.13542 | Limit Murraylink to 0 MW in either direction (Note: assumed Murraylink remains I/S and capable of Var support on BOTH ends of the interconnector)
S-LBBAT-L_0 | 0.21875 | 0 | Discretionary upper limit for Lake Bonney Battery (Load component) of 0 MW
I-SVML_060 | 0.21181 | 0 | SA to Vic on ML upper transfer limit of 60 MW
Q-X_ST_275CB+FDR | 0.21181 | 0 | Out = one or more of Stanwell(H29) 275kV CB(88732,CB 88312,CB8492, CB8612, CB88742, CB8622, CB8632, CB8642, CB8562, CB8552) and NQ 275kV feeders 818 and 821
N-WRWF1_ZERO | 0.20486 | 0.41667 | White Rock WF upper limit of 0 MW
I-NQTE_090 | 0.20139 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of 90 MW
N-DMSR_8J | 0.19792 | 1.5799 | Out= Dumaresq to Sapphire (8J) line
V-MLSY_NOEMTT_R | 0.19097 | 1.0417 | Out = One Moorabool to Sydenham 500 kV line, EMTT scheme not armed, Radial mode
T-LIPM | 0.18403 | 1.5312 | Out = Liapootah to Waddamana to Palmerston 220kV line, with associated 220kV CB I/S at Waddamana
N-ARDM_8C | 0.17708 | 1.1597 | Out= Armidale to Dumaresq (8C) line
S-CMWF_0 | 0.17014 | 0 | Discretionary upper limit for Clements Gap WF generation of 0 MW
S-CGTB1 | 0.15972 | 0.20139 | Cherry Gardens to Tailem Bend 275kV line O/S (NOTE: with both Black Range series caps I/S)
I-SVML_000 | 0.14931 | 0 | SA to Vic on ML upper transfer limit of 0 MW
V-RCWT | 0.14931 | 0 | Outage = Red Cliffs to Wemen 220 kV line section
Q-EMERASF1_ZERO | 0.14583 | 0.63889 | Emerald Solar Farm upper limit of 0 MW
Q-X_NQ_275_FDR3+SVC | 0.13889 | 0 | Out = three series 275kV feeders between Calvale and Ross + two series 275kV feeders North of Ross and one or more bus(Strathmore ,Nebo, Broadsound, Bouldercombe and Stanwell)+ Ross or Woree SVC OS, for trip of two series 275kV fdrs
Q-KEP-HYB_27MW | 0.13194 | 8.4931 | Kennedy Energy Park upper limit of 27MW
V-X_GTML2_KTTX2_R | 0.12847 | 0 | Out= Geelong to Moorabool No.2 220kV line and Keilor A2 500/220kV transformer, KTS No.1 and No.2 220kV bus tied
Q-CLST | 0.11458 | 0 | Out = 8874 or 8873 or 855 (H24 Calvale to H29 Stanwell) 275kV feeder
F-T-COGT | 0.097222 | 0 | Out = one Comalco to George Town 220kV line OR loss of both Comalco to Georgetown 220 kV lines or all Comalco potlines declared credible
T-FCSPS_RAMP | 0.090278 | 0 | Ramp down Basslink for outage of FCSPS
S-MAPS3-PV_0 | 0.079861 | 0 | Discretionary upper limit for SA WATER Mannum Adelaide Pumping Station No 3 PV (Kanmantoo) generation of 0 MW
V-X_HG_ML_TR | 0.065972 | 0 | Out = Haunted Gully to Moorabool and Haunted Gully to Tarrone 500kV lines
S-X_SEVC2+PAVC | 0.065972 | 10.1875 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S, (Note: with both Black Range series caps I/S)
S-MYTX1_44248OPEN | 0.0625 | 0 | Out = Mayura No.1 132/33kV transformer (with 33kV bus tie isolator 44248 open)
F-I_FFR_GLOBAL_2 | 0.0625 | 0 | Global FFR dispatch constraints. Used for initial FFR market start
S-LFPP_PELPT_BC-CP | 0.048611 | 0 | Out = Lefevre to Pelican Point 275kV line O/S (NOTE: with one Black Range series capacitors O/S), trip of Pelican Pt- Parafield Gardens West 275kV line resulting in loss of Pelican Pt and Snapper Pt PS a declared credible event
S-LFPP_PELPT_BC-2CP | 0.048611 | 0 | Out = Lefevre to Pelican Point 275kV line O/S (NOTE: with both Black Range series capacitors O/S), trip of Pelican Pt- Parafield Gardens West 275kV line resulting in loss of Pelican Pt+ Snapper PS a credible event
V-HY_500BUS | 0.045139 | 12.5243 | Out = Heywood (HYTS) No. 1 or No. 2 500 kV bus.
I-BL-FCSPS_NO_ACTION | 0.038194 | 0 | Constrains Basslink transfers to levels where no FCSPS action is required for loss of Basslink
Q-NQ_SEMI_RAMP_ZERO | 0.038194 | 1.7257 | Ramp North Qld semi-scheduled generators to zero and hold at zero.
Q-BCCP_812 | 0.034722 | 0 | Out= Bouldercombe to Calliope River (812), thermal limit equations for 811, 871 and 8859.
Q-X_NQ_275_FDR_SVC | 0.03125 | 0.60417 | Out = one 275 kV feeder between Calvale /Calliope River and Ross and Ross SVC or Woree SVC
Q-SRSF1_ZERO | 0.020833 | 0 | Susan River Solar Farm upper limit of 0MW
S-LFTI | 0.017361 | 8.1354 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S)
Q-STSTN_864 | 0.017361 | 0.95833 | 864 Stanwell Stanwell Power Station 275kV line
I-QN_1100 | 0.010417 | 0 | Qld to NSW on QNI limited to 1100 MW, includes constraint with dynamic headroom
I-VT_350 | 0.0069444 | 0 | Vic to Tas on Basslink upper limit of 350 MW
I-TE_ZERO | 0.0034722 | 0 | Terranora Interconnector zero transfer limit in either direction
I-NQTE_-090 | 0.0034722 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -90 MW

## Outage stats
NSP / Year | Unplanned | Short Notice | ≤ 30 days | ≤ 3 months | ≤ 6 months | ≤ 9 months | > 9 months
APT 2019 | 17 | 58 | 24 | 1 | 0 | 0 | 0
2020 | 13 | 23 | 13 | 2 | 0 | 0 | 0
2021 | 11 | 31 | 28 | 5 | 1 | 0 | 0
2022 | 15 | 37 | 21 | 6 | 2 | 0 | 2
2023 | 16 | 65 | 11 | 0 | 0 | 2 | 13
ElectraNet 2019 | 352 | 852 | 1077 | 687 | 142 | 6 | 0
2020 | 269 | 654 | 958 | 599 | 219 | 21 | 0
2021 | 338 | 645 | 1108 | 651 | 164 | 20 | 1
2022 | 432 | 901 | 1295 | 155 | 44 | 77 | 0
2023 | 317 | 745 | 1468 | 510 | 49 | 0 | 0
Essential E 2019 | 4 | 17 | 39 | 0 | 0 | 0 | 0
2020 | 3 | 22 | 62 | 1 | 0 | 0 | 0
2021 | 4 | 30 | 58 | 0 | 0 | 0 | 0
2022 | 17 | 28 | 35 | 3 | 0 | 0 | 0
2023 | 7 | 72 | 110 | 10 | 0 | 0 | 0
Powerlink 2019 | 2040 | 5250 | 8042 | 2154 | 180 | 0 | 0
2020 | 1897 | 6642 | 8078 | 3903 | 247 | 51 | 44
2021 | 1951 | 6022 | 6947 | 5002 | 756 | 39 | 6
2022 | 1986 | 6345 | 7511 | 5241 | 1248 | 148 | 60
2023 | 2395 | 5582 | 6700 | 3534 | 2429 | 166 | 9
AusNet 2019 | 364 | 1387 | 1588 | 69 | 0 | 0 | 0
2020 | 370 | 1128 | 1689 | 67 | 10 | 1 | 0
2021 | 280 | 1039 | 2047 | 71 | 0 | 0 | 0
2022 | 190 | 627 | 1881 | 49 | 0 | 0 | 0
2023 | 224 | 642 | 1949 | 64 | 0 | 0 | 0
TasNetworks 2019 | 198 | 500 | 1069 | 223 | 47 | 0 | 70
2020 | 108 | 1231 | 890 | 321 | 60 | 31 | 26
2021 | 143 | 604 | 906 | 227 | 97 | 39 | 111
2022 | 104 | 428 | 469 | 203 | 66 | 8 | 19
2023 | 135 | 732 | 1027 | 304 | 210 | 141 | 53
TransGrid 2019 | 327 | 1066 | 1868 | 827 | 10 | 0 | 0
2020 | 411 | 1061 | 1635 | 811 | 30 | 2 | 0
2021 | 384 | 877 | 1676 | 580 | 37 | 0 | 1
2022 | 302 | 849 | 1613 | 358 | 9 | 2 | 0
2023 | 301 | 892 | 1742 | 247 | 11 | 0 | 0

## NEM Changes
PROJECT | DATE | REGION | NOTES
Cultana – Yadnarie – Port Lincoln No. 1 132kV line | 2023-01-24 | SA | Part of Eyre Penninsula project
Strathmore No.2 275/132 kV Transformer | 2023-02-16 | Qld
Cultana – Yadnarie – Port Lincoln No. 2 132kV line | 2023-02-22 | SA | Part of Eyre Penninsula project
Hazelwood PS – Hazelwood BESS 2 220 kV Line | 2023-03-07 | Victoria
Wollar West Substation | 2023-03-21 | NSW | Wollar West substation has been cut into the existing Wellington - Wollar (79) 330 kV Line to form the following circuits: Wellington - Wollar West 79 330 kV Transmission Line, Wollar - Wollar West 75 330 kV Transmission Line.
South Morang SMTS F1 transformer | 2023-03-28 | Victoria | Part of VNI minor project
Drillham Substation | 2023-03-29 | Qld | T280 Drillham substation has been cut into the existing Columboola - Roma 7164 and 7174 132 kV transmission lines to form the following lines: Columboola - Drillham 7490 132 kV line Columboola - Drillham 7491 132 kV line Drillham - Roma 7164 132 kV line Drillham - Roma 7174 132 kV line
Rye Park Substation | 2023-04-03 | NSW | Rye Park substation has been cut into the existing Gullen Range Wind Farm - Yass (3J) 330 kV Line to form the following circuits: Gullen Range Wind Farm - Rye Park (3P) 330 kV Transmission Line Rye Park - Yass (3J) 330 kV Transmission Line
Tarong - Chinchilla 132 kV Line | 2023-04-06 | Qld | H18 Tarong - T13 Chinchilla No.7168 132 kV Line and H18 Tarong - T13 Chinchilla No.7183 132 kV Line have been decommissioned.
Tailem Bend – Tungkillo No. 1 275 kV Line | 2023-06-04 | SA | Transmission line commissioned
Tailem Bend – Cherry Gardens 275 kV Line | 2023-06-04 | SA | Transmission line decommissioned
Tungkillo – Cherry Gardens 275 kV line | 2023-06-19 | SA | Transmission line commissioned
Ross 275/132 kV No. 8 transformer | 2023-06-30 | Qld | Transformer commissioned
Glenrowan W1 220kV/33kV Transformer | 2023-07-13 | VIC | Transformer commissioned for Glenrowan Solar Farm
Wagga No 4 330kV 100 MVAR Capacitor | 2023-07-22 | NSW
Mudgeeraba No.3 275kV/110kV Transformer | 2023-08-21 | Qld | Transformer de-commissioned
Tarrone Terminal Station K2 500kV/132kV Transformer | 2023-08-24 | Victoria | Transformer commissioned for Tarrone Terminal Station
Para - Robertstown 275 kV Line | 2023-09-08 | SA | Line decommissioned
Tungkilo - Robertstown No.2 275 kV Line | 2023-09-08 | SA | Line commissioned
Cherry Gardens South 275 kV Reactor | 2023-09-15 | SA
Para - Tungkillo No. 2 275 kV Line | 2023-09-26 | SA | Line commissioned
R4 Millmerran - H14 Middle Ridge No. 9907 330 kV Line | 2023-10-11 | Qld | Line decommissioned
R4 Millmerran – R14 Tummaville No. 9914 330 kV Line | 2023-10-11 | Qld | Line Commissioned cutting decommissioned line into Tummaville.
R14 Tummaville – H14 Middle Ridge No. 9907 330 kV Line | 2023-10-11 | Qld | Line Commissioned cutting decommissioned line into Tummaville.
Western Downs - Banana Bridge No. 8990 275 kV Line | 2023-10-16 | Qld | Line Commissioned
Ross - Woree No. 8905 275 kV Line | 2023-11-01 | Qld | Line Commissioned
Wellington – Wellington North Solar Farm 7H 330 kV Line | 2023-12-08 | NSW | Line Commissioned
Robertstown – Bundey No. 1 275 kV Line | 2023-12-09 | SA | Part of Project Energy Connect
Bundey 275 kV Switchyard | 2023-12-09 | SA | Part of Project Energy Connect
Robertstown - Bundey No.2 275 kV Line | 2023-12-12 | SA | Part of Project Energy Connect
Bundey 330 kV Substation | 2023-12-15 | SA | Part of Project Energy Connect
Liddell Unit 1 | 1 May 2023 | NSW | Deregistered Generator
Liddell Unit 2 | 1 May 2023 | NSW | Deregistered Generator
Liddell Unit 4 | 1 May 2023 | NSW | Deregistered Generator
Tallawara B 320 Mw OCGT | 10 October 2023 | NSW | New Generator
Bouldercombe Bess (Gen Component) | 11 July 2023 | Qld | New Battery
Bouldercombe Bess (Load Component) | 11 July 2023 | Qld | New Battery
Goyder South Wind Farm 1A | 11 July 2023 | SA | New Generator
Pibess Gen1 | 12 April 2023 | Victoria | New Battery
Pibess Load1 | 12 April 2023 | Victoria | New Battery
Mannum 2 Solar Farm | 12 December 2023 | SA | New Generator
Rye Park 384 Mw Windfarm | 15 August 2023 | NSW | New Generator
Chinchilla Bess (Gen Component) | 21 November 2023 | Qld | New Battery
Chinchilla Bess (Load Component) | 21 November 2023 | Qld | New Battery
Glenrowan Solar Farm | 21 November 2023 | Victoria | New Generator
Goyder South Wind Farm 1B | 21 November 2023 | SA | New Generator
Ress Battery (Gen Mode) | 23 May 2023 | NSW | New Generator
Ress Battery (Load Mode) | 23 May 2023 | NSW | New Generator
Riverina Battery 2 (Gen Mode) 65 Mw | 23 May 2023 | NSW | New Battery
Riverina Battery 2 (Load Mode) 65 Mw | 23 May 2023 | NSW | New Battery
Hunter Economic Zone (28 Mw) Diesel Generator | 24 October 2023 | NSW | New Generator
Capital Battery 125.4 Mw (Gen Mode) | 25 July 2023 | NSW | New Generator
Capital Battery 125.4 Mw (Load Mode) | 25 July 2023 | NSW | New Generator
Torrens Island Battery (Generation Mode) Mw | 26 April 2023 | SA | New Battery
Torrens Island Battery (Load Mode) Mw | 26 April 2023 | SA | New Battery
Tailem Bend Battery (Gen Component) | 28 February 2023 | SA | New Generator
Tailem Bend Battery (Load Component) | 28 February 2023 | SA | New Generator
Tb2 Solar Gen | 28 February 2023 | NSW | New Generator
Avonlie Solar Farm (254 Mw) | 28 March 2023 | NSW | New Generator
Broken Hill Battery 50 Mw (Gen Mode) | 28 November 2023 | NSW | New Battery
Broken Hill Battery 50 Mw (Load Mode) | 28 November 2023 | NSW | New Battery
Dr Enelx V240 | 3 October 2023 | Victoria | New WDR unit
Darlington Point Battery (Gen Mode) 25 Mw | 30 May 2023 | NSW | New Battery
Darlington Point Battery (Load Mode) 25 Mw | 30 May 2023 | NSW | New Battery
Dulacca Wind Farm | 4 April 2023 | Qld | New Generator
Wyalong Solar Farm (90 Mw) | 6 June 2023 | NSW | New Generator
Hazelwood Battery (Generation Component) | 7 February 2023 | Victoria | New Battery
Hazelwood Battery (Load Component) | 7 February 2023 | Victoria | New Battery
Wandoan Solar Farm 1 | 7 March 2023 | Qld | New Generator
Flyers Creek Wind Farm (140 Mw) | 8 August 2023 | NSW | New Generator

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.