## Authorisation
2023 RCM - thermal ratings
Version # | Date | Summary of change
0 | 2023-04-13 | Original version
Authorisation
| Date | Title | Name
Approver | 2023-04-13 | Network Access Engineering Manager | Dugald Bell
DM# | 63390028

## Notes
Comments | Descriptions
TRIS Limit | (TRIS) AMP Tx Rating
Hard Limit: TRIS minus 20A | (TRIS) AMP Tx -20 A (if Hard Limit)
Manual Override | Manual Override
Reasonability Limit minus 5A | SCADA High Reasonability (HR) -5A
90% TPES POL | 90% Minimum Line Protection
TRIS Rating | Same as TRIS Limit
RLY Thermal Limit | Relay Thermal Limit
Facility | Facility name | Connection
CBS | Collie_ESR (1->4) | CBS connected via (1) New 300m of 330kV line to tee to CPS-SHO 91 line at 300m from CPS & (2) new 3km of 330kV line to SHO
CNS | Cunderdin solar farm | T-Connection to the 132 KV MRT-NOR line. Location of connection point in SWIS base case
FRW1 | Flat Rock windfarm 1 | Via tee-connection to the existing 132kV Kojonup to Albany (KOJ-ALB 81) transmission line at 50% line length.
KRW | King Rocks Wind Farm | New 33/132 kV substation with 1km cut-in cut-out connection into the Kondinin-Bounty 132 kV line at 50% of line length
New PTA load to supplied from new WHT (Whiteman Park) sub |  | WHT cut in/out of NT-HZM 81 line
The abbreviated names of the facilities, proposed substations and proposed tee point names may change when the facilities are connected to SWIS

## Lines
Equipment ID | Site ID | Line Description | # Connections | ALTLIMIT Time | Rating Unit | Equip. Type | Active Limits Y/N | 1 pu KV | LDSH Time | ALTLIMIT Time | Rating Unit | NORM IN | R | EMER IN | R | LDSH IN | R | NORM OUT | R | EMER OUT | R | LDSH OUT | R | Comments | Revision Date | Note
NT_A_81 | A | A 801 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
NT_A_81 | NT | NT 833 A81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
A_OP_81 | A | A 809 OP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
A_OP_81 | OP | OP 802 A81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
AFM_81_RWA | AFM | AFM 801 RO/WM81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
RO_81_RWA | RO | RO 809 AFM/WM81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
WM_81_RWA | WM | WM 806 RO/AFM81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_AKW_81 | KW | KW 812 AKW81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 225 | P | 225 | P | 225 | P | 225 | P | 225 | P | 225 | P | 90% TPES POL | 28/03/2023
KOJ_ALB_81 | ALB | ALB 810 KOJ81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
KOJ_ALB_81 | KOJ | KOJ 802 ALB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
ALB_KFA | ALB | ALB 810 KOJ/FRW1 81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | FRW1 tee to ALB-KOJ 81. Hard Limit: TRIS minus 20A | 2023-04-11
FRW1_KFA | FRW1 | FRW1 to KOJ/ALB81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | FRW1 tee to KOJ-ALB81. Hard Limit: TRIS minus 20A | 2023-04-11
KOJ_KFA | KOJ | KOJ 802 ALB/FRW1 81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | FRW1 tee to KOJ-ALB81. Hard Limit: TRIS minus 20A | 2023-04-11
MBR_ALB_81 | ALB | ALB 804 MBR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 230 | C | 230 | C | 230 | C | 230 | C | 230 | C | 230 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MBR_ALB_81 | MBR | MBR 802 ALB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 230 | C | 230 | C | 230 | C | 230 | C | 230 | C | 230 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
AMT_CTE_81 | AMT | AMT 801 CTE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
AMT_CTE_81 | CTE | CTE 811 AMT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_AMT_81 | AMT | AMT 808 SF81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1070 | L | 1070 | L | 1070 | L | 1070 | L | 1070 | L | 1070 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_AMT_81 | SF | SF 814 AMT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1070 | L | 1070 | L | 1070 | L | 1070 | L | 1070 | L | 1070 | L | AmpTx 41 Degree Rating | 28/03/2023
APJ_OLY_91 | APJ9 | APJ OLY91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
APJ_OLY_91 | OLY | OLY 903 APJ91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
PNJ_APJ_81 | APJ | APJ 810 PNJ81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PNJ_APJ_81 | PNJ | PNJ 801 APJ81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
APJ_81_SWA | APJ | APJ 804 SNR/WGP81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 528 | L | 528 | L | 528 | L | 528 | L | 528 | L | 528 | L | AmpTx 41 Degree Rating | 28/03/2023
SNR_81_SWA | SNR | SNR 801 APJ/WGP81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 528 | L | 528 | L | 528 | L | 528 | L | 528 | L | 528 | L | AmpTx 41 Degree Rating | 28/03/2023
APM_MYR_71 | APM | APM 708 MYR71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023
APM_MYR_71 | MYR | MYR 701 APM71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023
APM_SF_71 | APM | APM 701 SF71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
BCH_H_81 | BCH | BCH 808 H81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
BCH_H_81 | H | H 807 BCH81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_BCH_81 | BCH | BCH 802 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_BCH_81 | NT | NT 830 BCH81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
BCT_NB_81 | BCT | BCT 808 NB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023
BCT_NB_81 | NB | NB 809 BCT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_BCT_81 | BCT | BCT 801 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_BCT_81 | NT | NT 812 BCT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023
KEL_BDE_71 | KEL | KEL 701 BDE/MER71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 234 | X | 234 | X | 234 | X | 234 | X | 234 | X | 234 | X | Manual Override | 28/03/2023
BDE_MER_71 | MER | MER 706 BDE/KEL71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 234 | X | 234 | X | 234 | X | 234 | X | 234 | X | 234 | X | Manual Override | 28/03/2023
KEM_BDP_81 | BDP | BDP E01 KEM81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 572 | L | 572 | L | 572 | L | 572 | L | 572 | L | 572 | L | AmpTx 41 Degree Rating | 28/03/2023
KEM_BDP_81 | KEM | KEM 834 BDP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 572 | L | 572 | L | 572 | L | 572 | L | 572 | L | 572 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_BEC_81 | CT | CT 802 BEC81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 211 | P | 211 | P | 211 | P | 211 | P | 211 | P | 211 | P | 90% TPES POL | 28/03/2023
BEL_81_NEB | BEL | BEL 809 EP/NT81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_81_NEB | EP | EP 834 BEL/NT81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_81_NEB | NT | NT 816 BEL/EP81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
BEL_KDL_81 | BEL | BEL 801 KDL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
BEL_KDL_81 | KDL | KDL 807 BEL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
BEL_81_RWB | BEL | BEL 810 RVE/WE81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
RVE_81_RWB | RVE | RVE 808 WE/BEL81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
WE_81_RWB | WE | WE 802 RVE/BEL81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
BGA_81_BCE | BGA | BGA 802 CTB/EMD81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023
CTB_81_BCE | CTB | CTB 806 EMD/BGA81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023
EMD_81_BCE | EMD | EMD 802 CTB/BGA81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023
BGA_ENB_81 | BGA | BGA 801 ENB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | AmpTx 41 Degree Rating | 28/03/2023
BGA_ENB_81 | ENB | ENB 804 BGA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | AmpTx 41 Degree Rating | 28/03/2023
BOD_BGM_81 | BOD | BOD 810 BGM81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 900 | P | 900 | P | 900 | P | 900 | P | 900 | P | 900 | P | 90% TPES POL | 28/03/2023
BHK_71_KBB | BHK | BHK 701 KW/BP71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 55 | O | 55 | O | 55 | O | 55 | O | 55 | O | 55 | O | Reasonability Limit minus 5A | 28/03/2023
BP_71_KBB | BP | BP 705 KW/BHK71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_71_KBB | KW | KW 722 BHK/BP71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_BIB_81 | BIB | BIB 807 KW81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_BIB_81 | KW | KW 864 BIB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_BIB_81 | BIB | BIB 802 SF81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_BIB_81 | SF | SF 844 BIB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
WKT_BKF_81 | WKT | WKT 812 BKF81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 292 | C | 292 | C | 292 | C | 292 | C | 292 | C | 292 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
BLD_81_BPP | BLD | BLD 812 PCY/PKS81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PCY_81_BPP | PCY | PCY 801 PKS/BLD81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PKS_81_BPP | PKS | PKS 801 SUT1 HV CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 373 | T | 373 | T | 373 | T | 373 | T | 373 | T | 373 | T | Hard Limit: AmpTx minus 20A | 28/03/2023
WKT_BLD_81 | BLD | BLD 808 WKT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
WKT_BLD_81 | WKT | WKT 805 BLD81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
BLD_WMS_81 | BLD | BLD 802 WMS81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 355 | C | 355 | C | 355 | C | 355 | C | 355 | C | 355 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
BLD_WMS_81 | WMS | WMS 805 BLD81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 355 | C | 355 | C | 355 | C | 355 | C | 355 | C | 355 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
BLW_BWP_91 | BLW | BLW 903 BWP 91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
BLW_BWP_92 | BLW | BLW 907 BWP92 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MU_BLW_91 | BLW | BLW 901 MU91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_BLW_91 | MU | MU 954 BLW91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023
BLW_SHO_91 | BLW | BLW 905 SHO91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | AmpTx 41 Degree Rating | 28/03/2023
BLW_SHO_91 | SHO | SHO 924 BLW91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | AmpTx 41 Degree Rating | 28/03/2023
MJP_BNP_81 | MJP | MJP 801 BNP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | Reasonability Limit minus 5A | 28/03/2023
KDN_BNY_81 | BNY | BNY 801 KDN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | Hard Limit: AmpTx minus 20A | 28/03/2023
KDN_BNY_81 | KDN | KDN 801 BNY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | Hard Limit: AmpTx minus 20A | 28/03/2023
BNY_81_BKK | BNY | BNY 801 KDN/KRW CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | KRW tee to KDN-BNY81. Hard Limit: AmpTx minus 20A | 2023-04-11
KDN_81_BKK | KDN | KDN 801 BNY/KRW CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 183 | T | 183 | T | 183 | T | 183 | T | 183 | T | 183 | T | KRW tee to KDN-BNY 81. POL limitation removed | 2023-04-11
KRW_81_BKK | KRW | KRW to BNY/KDN CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 183 | T | 183 | T | 183 | T | 183 | T | 183 | T | 183 | T | KRW tee to KDN-BNY 81. POL limitation removed | 2023-04-11
WLT_BOD_81 | BOD | BOD 807 WLT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023
WLT_BOD_81 | WLT | WLT 807 BOD81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023
WLT_BOD_82 | BOD | BOD 802 WLT82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023
WLT_BOD_82 | WLT | WLT 802 BOD82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_BP_72 | KW | KW 752 BP72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023
MRR_BSI_81 | MRR | MRR 811 BSI81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 382 | P | 382 | P | 382 | P | 382 | P | 382 | P | 382 | P | 90% TPES POL | 28/03/2023
CAP_BSN_71 | CAP | CAP 709 BSN71 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | AmpTx 41 Degree Rating | 28/03/2023
CAP_BSN_72 | CAP | CAP 701 BSN72 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 374 | L | 374 | L | 374 | L | 374 | L | 374 | L | 374 | L | AmpTx 41 Degree Rating | 28/03/2023
KEM_81_PPBK | KEM | KEM 844 BSN/PIC/PNJ81 CURRENT | 4 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
BSN_MR_71 | BSN | BSN 702 MR71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023
BSN_81_PPBK | BSN | BSN 809 PNJ/PIC/KEM81 CURRENT | 4 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PIC_81_PPBK | PIC | PIC 803 BSN/PNJ/KEM81 CURRENT | 4 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PNJ_81_PPBK | PNJ | PNJ 804 PIC/BSN/KEM81 CURRENT | 4 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
BTN_81_MMB | BTN | BTN 802 MU/MJP81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
MJP_81_MMB | MJP | MJP 802 MU/BTN81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_81_MMB | MU | MU 814 MJP/BTN81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
BTN_82_MMB | BTN | BTN 807 MU/MJP82 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | AmpTx 41 Degree Rating | 28/03/2023
MJP_82_MMB | MJP | MJP 809 MU/BTN82 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_82_MMB | MU | MU 813 MJP/BTN82 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_BTY_81 | BTY | BTY 809 EP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1064 | L | 1064 | L | 1064 | L | 1064 | L | 1064 | L | 1064 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_BTY_81 | EP | EP 812 BTY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1064 | L | 1064 | L | 1064 | L | 1064 | L | 1064 | L | 1064 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_BTY_81 | BTY | BTY 801 ST81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_BTY_81 | ST | ST 864 BTY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_BUH_81 | BUH | BUH 802 MU81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 703 | L | 703 | L | 703 | L | 703 | L | 703 | L | 703 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_BUH_81 | MU | MU 815 BUH81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 703 | L | 703 | L | 703 | L | 703 | L | 703 | L | 703 | L | AmpTx 41 Degree Rating | 28/03/2023
PIC_BUH_81 | BUH | BUH 809 PIC81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PIC_BUH_81 | PIC | PIC 811 BUH81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
BYF_CC_81 | BYF | BYF 801 CC81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
BYF_CC_81 | CC | CC 801 BYF81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
BYF_81_SBS | BYF | BYF 808 SNR/ST81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
SNR_81_SBS | SNR | SNR 802 BYF/ST81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_81_SBS | ST | ST 812 BYF/SNR81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
CAP_71_CWP | CAP | CAP 727 PIC/WSD71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PIC_71_CWP | PIC | PIC 704 CAP/WSD71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
PIC_CAP_72 | PIC | PIC 712 CAP72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
MER_71_YCM | MER | MER 702 YER/CAR/SX71 CURRENT | 4 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 193 | P | 193 | P | 193 | P | 193 | P | 193 | P | 193 | P | 90% TPES POL | 28/03/2023
MSR_CBP_81 | MSR | MSR 810 CBP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 270 | P | 270 | P | 270 | P | 270 | P | 270 | P | 270 | P | 90% TPES POL | 28/03/2023
CC_CCL_132 | CC | CC 807 CCL81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 199 | L | 199 | L | 199 | L | 199 | L | 199 | L | 199 | L | AmpTx 41 Degree Rating | 28/03/2023
CC_81_KCM | CC | CC 802 KW/MED81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_81_KCM | KW | KW 844 CC/MED81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MED_81_KCM | MED | MED 801 KW/CC81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_CC_81 | CC | CC 809 ST81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_CC_81 | ST | ST 8114 CC81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CGT_MRT_X1 | CGT | CGT X03 MRT X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
CGT_MRT_X1 | MRT | MRT X15 CGT X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023
CGT_YLN_X1 | CGT | CGT X05 WKT/YLN X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 980 | I | 980 | I | 980 | I | 980 | I | 980 | I | 980 | I | Hard Limit: AmpTx minus 20A | 28/03/2023
CGT_YLN_X1 | YLN | YLN X03 CGT X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023
EP_CK_81 | CK | CK 803 EP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1225 | L | 1225 | L | 1225 | L | 1225 | L | 1225 | L | 1225 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_CK_81 | EP | EP 844 CK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1225 | L | 1225 | L | 1225 | L | 1225 | L | 1225 | L | 1225 | L | AmpTx 41 Degree Rating | 28/03/2023
CK_NP_81 | CK | CK 806 NP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
CK_NP_81 | NP | NP 807 CK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_CK_81 | CK | CK 810 WT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_CK_81 | WT | WT 844 CK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_CKB_81 | KW | KW 862 CKB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1019 | L | 1019 | L | 1019 | L | 1019 | L | 1019 | L | 1019 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_CKB_82 | KW | KW 854 CKB82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 540 | L | 540 | L | 540 | L | 540 | L | 540 | L | 540 | L | AmpTx 41 Degree Rating | 28/03/2023
CKN_NOW_81 | CKN | CKN 802 NOW81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 200 | P | 200 | P | 200 | P | 200 | P | 200 | P | 200 | P | 90% TPES POL | 28/03/2023
CKN_WNO_81 | CKN | CKN 801 WNO81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CKN_WNO_81 | WNO | WNO 808 CKN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CKN_YP_81 | CKN | CKN 809 YP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CKN_YP_81 | YP | YP 810 CKN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CL_COL_71 | CL | CL 710 COL71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
CL_COL_71 | COL | COL 703 CL71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
CL_VP_71 | CL | CL 701 VP71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023
CL_VP_71 | VP | VP 708 CL71 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 738 | P | 738 | P | 738 | P | 738 | P | 738 | P | 738 | P | 90% TPES POL | 28/03/2023
PIC_CLP_71 | PIC | PIC 702 CLP71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 202 | P | 202 | P | 202 | P | 202 | P | 202 | P | 202 | P | To be decommissioned under T0496422 - CLP decommissioning | 2023-04-11
MU_CO_71 | CO | CO 709 MU71 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MU_CO_71 | MU | MU 708 CO71 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MU_CO_72 | CO | CO 701 MU72 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 287 | L | 287 | L | 287 | L | 287 | L | 287 | L | 287 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_ST_4 | MU_ST | MU 710 CO72 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 245 | O | 245 | O | 245 | O | 245 | O | 245 | O | 245 | O | Reasonability Limit minus 5A | 28/03/2023
CT_COL_71 | CT | CT 704 COL71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 880 | D | 880 | D | 880 | D | 880 | D | 880 | D | 880 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
GTN_CPN_81 | CPN | CPN 805 GTN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
GTN_CPN_81 | GTN | GTN 801 CPN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
CPN_RAN_81 | CPN | CPN 808 RAN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023
CPN_RAN_81 | RAN | RAN 802 CPN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023
CPS_SHO_91 | SHO | SHO 932 CPS91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | AmpTx 41 Degree Rating | 28/03/2023
CPS_CCS_91 | CPS | CPS to CBS/SHO CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | CBS tee to CPS-SHO91. AmpTx 41 Degree Rating | 2023-04-11
CBS_CCS_91 | CBS | CBS to CPS/SHO CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | CBS tee to CPS-SHO91. AmpTx 41 Degree Rating | 2023-04-11
SHO_CCS_91 | SHO | SHO 932 to CPS/CBS CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | CBS tee to CPS-SHO91. AmpTx 41 Degree Rating | 2023-04-11
CBS_SHO_91 | CBS | CBS to SHO CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | New CBS-SHO 91. AmpTx 41 Degree Rating | 2023-04-11
SHO_CBS_91 | SHO | SHO to CBS CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | New CBS-SHO 91. AmpTx 41 Degree Rating | 2023-04-11
CT_KDL_81 | CT | CT 819 KDL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_KDL_81 | KDL | KDL 802 CT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
KNL_CT_81 | CT | CT 821 KNL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 2877 | L | 2877 | L | 2877 | L | 2877 | L | 2877 | L | 2877 | L | AmpTx 41 Degree Rating | 28/03/2023
KNL_CT_81 | KNL | KNL 801 CT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 2877 | L | 2877 | L | 2877 | L | 2877 | L | 2877 | L | 2877 | L | AmpTx 41 Degree Rating | 28/03/2023
KNL_CT_81 | CT | CT 821 KNL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 2233 | T | 2233 | T | 2233 | T | 2233 | T | 2233 | T | 2233 | T | Hard Limit: TRIS minus 20A | 2023-04-11
KNL_CT_81 | KNL | KNL 801 CT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 2233 | T | 2233 | T | 2233 | T | 2233 | T | 2233 | T | 2233 | T | Hard Limit: TRIS minus 20A | 2023-04-11
CT_MDN_81 | CT | CT 817 MDN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_MDN_81 | MDN | MDN 809 CT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_81_CMP | CT | CT 812 MSS/PNJ81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
MSS_81_CMP | MSS | MSS 802 CT/PNJ81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
PNJ_81_CMP | PNJ | PNJ 809 CT/MSS81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_MW_71 | CT | CT 716 MW71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 370 | L | 370 | L | 370 | L | 370 | L | 370 | L | 370 | L | AmpTx 41 Degree Rating | 28/03/2023 | decomissioned
CT_RTN_81 | CT | CT 805 RTN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_RTN_81 | RTN | RTN 807 CT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_RVE_81 | CT | CT 801 RVE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_RVE_81 | RVE | RVE 801 CT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_CT_81 | CT | CT 803 ST81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
ST_CT_81 | ST | ST 874 CT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
CT_72_CVT | CT | CT 713 TT/VP72 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
TT_72_CVT | TT | TT 701 CT/VP72 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
VP_72_CVT | VP | VP 701 CT/TT72 CURRENT. | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_VP_71 | CT | CT 717 VP71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_VP_71 | VP | VP 712 CT71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_WE_81 | CT | CT 820 WE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
CT_WE_81 | WE | WE 808 CT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
CTB_ENB_81 | CTB | CTB 811 ENB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
CTB_ENB_81 | ENB | ENB 810 CTB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
CTB_KMC_81 | CTB | CTB 810 KMC81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 127 | P | 127 | P | 127 | P | 127 | P | 127 | P | 127 | P | 90% TPES POL | 28/03/2023
PJR_CTB_81 | CTB | CTB 803 PJR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_CTB_81 | PJR | PJR 812 CTB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | AmpTx 41 Degree Rating | 28/03/2023
CTB_RGN_81 | CTB | CTB 809 RGN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
CTB_RGN_81 | RGN | RGN 808 CTB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 595 | O | 595 | O | 595 | O | 595 | O | 595 | O | 595 | O | Reasonability Limit minus 5A | 28/03/2023
WT_CTE_81 | CTE | CTE 801 WT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_CTE_81 | WT | WT 824 CTE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | AmpTx 41 Degree Rating | 28/03/2023
CUN_KEL_71 | CUN | CUN 701 KEL71 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 135 | P | 135 | P | 135 | P | 135 | P | 135 | P | 135 | P | 90% TPES POL | 28/03/2023
NOR_CUN_71 | CUN | CUN 709 NOR71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 324 | L | 324 | L | 324 | L | 324 | L | 324 | L | 324 | L | AmpTx 41 Degree Rating | 28/03/2023
NOR_CUN_71 | NOR | NOR 701 CUN71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 202 | P | 202 | P | 202 | P | 202 | P | 202 | P | 202 | P | 90% TPES POL | 28/03/2023
CVE_G_81 | CVE | CVE 808 G81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CVE_G_81 | G | G 806 CVE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
CVE_WLN_81 | CVE | CVE 801 WLN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
CVE_WLN_81 | WLN | WLN 802 CVE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
D_K_81 | D | D 809 K81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
D_K_81 | K | K 810 D81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
D_MJ_81 | D | D 801 MJ81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
D_MJ_81 | MJ | MJ 802 D81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
D_SVY_81 | D | D 807 SVY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
D_SVY_81 | SVY | SVY 809 D81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_E_71 | E | E 712 SF71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_E_71 | SF | SF 702 E71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_E_72 | E | E 704 SF72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 615 | L | 615 | L | 615 | L | 615 | L | 615 | L | 615 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_E_72 | SF | SF 705 E72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 615 | L | 615 | L | 615 | L | 615 | L | 615 | L | 615 | L | AmpTx 41 Degree Rating | 28/03/2023
EMD_81_PEE | EMD | EMD 801 PJR/ENB81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023
ENB_81_PEE | ENB | ENB 802 PJR/EMD81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_81_PEE | PJR | PJR 814 ENB/EMD81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023
ENB_TS_81 | ENB | ENB 801 TS81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
ENB_TS_81 | TS | TS 804 ENB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
ENT_TST_91 | ENT | ENT 932 TST91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
ENT_TST_91 | TST | TST 942 ENT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
ENT_WDW_91 | ENT | ENT 944 WDW91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
ENT_YDT_91 | ENT | ENT 934 YDT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
ENT_YDT_91 | YDT | YDT 932 ENT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
EP_W_81 | EP | EP 814 HAY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | L | 480 | L | 480 | L | 480 | L | 480 | L | 480 | L | AmpTx 41 Degree Rating | 28/03/2023
W_HAY_81 | HAY | HAY 808 EP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | L | 480 | L | 480 | L | 480 | L | 480 | L | 480 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_W_82 | EP | EP 824 HAY82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 488 | L | 488 | L | 488 | L | 488 | L | 488 | L | 488 | L | AmpTx 41 Degree Rating | 28/03/2023
W_HAY_82 | HAY | HAY 801 EP82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 488 | L | 488 | L | 488 | L | 488 | L | 488 | L | 488 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_JTE_81 | EP | EP 854 JTE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 355 | T | 355 | T | 355 | T | 355 | T | 355 | T | 355 | T | Hard Limit: AmpTx minus 20A | 28/03/2023
EP_JTE_82 | EP | EP 829 JTE82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 242 | T | 242 | T | 242 | T | 242 | T | 242 | T | 242 | T | Hard Limit: AmpTx minus 20A | 28/03/2023
EP_NP_81 | EP | EP 852 NP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1010 | L | 1010 | L | 1010 | L | 1010 | L | 1010 | L | 1010 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_NP_81 | NP | NP 804 EP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1010 | L | 1010 | L | 1010 | L | 1010 | L | 1010 | L | 1010 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_EP_82 | EP | EP 822 ST82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_EP_82 | ST | ST 844 EP82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_SUM_81 | EP | EP 839A SUM81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 180 | P | 180 | P | 180 | P | 180 | P | 180 | P | 180 | P | 90% TPES POL | 28/03/2023
EP_SUM_82 | EP | EP 809B SUM82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 180 | P | 180 | P | 180 | P | 180 | P | 180 | P | 180 | P | 90% TPES POL | 28/03/2023
EP_W_71 | EP | EP 704 W71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 257 | L | 257 | L | 257 | L | 257 | L | 257 | L | 257 | L | AmpTx 41 Degree Rating | 28/03/2023
EP_W_72 | EP | EP 712 W72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 260 | L | 260 | L | 260 | L | 260 | L | 260 | L | 260 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_FFD_81 | FFD | FFD 808 GLT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_FFD_81 | GLT | GLT 805 FFD81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
FFD_MDY_81 | FFD | FFD 802 MDY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
FFD_MDY_81 | MDY | MDY 801 FFD81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
FFD_MVE_81 | FFD | FFD 801 MVE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 90% TPES POL | 28/03/2023 | SCADA Point Name FFD 801 MVE81 CURRENT is not available in AEMO-WP Rating Format table
G_MDN_81 | G | G 808 MDN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
G_MDN_81 | MDN | MDN 801 G81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
G_SNR_81 | G | G 801 SNR81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
G_SNR_81 | SNR | SNR 808 G81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
TS_GGV_81 | TS | TS 801 GGV81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 123 | P | 123 | P | 123 | P | 123 | P | 123 | P | 123 | P | 90% TPES POL | 28/03/2023
GLT_HZM_81 | GLT | GLT 808 HZM81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_HZM_81 | HZM | HZM 807 GLT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_MJ_81 | GLT | GLT 802 MJ81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_MJ_81 | MJ | MJ 810 GLT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_MJ_82 | GLT | GLT 801 MJ82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1175 | L | 1175 | L | 1175 | L | 1175 | L | 1175 | L | 1175 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_MJ_82 | MJ | MJ 801 GLT82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1175 | L | 1175 | L | 1175 | L | 1175 | L | 1175 | L | 1175 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_GLT_82 | GLT | GLT 809 NT82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1213 | L | 1213 | L | 1213 | L | 1213 | L | 1213 | L | 1213 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_GLT_82 | NT | NT 838 GLT82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1213 | L | 1213 | L | 1213 | L | 1213 | L | 1213 | L | 1213 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_NT_91 | GLT | GLT 952 NT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
GLT_NT_91 | NT | NT 964 GLT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
GLT_ST_91 | GLT | GLT 944 ST91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
GLT_ST_91 | ST | ST 972 GLT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
GLT_WLT_81 | GLT | GLT 804 WLT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023
GLT_WLT_81 | WLT | WLT 805 GLT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_GNI_81 | ST | ST 8104 GNI81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 204 | P | 204 | P | 204 | P | 204 | P | 204 | P | 204 | P | 90% TPES POL | 28/03/2023
ST_GNI_82 | ST | ST 8112 GNI82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 204 | P | 204 | P | 204 | P | 204 | P | 204 | P | 204 | P | 90% TPES POL | 28/03/2023
GNN_NBT_91 | NBT | NBT 944 GNN91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MGA_GTN_81 | GTN | GTN 803 MGA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
MGA_GTN_81 | MGA | MGA 842 GTN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
GTN_RAN_81 | GTN | GTN 810 RAN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | AmpTx 41 Degree Rating | 28/03/2023
GTN_RAN_81 | RAN | RAN 809 GTN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | AmpTx 41 Degree Rating | 28/03/2023
WWF_GTN_81 | GTN | GTN 809 WWF81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
WWF_GTN_81 | WWF | WWF 802 GTN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
H_MO_81 | H | H 801 MO81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023
H_MO_81 | MO | MO 801 H81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023
MIL_HAY_81 | HAY | HAY 804 MIL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | Hard Limit: AmpTx minus 20A | 30/03/2023
MIL_HAY_81 | MIL | MIL 804 HAY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
HBK_MUC_81 | HBK | HBK 807 MUC81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
HBK_MUC_81 | MUC | MUC 804 HBK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_HBK_81 | HBK | HBK 802 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_HBK_81 | NT | NT 831 HBK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_HZM_81 | HZM | HZM 802 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_HZM_81 | NT | NT 805 HZM81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 28/03/2023
HZM_WHT_81 | HZM | HZM 802 to WHT CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 2023-04-11
WHT_HZM_81 | WHT | WHT to HZM 802 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 2023-04-11
WHT_NT_81 | WHT | WHT to NT 805 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 2023-04-11
NT_WHT_81 | NT | NT 805 to WHT CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 2023-04-11
JDP_MUL_81 | JDP | JDP 809 MUL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
JDP_MUL_81 | MUL | MUL 813 JDP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
JDP_WNO_81 | JDP | JDP 801 WNO81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
JDP_WNO_81 | WNO | WNO 802 JDP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
K_MDY_81 | K | K 801 MDY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 593 | L | 593 | L | 593 | L | 593 | L | 593 | L | 593 | L | AmpTx 41 Degree Rating | 28/03/2023
K_MDY_81 | MDY | MDY 809 K81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 593 | L | 593 | L | 593 | L | 593 | L | 593 | L | 593 | L | AmpTx 41 Degree Rating | 28/03/2023
KOJ_KAT_71 | KAT | KAT 702 KOJ71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | Reasonability Limit minus 5A | 28/03/2023
KOJ_KAT_71 | KOJ | KOJ 711 KAT71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
KAT_WAG_71 | KAT | KAT 710 WAG71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | Reasonability Limit minus 5A | 28/03/2023
KAT_WAG_71 | WAG | WAG 704 KAT71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | Reasonability Limit minus 5A | 28/03/2023
KDN_MRT_X1 | KDN | KDN X35 MRT X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023
KDN_MRT_X1 | MRT | MRT X35 KDN X1 CURRENT. | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 815 | O | 815 | O | 815 | O | 815 | O | 815 | O | 815 | O | Reasonability Limit minus 5A | 28/03/2023
NGS_KDN_X1 | KDN | KDN X31 MU/NGS X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023
NGS_KDN_X1 | NGS | NGS X31 KDN X1 CURRENT. | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 878 | O | 878 | O | 878 | O | 878 | O | 878 | O | 878 | O | Reasonability Limit minus 5A | 28/03/2023
KDP_81_KKM | KDP | KDP 801 KW/MSR81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_81_KKM | KW | KW 814 KDP/MSR81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | AmpTx 41 Degree Rating | 28/03/2023
MSR_81_KKM | MSR | MSR 826 KW/KDP81 CURRENT. | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | AmpTx 41 Degree Rating | 28/03/2023
KMP_KEM_91 | KEM | KEM 964 KMP91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
KMP_KEM_91 | KMP | KMP KEM91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
KEM_91_KKO | KEM | KEM 962 KW/OLY91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_91_KKO | KW | KW 934 KEM/OLY91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023
OLY_91_KKO | OLY | OLY 905 KEM/KW91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023
KEM_91_LSK | KEM | KEM 952 SHO/LWT91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023
LWT_91_LSK | LWT | LWT 922.0 SHO/KEM91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023
SHO_91_LSK | SHO | SHO 934 KEM/LWT91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023
KEM_MRR_81 | KEM | KEM 824 MRR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | AmpTx 41 Degree Rating | 28/03/2023
KEM_MRR_81 | MRR | MRR 801 KEM81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | AmpTx 41 Degree Rating | 28/03/2023
KEM_MRR_82 | KEM | KEM 814 MRR82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | AmpTx 41 Degree Rating | 28/03/2023
KEM_MRR_82 | MRR | MRR 807 KEM82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_KEM_91 | KEM | KEM 932 MU91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_KEM_91 | MU | MU 944 KEM91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023
MSR_KMK_81 | KMK | KMK 806 MSR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | Reasonability Limit minus 5A | 28/03/2023
MSR_KMK_81 | MSR | MSR 813 KMK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 247 | P | 247 | P | 247 | P | 247 | P | 247 | P | 247 | P | 90% TPES POL | 28/03/2023
MUC_KMM_81 | MUC | MUC 803 KMM81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 90 | P | 90 | P | 90 | P | 90 | P | 90 | P | 90 | P | 90% TPES POL | 28/03/2023
MSR_KND_81 | KND | KND 801 MSR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MSR_KND_81 | MSR | MSR 828 KND81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
ST_KNL_91 | KNL | KNL 901 ST91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
ST_KNL_91 | ST | ST 924 KNL91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
ST_KNL_91 | KNL | KNL 901 ST91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 881 | T | 881 | T | 881 | T | 881 | T | 881 | T | 881 | T | Hard Limit: TRIS minus 20A | 2023-04-11
ST_KNL_91 | ST | ST 924 KNL91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 881 | T | 881 | T | 881 | T | 881 | T | 881 | T | 881 | T | Hard Limit: TRIS minus 20A | 2023-04-11
KOJ_MBR_81 | KOJ | KOJ 812 MBR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | Reasonability Limit minus 5A | 28/03/2023
KOJ_MBR_81 | MBR | MBR 805 KOJ81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | Reasonability Limit minus 5A | 28/03/2023
MU_KOJ_81 | KOJ | KOJ 801 MU81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 350 | L | 350 | L | 350 | L | 350 | L | 350 | L | 350 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_KOJ_81 | MU | MU 812 KOJ81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 350 | L | 350 | L | 350 | L | 350 | L | 350 | L | 350 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_KOJ_82 | KOJ | KOJ 807 MU82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_KOJ_82 | MU | MU 809 KOJ82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
KOJ_WAG_71 | KOJ | KOJ 702 WAG71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 167 | L | 167 | L | 167 | L | 167 | L | 167 | L | 167 | L | AmpTx 41 Degree Rating | 28/03/2023
KOJ_WAG_71 | WAG | WAG 710 KOJ71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 167 | L | 167 | L | 167 | L | 167 | L | 167 | L | 167 | L | AmpTx 41 Degree Rating | 28/03/2023
MSR_KPP_81 | MSR | MSR 816 KPP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MSR_KPP_82 | MSR | MSR 822 KPP82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
TST_KRA_91 | KRA | KRA 901 TST91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
TST_KRA_91 | TST | TST 934 KRA91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
KW_MSR_81 | KW | KW 824 MSR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_MSR_81 | MSR | MSR 817 KW81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_NGK_91 | KW | KW 942 NGK91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 675 | L | 675 | L | 675 | L | 675 | L | 675 | L | 675 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_NT_91 | KW | KW 944 NT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
KW_NT_91 | NT | NT 984 KW91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
KW_SF_82 | KW | KW 894 SF82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_SF_82 | SF | SF 834 KW82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_ST_81 | KW | KW 834 ST81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1787 | L | 1787 | L | 1787 | L | 1787 | L | 1787 | L | 1787 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_ST_81 | ST | ST 832 KW81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1787 | L | 1787 | L | 1787 | L | 1787 | L | 1787 | L | 1787 | L | AmpTx 41 Degree Rating | 28/03/2023
KW_ST_91 | KW | KW 954 ST91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
KW_ST_91 | ST | ST 952 KW91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
KW_ST_92 | KW | KW 964 ST92 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
KW_ST_92 | ST | ST 922 KW92 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
NT_LDE_81 | LDE | LDE 808 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_LDE_81 | NT | NT 835 LDE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
LDE_WGA_81 | LDE | LDE 802 WGA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
LDE_WGA_81 | WGA | WGA 801 LDE81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MSR_LTH_81 | LTH | LTH 802 MSR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 597 |  | 597 |  | 597 |  | 597 |  | 597 |  | 597 |  | AmpTx 41 Degree Rating | 30/03/2023
MSR_LTH_81 | MSR | MSR 825 LTH81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 597 |  | 597 |  | 597 |  | 597 |  | 597 |  | 597 |  | AmpTx 41 Degree Rating | 30/03/2023
MSR_MRN_81 | MSR | MSR 825 MRN81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 597 | L | 597 | L | 597 | L | 597 | L | 597 |  | 597 |  | MRN cut in/out MSR-LTH 81. TRIS Limit | 2023-04-11
MSR_MRN_81 | MRN | MRN 808 MSR81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 597 | L | 597 | L | 597 | L | 597 | L | 597 |  | 597 |  | MRN cut in/out MSR-LTH 81. TRIS Limit | 2023-04-11
MRN_LTH_81 | MRN | MRN 802 LTH81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 597 | L | 597 | L | 597 | L | 597 | L | 597 |  | 597 |  | MRN cut in/out MSR-LTH 81. TRIS Limit | 2023-04-11
MRN_LTH_81 | LTH | LTH 802 MRN81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 597 | L | 597 | L | 597 | L | 597 | L | 597 |  | 597 |  | MRN cut in/out MSR-LTH 81. TRIS Limit | 2023-04-11
LTH_KW_81 | LTH | LTH 807 KW81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 901 | L | 901 | L | 901 | L | 901 | L | 901 |  | 901 |  | New LTH-KW 81. Design Limit Rating minus 5A | 2023-04-11
LTH_KW_81 | KW | KW 884 LTH81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 901 | L | 901 | L | 901 | L | 901 | L | 901 |  | 901 |  | New LTH-KW 81. Design Limit Rating minus 5A | 2023-04-11
LTH_TLA_81 | LTH | LTH 805 TLA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | SCADA Point Name LTH 805 TLA81 CURRENT is not available in AEMO-WP Rating Format table
LTH_TLA_81 | TLA | TLA 804 LTH81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | SCADA Point Name TLA 804 LTH81 CURRENT is not available in AEMO-WP Rating Format table
LWT_ST_91 | LWT | LWT 942.0 ST91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 2015 | L | 2015 | L | 2015 | L | 2015 | L | 2015 | L | 2015 | L | AmpTx 41 Degree Rating | 28/03/2023
LWT_ST_91 | ST | ST 962 LWT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 2015 | L | 2015 | L | 2015 | L | 2015 | L | 2015 | L | 2015 | L | AmpTx 41 Degree Rating | 28/03/2023
MA_NB_81 | MA | MA 801 NB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
MA_NB_81 | NB | NB 802 MA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
MA_OP_81 | MA | MA 807 OP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
MA_OP_81 | OP | OP 801 MA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
MGA_MBA_81 | MBA | MBA 802 MGA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023
MGA_MBA_81 | MGA | MGA 834 MBA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023
TS_MBA_81 | MBA | MBA 806 TS81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
TS_MBA_81 | TS | TS 807 MBA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
MCE_N_71 | MCE | MCE 701 N71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
MCE_N_71 | N | N 706 MCE71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_MCE_71 | MCE | MCE 709 WT71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | Reasonability Limit minus 5A | 28/03/2023
WT_MCE_71 | WT | WT 712 MCE71 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | Reasonability Limit minus 5A | 28/03/2023
MDP_MRT_81 | MDP | MDP 801 MRT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1230 | D | 1230 | D | 1230 | D | 1230 | D | 1230 | D | 1230 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
MDP_MRT_81 | MRT | MRT 807 MDP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1230 | D | 1230 | D | 1230 | D | 1230 | D | 1230 | D | 1230 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
MED_RO_81 | MED | MED 809 RO81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MED_RO_81 | RO | RO 801 MED81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MRT_MER_81 | MRT | MRT 801 MER81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 512 | L | 512 | L | 512 | L | 512 | L | 512 | L | 512 | L | AmpTx 41 Degree Rating | 28/03/2023
MRT_MER_81 | MER | MER 800 MRT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 512 | L | 512 | L | 512 | L | 512 | L | 512 | L | 512 | L | AmpTx 41 Degree Rating | 28/03/2023
MGA_TS_81 | MGA | MGA 844 TS81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
MGA_TS_81 | TS | TS 808 MGA81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
MGA_WWF_81 | MGA | MGA 824 WWF81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023
MGA_WWF_81 | WWF | WWF 806 MGA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023
MH_81_MWM | MH | MH 809 MSS/WAI81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
MSS_81_MWM | MSS | MSS 805 MH/WAI81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
WAI_81_MWM | WAI | WAI 809 MH/MSS81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
MH_PNJ_81 | MH | MH 802 PNJ81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 680 | L | 680 | L | 680 | L | 680 | L | 680 | L | 680 | L | AmpTx 41 Degree Rating | 28/03/2023
MH_PNJ_81 | PNJ | PNJ 806 MH81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 680 | L | 680 | L | 680 | L | 680 | L | 680 | L | 680 | L | AmpTx 41 Degree Rating | 28/03/2023
JAM_MIL_81 | MIL | MIL 808 MLA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
MLA_JAM_81 | MLA | MLA 803 MIL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | Hard Limit: AmpTx minus 20A | 28/03/2023
JAM_MIL_82 | MIL | MIL 801 MLA82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MLA_JAM_82 | MLA | MLA 806 MIL82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MLA_MO_81 | MLA | MLA 807 MO81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
MLA_MO_81 | MO | MO 812 MLA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_MLA_81 | MLA | MLA 802 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_MLA_81 | NT | NT 811 MLA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_MLA_82 | MLA | MLA 805 NT82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_MLA_82 | NT | NT 813 MLA82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
MLA_Y_81 | MLA | MLA 801 Y81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MOR_MUC_81 | MOR | MOR 801 MUC81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
MOR_MUC_81 | MUC | MUC 801 MOR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
MOR_TS_81 | MOR | MOR 806 TS81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
MOR_TS_81 | TS | TS 802 MOR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023
PIC_MRR_81 | MRR | MRR 810 MRR PIC 81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
PIC_MRR_81 | PIC | PIC 806 MRR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
MRT_MRS_81 | MRT | MRT X44 MRS X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 1245 | O | 1245 | O | 1245 | O | 1245 | O | 1245 | O | 1245 | O | Reasonability Limit minus 5A | 28/03/2023
MRT_NOR_81 | MRT | MRT 803 NOR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | RLY Thermal Limit | 28/03/2023
MRT_NOR_81 | NOR | NOR 802 MRT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | RLY Thermal Limit | 28/03/2023
MRT_81_NCM | MRT | MRT 803 CNS/NOR81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | CNS tee to MRT-NOR 81. RLY Thermal Limit | 2023-04-11
CNS_81_NCM | CNS | CNS to MRT/NOR81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | CNS tee to MRT-NOR 81. RLY Thermal Limit | 2023-04-11
NOR_81_NCM | NOR | NOR 802 CNS/MRT81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | CNS tee to MRT-NOR 81. RLY Thermal Limit | 2023-04-11
WM_81_MWO | WM | WM 803 MSR/OFE81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MSR_81_MWO | MSR | MSR 814 WM/OFE81 CURRENT | 3 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | SCADA Point Name MSR 814 WM/OFE81 CURRENT is not available in AEMO-WP Rating Format table
MSS_PLD_81 | MSS | MSS 801 PLD81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 590 | U | 590 | U | 590 | U | 590 | U | 590 | U | 590 | U | Hard Limit: AmpTx minus 20A | 28/03/2023
MSS_PLD_82 | MSS | MSS 808 PLD82 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 610 | L | 610 | L | 610 | L | 610 | L | 610 | L | 610 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_NGS_X1 | MU | MU X24 NGS/KDN X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MU_NGS_X1 | NGS | NGS X15 KDN/MU X1 CURRENT. | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MU_NT_91 | MU | MU 924 NT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_NT_91 | NT | NT 994 MU91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_WCL_81 | MU | MU 817 WCL81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
MU_WCL_81 | WCL | WCL 805 MU81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_MUC_81 | MUC | MUC 807 PJR81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_MUC_81 | PJR | PJR 834 MUC81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_MUC_82 | MUC | MUC 809 PJR82 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
PJR_MUC_82 | PJR | PJR 824 MUC82 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
MUL_PBY_81 | MUL | MUL 802 PBY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MUL_PBY_81 | PBY | PBY 807 MUL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MUL_WGA_81 | MUL | MUL 801 WGA81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MUL_WGA_81 | WGA | WGA 809 MUL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MUR_RTN_81 | MUR | MUR 809 RTN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MUR_RTN_81 | RTN | RTN 801 MUR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_MUR_81 | MUR | MUR 802 ST81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_MUR_81 | ST | ST 822 MUR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MW_WUN_71 | WUN | WUN 701 MW71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023 | decomissioned
MYR_OC_71 | MYR | MYR 708 OC71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
MYR_OC_71 | OC | OC 704 MYR71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | Reasonability Limit minus 5A | 28/03/2023
WT_N_71 | N | N 701 WT71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_N_71 | WT | WT 709 N71 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 675 | P | 675 | P | 675 | P | 675 | P | 675 | P | 675 | P | 90% TPES POL | 28/03/2023
WT_N_72 | N | N 709 WT72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_N_72 | WT | WT 706 N72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
NB_PBY_81 | NB | NB 801 PBY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
NB_PBY_81 | PBY | PBY 802 NB81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
NBT_NT_91 | NBT | NBT 972 NT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
NBT_NT_91 | NT | NT 962 NBT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
NBT_PJR_81 | NBT | NBT 864 PJR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | AmpTx 41 Degree Rating | 28/03/2023
NBT_PJR_81 | PJR | PJR 884 NBT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | AmpTx 41 Degree Rating | 28/03/2023
NBT_WNO_81 | NBT | NBT 874 WNO81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | AmpTx 41 Degree Rating | 28/03/2023
NBT_WNO_81 | WNO | WNO 810 NBT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | AmpTx 41 Degree Rating | 28/03/2023
NBT_YDT_91 | NBT | NBT 962 YDT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
NBT_YDT_91 | YDT | YDT 934 NBT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023
NGN_71_NWN | NGN | NGN 702 NGS/WAG71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 315 | O | 315 | O | 315 | O | 315 | O | 315 | O | 315 | O | Reasonability Limit minus 5A | 28/03/2023
NGS_71_NWN | NGS | NGS 703 NGN/WAG71 CURRENT | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
WAG_71_NWN | WAG | WAG 713 NGN/NGS71 CURRENT. | 3 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 225 | P | 225 | P | 225 | P | 225 | P | 225 | P | 225 | P | 90% TPES POL | 28/03/2023
NGS_NGN_71 | NGS | NGS 701 NGN71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
NT_NOR_81 | NOR | NOR 811 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 441 | L | 441 | L | 441 | L | 441 | L | 441 | L | 441 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_NOR_81 | NT | NT 803 NOR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 441 | L | 441 | L | 441 | L | 441 | L | 441 | L | 441 | L | AmpTx 41 Degree Rating | 28/03/2023
NOR_SVY_81 | NOR | NOR 807 SVY81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
NOR_SVY_81 | SVY | SVY 802 NOR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023
NOR_WUN_71 | NOR | NOR 710 WUN71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 287 | L | 287 | L | 287 | L | 287 | L | 287 | L | 287 | L | AmpTx 41 Degree Rating | 28/03/2023 | decomissioned
NP_SRD_81 | NP | NP 801 SRD81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 90% TPES POL | 28/03/2023
NP_SRD_81 | NP | NP 801 SRD81 CURRENT | 1 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 90% TPES POL | 01/07/2022
NT_PJR_81 | NT | NT 802 PJR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1580 | C | 1580 | C | 1580 | C | 1580 | C | 1580 | C | 1580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
NT_PJR_81 | PJR | PJR 844 NT81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1580 | C | 1580 | C | 1580 | C | 1580 | C | 1580 | C | 1580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
NT_SPK_81 | NT | NT 804 SPK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
NT_SPK_81 | SPK | SPK 808 NT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
SF_OC_71 | OC | OC 702 SF71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 700 | C | 700 | C | 700 | C | 700 | C | 700 | C | 700 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
SF_OC_71 | SF | SF 704 OC71 CURRENT. | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 700 | C | 700 | C | 700 | C | 700 | C | 700 | C | 700 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
SF_OC_72 | OC | OC 712 SF72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 712 | L | 712 | L | 712 | L | 712 | L | 712 | L | 712 | L | AmpTx 41 Degree Rating | 28/03/2023
OLY_91_SSO | OLY | OLY 901 SHO/ST91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023
SHO_91_SSO | SHO | SHO 944 OLY/ST91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_91_SSO | ST | ST 932 OLY/SHO91 CURRENT | 3 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023
OP_Y_81 | OP | OP 809 Y81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
OP_Y_81 | Y | Y 810 OP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
WKT_PCY_81 | PCY | PCY 807 WKT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
WKT_PCY_81 | WKT | WKT 811 PCY81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023
PIC_WOR_81 | PIC | PIC 808 WOR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 995 | L | 995 | L | 995 | L | 995 | L | 995 | L | 995 | L | AmpTx 41 Degree Rating | 28/03/2023
PIC_WOR_81 | WOR | WOR 806 PIC81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 995 | L | 995 | L | 995 | L | 995 | L | 995 | L | 995 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_RGN_81 | PJR | PJR 822 RGN81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_RGN_81 | RGN | RGN 802 PJR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_YP_81 | PJR | PJR 864 YP81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
PJR_YP_81 | YP | YP 801 PJR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
RO_WAI_81 | RO | RO 802 WAI81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 801 | L | 801 | L | 801 | L | 801 | L | 801 | L | 801 | L | AmpTx 41 Degree Rating | 28/03/2023
RO_WAI_81 | WAI | WAI 801 RO81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 801 | L | 801 | L | 801 | L | 801 | L | 801 | L | 801 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_SF_81 | SF | SF 824 ST81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1215 | L | 1215 | L | 1215 | L | 1215 | L | 1215 | L | 1215 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_SF_81 | ST | ST 834 SF81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1215 | L | 1215 | L | 1215 | L | 1215 | L | 1215 | L | 1215 | L | AmpTx 41 Degree Rating | 28/03/2023
SHO_WLT_91 | SHO | SHO 942 WLT91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 2034 | L | 2034 | L | 2034 | L | 2034 | L | 2034 | L | 2034 | L | AmpTx 41 Degree Rating | 28/03/2023
SHO_WLT_91 | WLT | WLT 901 SHO91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 2034 | L | 2034 | L | 2034 | L | 2034 | L | 2034 | L | 2034 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_SPK_81 | SPK | SPK 805 WT81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_SPK_81 | WT | WT 854 SPK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_WLN_81 | ST | ST 894 WLN81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
ST_WLN_81 | WLN | WLN 809 ST81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023
YER_SX_71 | SX | SX 709 YER/CAR/MER71 CURRENT. | 4 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 352 | L | 352 | L | 352 | L | 352 | L | 352 | L | 352 | L | AmpTx 41 Degree Rating | 28/03/2023
TST_TS_81 | TS | TS 820 TST81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 678 | L | 678 | L | 678 | L | 678 | L | 678 | L | 678 | L | AmpTx 41 Degree Rating | 28/03/2023
TST_TS_81 | TST | TST 841 TS81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 678 | L | 678 | L | 678 | L | 678 | L | 678 | L | 678 | L | AmpTx 41 Degree Rating | 28/03/2023
WCL_WOR_81 | WCL | WCL 801 WOR81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023
WCL_WOR_81 | WOR | WOR 801 WCL81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_WD_71 | WD | WD 709 WT71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_WD_71 | WT | WT 703 WD71 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_WD_72 | WD | WD 701 WT72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
WT_WD_72 | WT | WT 713 WD72 CURRENT | 2 | RCM | AMP | LINE | Y | 66 | 15 | RCM | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023
WGP_WOR_81 | WGP | WGP 808 WOR81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 28/03/2023
WGP_WOR_81 | WOR | WOR 809 WGP81 CURRENT. | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 796 | L | 796 | L | 796 |  | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 28/03/2023
YLN_WKT_X1 | WKT | WKT X42 CGT/YLN X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 442 | P | 442 | P | 442 | P | 442 | P | 442 | P | 442 | P | 90% TPES POL | 28/03/2023
YLN_WKT_X1 | YLN | YLN X05 WKT X1 CURRENT | 2 | RCM | AMP | LINE | Y | 220 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023
WMS_WMK_81 | WMS | WMS 801 WMK81 CURRENT | 2 | RCM | AMP | LINE | Y | 132 | 15 | RCM | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023
YDT_YDW_91 | YDT | YDT 944 YDW91 CURRENT | 2 | RCM | AMP | LINE | Y | 330 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023

## Transformers
Site ID | Equipment ID | Transformer Description | ALTLIMIT Time | Rating Unit | Equip. Type | Active Limits Y/N | 1 pu KV | LDSH Time | ALTLIMIT Time | Rating Unit | NORM IN | R | EMER IN | R | LDSH IN | R | NORM OUT | R | EMER OUT | R | LDSH OUT | R | Comments | Revision Date | User Name | Static/Dynamic
BSN | T4_L | BSN715T4 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 558 | P | 558 | P | 558 | P | 558 | P | 558 | P | 558 | P | 90% TPES POL | 28/03/2023 | N039716 | Static
CT | T3_L | CT711T3 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1104 | T | 1104 | T | 1104 | T | 1104 | T | 1104 | T | 1104 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
CT | T1_L | CT714T1 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1088 | T | 1088 | T | 1088 | T | 1088 | T | 1088 | T | 1088 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
CT | T4_L | CT722T4 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1063 | T | 1063 | T | 1063 | T | 1063 | T | 1063 | T | 1063 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
CT | T3_H | CT806T3 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 577 | T | 577 | T | 577 | T | 577 | T | 577 | T | 577 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
CT | T1_H | CT808T1 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 569 | T | 569 | T | 569 | T | 569 | T | 569 | T | 569 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
CT | T4_H | CT814T4 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 555 | C | 555 | C | 555 | C | 555 | C | 555 | C | 555 | C | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
EP | T5_L | EP705T5 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
EP | T3_L | EP713T3 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
EP | T5_H | EP832T5 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
EP | T3_H | EP842T3 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
GLT | T1_L | GLT807T1 LV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 2231 | T | 2231 | T | 2231 | T | 2231 | T | 2231 | T | 2231 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
GLT | T1_H | GLT954T1 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 892 | T | 892 | T | 892 | T | 892 | T | 892 | T | 892 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KDN | T2_T | KDN614T2 TV | RCM | AMP | TRANS | Y | 33 | 15 | RCM | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | Static
KEM | T1_L | KEM812T1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 1054 | T | 1054 | T | 1054 | T | 1054 | T | 1054 | T | 1054 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KEM | T2_L | KEM822T2 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2336 | D | 2336 | D | 2336 | D | 2336 | D | 2336 | D | 2336 | D | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KEM | T13_LV | KEM842T13 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 1870 | O | 1870 | O | 1870 | O | 1870 | O | 1870 | O | 1870 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | Static
KEM | T13_H | KEM934T13 LV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 994 | T | 994 | T | 994 | T | 994 | T | 994 | T | 994 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KNL | T1_L | KNL801T1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2253 | T | 2253 | T | 2253 | T | 2253 | T | 2253 | T | 2253 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KNL | T1_H | KNL901T1 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 901 | T | 901 | T | 901 | T | 901 | T | 901 | T | 901 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KOJ | T1_L | KOJ703T1 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 219 | T | 219 | T | 219 | T | 219 | T | 219 | T | 219 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KOJ | T2_L | KOJ709T2 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 192 | T | 192 | T | 192 | T | 192 | T | 192 | T | 192 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KW | SDT1_T | KW504SDT1 TV | RCM | AMP | TRANS | Y | 22 | 15 | RCM | AMP | 1653 | C | 1653 | C | 1653 | C | 1653 | C | 1653 | C | 1653 | C | Remove as not applicable to RCM calculation. AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KW | SDT2_T | KW509SDT2 TV | RCM | AMP | TRANS | Y | 22 | 15 | RCM | AMP | 1653 | C | 1653 | C | 1653 | C | 1653 | C | 1653 | C | 1653 | C | Remove as not applicable to RCM calculation. AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KW | SDT1_H | KW822SDT1 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 276 | T | 276 | T | 276 | T | 276 | T | 276 | T | 276 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KW | SDT2_H | KW852SDT2 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 276 | T | 276 | T | 276 | T | 276 | T | 276 | T | 276 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KW | BTT1_L | KW884BTT1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2270 | T | 2270 | T | 2270 | T | 2270 | T | 2270 | T | 2270 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
KW | BTT1_H | KW932BTT1 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 908 | T | 908 | T | 908 | T | 908 | T | 908 | T | 908 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MER | T3_803_L | MER701T3(132/66) LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 435 | T | 435 | T | 435 | T | 435 | T | 435 | T | 435 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MER | T1_807_L | MER707T1(132/66) LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 385 | T | 385 | T | 385 | T | 385 | T | 385 | T | 385 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MU | SDT2_L | MU709SDT2 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 245 | O | 245 | O | 245 | O | 245 | O | 245 | O | 245 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | Static
MU | SDT1_L | MU711SDT1 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 245 | O | 245 | O | 245 | O | 245 | O | 245 | O | 245 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | Static
MU | BTT2_L | MU801BTT2 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 1282 | T | 1282 | T | 1282 | T | 1282 | T | 1282 | T | 1282 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MU | SDT2_H | MU810SDT2 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 122 | T | 122 | T | 122 | T | 122 | T | 122 | T | 122 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MU | SDT1_H | MU811SDT1 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 122 | T | 122 | T | 122 | T | 122 | T | 122 | T | 122 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MU | BTT1_L | MU824BTT1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2528 | T | 2528 | T | 2528 | T | 2528 | T | 2528 | T | 2528 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MU | BTT3_H | MU903BTT3 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 768 | T | 768 | T | 768 | T | 768 | T | 768 | T | 768 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MU | BTT1_H | MU914BTT1 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 985 | P | 985 | P | 985 | P | 985 | P | 985 | P | 985 | P | 90% TPES POL | 28/03/2023 | N039716 | Static
MU | BTT2_H | MUX23BTT2 HV | RCM | AMP | TRANS | Y | 220 | 15 | RCM | AMP | 769 | T | 769 | T | 769 | T | 769 | T | 769 | T | 769 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
MU | BTT3_L | MUX33BTT3 LV | RCM | AMP | TRANS | Y | 220 | 15 | RCM | AMP | 1152 | D | 1152 | D | 1152 | D | 1152 | D | 1152 | D | 1152 | D | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NBT | T2_L | NBT872T2 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2253 | T | 2253 | T | 2253 | T | 2253 | T | 2253 | T | 2253 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NBT | T2_H | NBT964T2 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 901 | T | 901 | T | 901 | T | 901 | T | 901 | T | 901 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NGS | T1_L | NGS704T1 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 234 | T | 234 | T | 234 | T | 234 | T | 234 | T | 234 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NGS | T1_H | NGSX15T1 HV | RCM | AMP | TRANS | Y | 220 | 15 | RCM | AMP | 73 | T | 73 | T | 73 | T | 73 | T | 73 | T | 73 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NOR | T2_804_L | NOR703T2(132/66) LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 332 | T | 332 | T | 332 | T | 332 | T | 332 | T | 332 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NOR | T1_810_L | NOR709T1(132/66) LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 332 | T | 332 | T | 332 | T | 332 | T | 332 | T | 332 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NOR | T2_804_H | NOR804T2(132/66) HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 166 | T | 166 | T | 166 | T | 166 | T | 166 | T | 166 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NOR | T1_810_H | NOR810T1(132/66) HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 166 | T | 166 | T | 166 | T | 166 | T | 166 | T | 166 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NT | T1_L | NT801T1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | Static
NT | T2_L | NT808T2 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2145 | T | 2145 | T | 2145 | T | 2145 | T | 2145 | T | 2145 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NT | T1_H | NT952T1 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 901 | T | 901 | T | 901 | T | 901 | T | 901 | T | 901 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
NT | T2_H | NT982T2 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 892 | T | 892 | T | 892 | T | 892 | T | 892 | T | 892 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
PIC | T1_L | PIC705T1 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 962 | T | 962 | T | 962 | T | 962 | T | 962 | T | 962 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
PIC | T2_L | PIC710T2 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 962 | T | 962 | T | 962 | T | 962 | T | 962 | T | 962 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
PIC | T1_H | PIC805T1 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 503 | T | 503 | T | 503 | T | 503 | T | 503 | T | 503 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
PIC | T2_H | PIC809T2 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 503 | T | 503 | T | 503 | T | 503 | T | 503 | T | 503 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
SF | T4_L | SF703T4 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
SF | T3_L | SF709T3 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
SF | T5_L | SF712T5 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 845 | T | 845 | T | 845 | T | 845 | T | 845 | T | 845 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
SF | T3_H | SF822T3 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
SF | T4_H | SF832T4 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
SF | T5_H | SF895T5 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 442 | T | 442 | T | 442 | T | 442 | T | 442 | T | 442 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
ST | T1_L | ST842T1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2224 | T | 2224 | T | 2224 | T | 2224 | T | 2224 | T | 2224 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
ST | T2_L | ST862T2 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2143 | T | 2143 | T | 2143 | T | 2143 | T | 2143 | T | 2143 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
ST | T3_L | ST892T3 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | Static
ST | T1_H | ST934T1 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 923 | C | 923 | C | 923 | C | 923 | C | 923 | C | 923 | C | RLY Thermal Limit | 28/03/2023 | N039716 | Static
ST | T2_H | ST954T2 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 857 | T | 857 | T | 857 | T | 857 | T | 857 | T | 857 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
ST | T3_H | ST964T3 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 892 | T | 892 | T | 892 | T | 892 | T | 892 | T | 892 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
TST | T1_L | TST841T1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2231 | T | 2231 | T | 2231 | T | 2231 | T | 2231 | T | 2231 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
TST | T1_H | TST944T1 HV | RCM | AMP | TRANS | Y | 330 | 15 | RCM | AMP | 901 | T | 901 | T | 901 | T | 901 | T | 901 | T | 901 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WKT | T1_L | WKT807T1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 639 | T | 639 | T | 639 | T | 639 | T | 639 | T | 639 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WKT | T2_L | WKT810T2 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 639 | T | 639 | T | 639 | T | 639 | T | 639 | T | 639 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WKT | T17_L | WKT820T17 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 1282 | T | 1282 | T | 1282 | T | 1282 | T | 1282 | T | 1282 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WKT | T1_H | WKTX22T1 HV | RCM | AMP | TRANS | Y | 220 | 15 | RCM | AMP | 383 | T | 383 | T | 383 | T | 383 | T | 383 | T | 383 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WKT | T2_H | WKTX32T2 HV | RCM | AMP | TRANS | Y | 220 | 15 | RCM | AMP | 383 | T | 383 | T | 383 | T | 383 | T | 383 | T | 383 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WLT | T1_L | WLT801T1 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2056 | C | 2056 | C | 2056 | C | 2056 | C | 2056 | C | 2056 | C | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WLT | T2_L | WLT806T2 LV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 2056 | C | 2056 | C | 2056 | C | 2056 | C | 2056 | C | 2056 | C | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WT | T1_L | WT705T1 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WT | T2_L | WT708T2 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | 1021 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WT | T3_L | WT711T3 LV | RCM | AMP | TRANS | Y | 66 | 15 | RCM | AMP | 862 | T | 862 | T | 862 | T | 862 | T | 862 | T | 862 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WT | T1_H | WT822T1 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WT | T2_H | WT842T2 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | 534 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static
WT | T3_H | WT852T3 HV | RCM | AMP | TRANS | Y | 132 | 15 | RCM | AMP | 451 | T | 451 | T | 451 | T | 451 | T | 451 | T | 451 | T | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | Static

## Lines check (hidden)
Check | Line Description | # Connections | ALTLIMIT Time | Rating Unit | Equip. Type | Active Limits Y/N | 1 pu KV | LDSH Time | ALTLIMIT Time | Rating Unit | NORM IN | R | EMER IN | R | LDSH IN | R | NORM OUT | R | EMER OUT | R | LDSH OUT | R | Comments | Revision Date | User Name | Error Flag | Error Reason
FALSE | A 801 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | NT 833 A81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | A 809 OP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | OP 802 A81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | AFM 801 RO/WM81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RO 809 AFM/WM81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WM 806 RO/AFM81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 812 AKW81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 225 | P | 225 | P | 225 | P | 225 | P | 225 | P | 225 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | ALB 810 KOJ81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | KOJ 802 ALB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | 280 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | ALB 804 MBR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 230 | C | 230 | C | 230 | C | 230 | C | 230 | C | 230 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MBR 802 ALB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 230 | C | 230 | C | 230 | C | 230 | C | 230 | C | 230 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | AMT 801 CTE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CTE 811 AMT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | AMT 808 SF81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1070 | L | 1070 | L | 1070 | L | 1070 | L | 1070 | L | 1070 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SF 814 AMT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1070 | L | 1070 | L | 1070 | L | 1070 | L | 1070 | L | 1070 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | APJ OLY91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | OLY 903 APJ91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | APJ 810 PNJ81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PNJ 801 APJ81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | APJ 804 SNR/WGP81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 528 | L | 528 | L | 528 | L | 528 | L | 528 | L | 528 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SNR 801 APJ/WGP81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 528 | L | 528 | L | 528 | L | 528 | L | 528 | L | 528 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | APM 708 MYR71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MYR 701 APM71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | APM 701 SF71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BCH 808 H81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | H 807 BCH81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BCH 802 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 830 BCH81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BCT 808 NB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NB 809 BCT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BCT 801 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 812 BCT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
TRUE | KEL 701 BDE/MER71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
TRUE | MER 706 BDE/KEL71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BDP E01 KEM81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 572 | L | 572 | L | 572 | L | 572 | L | 572 | L | 572 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KEM 834 BDP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 572 | L | 572 | L | 572 | L | 572 | L | 572 | L | 572 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 802 BEC81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 211 | P | 211 | P | 211 | P | 211 | P | 211 | P | 211 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | BEL 809 EP/NT81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EP 834 BEL/NT81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 816 BEL/EP81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BEL 801 KDL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KDL 807 BEL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BEL 810 RVE/WE81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RVE 808 WE/BEL81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WE 802 RVE/BEL81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BGA 802 CTB/EMD81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CTB 806 EMD/BGA81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EMD 802 CTB/BGA81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BGA 801 ENB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ENB 804 BGA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BOD 810 BGM81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 900 | P | 900 | P | 900 | P | 900 | P | 900 | P | 900 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | BHK 701 KW/BP71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 55 | O | 55 | O | 55 | O | 55 | O | 55 | O | 55 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | BP 705 KW/BHK71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 722 BHK/BP71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BIB 807 KW81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 864 BIB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BIB 802 SF81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SF 844 BIB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WKT 812 BKF81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 292 | C | 292 | C | 292 | C | 292 | C | 292 | C | 292 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | BLD 812 PCY/PKS81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PCY 801 PKS/BLD81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PKS 801 SUT1 HV CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 373 | T | 373 | T | 373 | T | 373 | T | 373 | T | 373 | T | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | BLD 808 WKT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WKT 805 BLD81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BLD 802 WMS81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 355 | C | 355 | C | 355 | C | 355 | C | 355 | C | 355 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | WMS 805 BLD81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 355 | C | 355 | C | 355 | C | 355 | C | 355 | C | 355 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | BLW 903 BWP 91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | BLW 907 BWP92 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | BLW 901 MU91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 954 BLW91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BLW 905 SHO91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SHO 924 BLW91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MJP 801 BNP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | BNY 801 KDN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | KDN 801 BNY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | 111 | T | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | BOD 807 WLT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WLT 807 BOD81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BOD 802 WLT82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WLT 802 BOD82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 752 BP72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MRR 811 BSI81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 382 | P | 382 | P | 382 | P | 382 | P | 382 | P | 382 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | CAP 709 BSN71 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CAP 701 BSN72 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 374 | L | 374 | L | 374 | L | 374 | L | 374 | L | 374 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KEM 844 BSN/PIC/PNJ81 CURRENT | 4 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BSN 702 MR71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BSN 809 PNJ/PIC/KEM81 CURRENT | 4 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PIC 803 BSN/PNJ/KEM81 CURRENT | 4 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PNJ 804 PIC/BSN/KEM81 CURRENT | 4 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BTN 802 MU/MJP81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MJP 802 MU/BTN81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 814 MJP/BTN81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BTN 807 MU/MJP82 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MJP 809 MU/BTN82 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 813 MJP/BTN82 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | 259 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BTY 809 EP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1064 | L | 1064 | L | 1064 | L | 1064 | L | 1064 | L | 1064 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EP 812 BTY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1064 | L | 1064 | L | 1064 | L | 1064 | L | 1064 | L | 1064 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BTY 801 ST81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 864 BTY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BUH 802 MU81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 703 | L | 703 | L | 703 | L | 703 | L | 703 | L | 703 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 815 BUH81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 703 | L | 703 | L | 703 | L | 703 | L | 703 | L | 703 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BUH 809 PIC81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PIC 811 BUH81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BYF 801 CC81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CC 801 BYF81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | BYF 808 SNR/ST81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SNR 802 BYF/ST81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 812 BYF/SNR81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CAP 727 PIC/WSD71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PIC 704 CAP/WSD71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | PIC 712 CAP72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MER 702 YER/CAR/SX71 CURRENT | 4 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 193 | P | 193 | P | 193 | P | 193 | P | 193 | P | 193 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | MSR 810 CBP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 270 | P | 270 | P | 270 | P | 270 | P | 270 | P | 270 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
#N/A | CC 807 CCL81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 199 | L | 199 | L | 199 | L | 199 | L | 199 | L | 199 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CC 802 KW/MED81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 844 CC/MED81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MED 801 KW/CC81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CC 809 ST81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 8114 CC81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CGT X03 MRT X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MRT X15 CGT X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | CGT X05 WKT/YLN X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 980 | I | 980 | I | 980 | I | 980 | I | 980 | I | 980 | I | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | YLN X03 CGT X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | CK 803 EP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1225 | L | 1225 | L | 1225 | L | 1225 | L | 1225 | L | 1225 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EP 844 CK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1225 | L | 1225 | L | 1225 | L | 1225 | L | 1225 | L | 1225 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CK 806 NP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NP 807 CK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CK 810 WT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WT 844 CK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 862 CKB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1019 | L | 1019 | L | 1019 | L | 1019 | L | 1019 | L | 1019 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 854 CKB82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 540 | L | 540 | L | 540 | L | 540 | L | 540 | L | 540 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CKN 802 NOW81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 200 | P | 200 | P | 200 | P | 200 | P | 200 | P | 200 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | CKN 801 WNO81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WNO 808 CKN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CKN 809 YP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | YP 810 CKN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CL 710 COL71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
#N/A | COL 703 CL71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | CL 701 VP71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | 809 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | VP 708 CL71 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 738 | P | 738 | P | 738 | P | 738 | P | 738 | P | 738 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | PIC 702 CLP71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 202 | P | 202 | P | 202 | P | 202 | P | 202 | P | 202 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | CO 709 MU71 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MU 708 CO71 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | CO 701 MU72 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 287 | L | 287 | L | 287 | L | 287 | L | 287 | L | 287 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 710 CO72 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 245 | O | 245 | O | 245 | O | 245 | O | 245 | O | 245 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | CT 704 COL71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 880 | D | 880 | D | 880 | D | 880 | D | 880 | D | 880 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | CPN 805 GTN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | GTN 801 CPN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | CPN 808 RAN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RAN 802 CPN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SHO 932 CPS91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | 1830 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 819 KDL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KDL 802 CT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 821 KNL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 2877 | L | 2877 | L | 2877 | L | 2877 | L | 2877 | L | 2877 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KNL 801 CT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 2877 | L | 2877 | L | 2877 | L | 2877 | L | 2877 | L | 2877 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 817 MDN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MDN 809 CT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 812 MSS/PNJ81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MSS 802 CT/PNJ81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PNJ 809 CT/MSS81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 716 MW71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 370 | L | 370 | L | 370 | L | 370 | L | 370 | L | 370 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 805 RTN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RTN 807 CT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 801 RVE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RVE 801 CT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 803 ST81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | ST 874 CT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | 1180 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | CT 713 TT/VP72 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | TT 701 CT/VP72 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | VP 701 CT/TT72 CURRENT. | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CT 717 VP71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
#N/A | VP 712 CT71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0 | SCADA Point Name VP 711 CT71 CURRENT is not available in AEMO-WP Rating Format table
FALSE | CT 820 WE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WE 808 CT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CTB 811 ENB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | ENB 810 CTB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | CTB 810 KMC81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 127 | P | 127 | P | 127 | P | 127 | P | 127 | P | 127 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | CTB 803 PJR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PJR 812 CTB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | 861 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CTB 809 RGN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RGN 808 CTB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 595 | O | 595 | O | 595 | O | 595 | O | 595 | O | 595 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | CTE 801 WT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WT 824 CTE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CUN 701 KEL71 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 135 | P | 135 | P | 135 | P | 135 | P | 135 | P | 135 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | CUN 709 NOR71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 324 | L | 324 | L | 324 | L | 324 | L | 324 | L | 324 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NOR 701 CUN71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 202 | P | 202 | P | 202 | P | 202 | P | 202 | P | 202 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | CVE 808 G81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | G 806 CVE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | CVE 801 WLN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WLN 802 CVE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | D 809 K81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | K 810 D81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | D 801 MJ81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MJ 802 D81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | D 807 SVY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SVY 809 D81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
#N/A | E 712 SF71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
#N/A | SF 702 E71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
#N/A | E 704 SF72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 615 | L | 615 | L | 615 | L | 615 | L | 615 | L | 615 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
#N/A | SF 705 E72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 615 | L | 615 | L | 615 | L | 615 | L | 615 | L | 615 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EMD 801 PJR/ENB81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ENB 802 PJR/EMD81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PJR 814 ENB/EMD81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | 454 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ENB 801 TS81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | TS 804 ENB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | 580 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | ENT 932 TST91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | TST 942 ENT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | ENT 944 WDW91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | ENT 934 YDT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | YDT 932 ENT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
#N/A | EP 708 F71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 378 | P | 378 | P | 378 | P | 378 | P | 378 | P | 378 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
#N/A | EP 714 F72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 378 | P | 378 | P | 378 | P | 378 | P | 378 | P | 378 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | EP 814 HAY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | L | 480 | L | 480 | L | 480 | L | 480 | L | 480 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | HAY 808 EP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | L | 480 | L | 480 | L | 480 | L | 480 | L | 480 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EP 824 HAY82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 488 | L | 488 | L | 488 | L | 488 | L | 488 | L | 488 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | HAY 801 EP82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 488 | L | 488 | L | 488 | L | 488 | L | 488 | L | 488 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EP 854 JTE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 355 | T | 355 | T | 355 | T | 355 | T | 355 | T | 355 | T | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | EP 829 JTE82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 242 | T | 242 | T | 242 | T | 242 | T | 242 | T | 242 | T | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | EP 852 NP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1010 | L | 1010 | L | 1010 | L | 1010 | L | 1010 | L | 1010 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NP 804 EP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1010 | L | 1010 | L | 1010 | L | 1010 | L | 1010 | L | 1010 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EP 822 ST82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 844 EP82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EP 839A SUM81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 180 | P | 180 | P | 180 | P | 180 | P | 180 | P | 180 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | EP 809B SUM82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 180 | P | 180 | P | 180 | P | 180 | P | 180 | P | 180 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | EP 704 W71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 257 | L | 257 | L | 257 | L | 257 | L | 257 | L | 257 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | EP 712 W72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 260 | L | 260 | L | 260 | L | 260 | L | 260 | L | 260 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | FFD 808 GLT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | GLT 805 FFD81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | FFD 802 MDY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MDY 801 FFD81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | FFD 801 MVE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 90% TPES POL | 28/03/2023 | N039716 | 0 | SCADA Point Name FFD 801 MVE81 CURRENT is not available in AEMO-WP Rating Format table
FALSE | G 808 MDN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MDN 801 G81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | G 801 SNR81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SNR 808 G81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | TS 801 GGV81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 123 | P | 123 | P | 123 | P | 123 | P | 123 | P | 123 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | GLT 808 HZM81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | HZM 807 GLT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | GLT 802 MJ81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MJ 810 GLT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | GLT 801 MJ82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1175 | L | 1175 | L | 1175 | L | 1175 | L | 1175 | L | 1175 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MJ 801 GLT82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1175 | L | 1175 | L | 1175 | L | 1175 | L | 1175 | L | 1175 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | GLT 809 NT82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1213 | L | 1213 | L | 1213 | L | 1213 | L | 1213 | L | 1213 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 838 GLT82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1213 | L | 1213 | L | 1213 | L | 1213 | L | 1213 | L | 1213 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | GLT 952 NT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | NT 964 GLT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | GLT 944 ST91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | ST 972 GLT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | GLT 804 WLT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WLT 805 GLT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 8104 GNI81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 204 | P | 204 | P | 204 | P | 204 | P | 204 | P | 204 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | ST 8112 GNI82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 204 | P | 204 | P | 204 | P | 204 | P | 204 | P | 204 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | NBT 944 GNN91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | GTN 803 MGA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MGA 842 GTN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | GTN 810 RAN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RAN 809 GTN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | 831 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | GTN 809 WWF81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WWF 802 GTN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | H 801 MO81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
#N/A | MO 801 H81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | 690 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0 | SCADA Point Name MO 801 H81 CURRENT is not available in AEMO-WP Rating Format table
TRUE | HAY 804 MIL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1100 | L | 1100 | L | 1100 | L | 1100 | L | 1100 | L | 1100 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 1 | SCADA Point Name is not available in SALM Register for the line HAY-MIL81 at line end HAY
FALSE | MIL 804 HAY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 1 | SCADA Point Name MIL 804 HAY81 CURRENT is not available in AEMO-WP Rating Format table
FALSE | HBK 807 MUC81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MUC 804 HBK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | HBK 802 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 831 HBK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | HZM 802 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 805 HZM81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | JDP 809 MUL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MUL 813 JDP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | JDP 801 WNO81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WNO 802 JDP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | K 801 MDY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 593 | L | 593 | L | 593 | L | 593 | L | 593 | L | 593 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MDY 809 K81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 593 | L | 593 | L | 593 | L | 593 | L | 593 | L | 593 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KAT 702 KOJ71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | KOJ 711 KAT71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KAT 710 WAG71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
#N/A | WAG 704 KAT71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | KDN X35 MRT X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | MRT X35 KDN X1 CURRENT. | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 815 | O | 815 | O | 815 | O | 815 | O | 815 | O | 815 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | KDN X31 MU/NGS X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | NGS X31 KDN X1 CURRENT. | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 878 | O | 878 | O | 878 | O | 878 | O | 878 | O | 878 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
TRUE | KDP 801 KW/MSR81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 814 KDP/MSR81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MSR 826 KW/KDP81 CURRENT. | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | 749 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KEM 964 KMP91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | KMP KEM91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | KEM 962 KW/OLY91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 934 KEM/OLY91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | OLY 905 KEM/KW91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KEM 952 SHO/LWT91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | LWT 922.0 SHO/KEM91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SHO 934 KEM/LWT91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KEM 824 MRR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MRR 801 KEM81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KEM 814 MRR82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MRR 807 KEM82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | 788 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KEM 932 MU91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 944 KEM91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KMK 806 MSR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | MSR 813 KMK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 247 | P | 247 | P | 247 | P | 247 | P | 247 | P | 247 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | MUC 803 KMM81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 90 | P | 90 | P | 90 | P | 90 | P | 90 | P | 90 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | KND 801 MSR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MSR 828 KND81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | 980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | KNL 901 ST91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | ST 924 KNL91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | KOJ 812 MBR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | 307 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | MBR 805 KOJ81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | 395 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | KOJ 801 MU81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 350 | L | 350 | L | 350 | L | 350 | L | 350 | L | 350 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 812 KOJ81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 350 | L | 350 | L | 350 | L | 350 | L | 350 | L | 350 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KOJ 807 MU82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 809 KOJ82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KOJ 702 WAG71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 167 | L | 167 | L | 167 | L | 167 | L | 167 | L | 167 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WAG 710 KOJ71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 167 | L | 167 | L | 167 | L | 167 | L | 167 | L | 167 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MSR 816 KPP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MSR 822 KPP82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | 380 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | KRA 901 TST91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | TST 934 KRA91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | KW 824 MSR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MSR 817 KW81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 942 NGK91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 675 | L | 675 | L | 675 | L | 675 | L | 675 | L | 675 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 944 NT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | NT 984 KW91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | KW 894 SF82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SF 834 KW82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
TRUE | KW 834 ST81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1787 | L | 1787 | L | 1787 | L | 1787 | L | 1787 | L | 1787 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
TRUE | ST 832 KW81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1787 | L | 1787 | L | 1787 | L | 1787 | L | 1787 | L | 1787 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | KW 954 ST91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | ST 952 KW91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | KW 964 ST92 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | ST 922 KW92 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | 1980 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | LDE 808 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 835 LDE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | LDE 802 WGA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WGA 801 LDE81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
TRUE | LTH 802 MSR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 715 | L | 715 | L | 715 | L | 715 | L | 715 | L | 715 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 1 | SCADA Point Name LTH 802 MSR81 CURRENT is not available in AEMO-WP Rating Format table
TRUE | MSR 825 LTH81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 715 | L | 715 | L | 715 | L | 715 | L | 715 | L | 715 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 1 | SCADA Point Name MSR 825 LTH81 CURRENT is not available in AEMO-WP Rating Format table
FALSE | LTH 805 TLA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0 | SCADA Point Name LTH 805 TLA81 CURRENT is not available in AEMO-WP Rating Format table
FALSE | TLA 804 LTH81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0 | SCADA Point Name TLA 804 LTH81 CURRENT is not available in AEMO-WP Rating Format table
FALSE | LWT 942.0 ST91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 2015 | L | 2015 | L | 2015 | L | 2015 | L | 2015 | L | 2015 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 962 LWT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 2015 | L | 2015 | L | 2015 | L | 2015 | L | 2015 | L | 2015 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MA 801 NB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NB 802 MA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MA 807 OP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | OP 801 MA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MBA 802 MGA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MGA 834 MBA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MBA 806 TS81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | TS 807 MBA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MCE 701 N71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | N 706 MCE71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MCE 709 WT71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | WT 712 MCE71 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | MDP 801 MRT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1230 | D | 1230 | D | 1230 | D | 1230 | D | 1230 | D | 1230 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MRT 807 MDP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1230 | D | 1230 | D | 1230 | D | 1230 | D | 1230 | D | 1230 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MED 809 RO81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RO 801 MED81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MRT 801 MER81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 512 | L | 512 | L | 512 | L | 512 | L | 512 | L | 512 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
#N/A | MER 800 MRT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 512 | L | 512 | L | 512 | L | 512 | L | 512 | L | 512 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0 | SCADA Point Name is not available in SALM Register for the line MER-MRT81 at line end MER
FALSE | MGA 844 TS81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | TS 808 MGA81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MGA 824 WWF81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | WWF 806 MGA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | 638 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MH 809 MSS/WAI81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MSS 805 MH/WAI81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WAI 809 MH/MSS81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MH 802 PNJ81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 680 | L | 680 | L | 680 | L | 680 | L | 680 | L | 680 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PNJ 806 MH81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 680 | L | 680 | L | 680 | L | 680 | L | 680 | L | 680 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MIL 808 MLA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MLA 803 MIL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | 780 | D | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MIL 801 MLA82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MLA 806 MIL82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MLA 807 MO81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
#N/A | MO 812 MLA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MLA 802 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 811 MLA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MLA 805 NT82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 813 MLA82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MLA 801 Y81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MOR 801 MUC81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MUC 801 MOR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MOR 806 TS81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | TS 802 MOR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | 410 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MRR 810 MRR PIC 81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PIC 806 MRR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MRT X44 MRS X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 1245 | O | 1245 | O | 1245 | O | 1245 | O | 1245 | O | 1245 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | MRT 803 NOR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | RLY Thermal Limit | 28/03/2023 | N039716 | 0
FALSE | NOR 802 MRT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | 441 | C | RLY Thermal Limit | 28/03/2023 | N039716 | 0
FALSE | WM 803 MSR/OFE81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MSR 814 WM/OFE81 CURRENT | 3 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0 | SCADA Point Name MSR 814 WM/OFE81 CURRENT is not available in AEMO-WP Rating Format table
FALSE | MSS 801 PLD81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 590 | U | 590 | U | 590 | U | 590 | U | 590 | U | 590 | U | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MSS 808 PLD82 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 610 | L | 610 | L | 610 | L | 610 | L | 610 | L | 610 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU X24 NGS/KDN X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | NGS X15 KDN/MU X1 CURRENT. | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | 580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MU 924 NT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 994 MU91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | 1687 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MU 817 WCL81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WCL 805 MU81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | 647 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MUC 807 PJR81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PJR 834 MUC81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MUC 809 PJR82 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | PJR 824 MUC82 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | MUL 802 PBY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PBY 807 MUL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MUL 801 WGA81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WGA 809 MUL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MUR 809 RTN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RTN 801 MUR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MUR 802 ST81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 822 MUR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WUN 701 MW71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | 251 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | MYR 708 OC71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | OC 704 MYR71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | 745 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | N 701 WT71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | 908 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WT 709 N71 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 675 | P | 675 | P | 675 | P | 675 | P | 675 | P | 675 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | N 709 WT72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WT 706 N72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NB 801 PBY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PBY 802 NB81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NBT 972 NT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | NT 962 NBT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | NBT 864 PJR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PJR 884 NBT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NBT 874 WNO81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WNO 810 NBT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | 1412 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NBT 962 YDT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | YDT 934 NBT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | NGN 702 NGS/WAG71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 315 | O | 315 | O | 315 | O | 315 | O | 315 | O | 315 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | NGS 703 NGN/WAG71 CURRENT | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | WAG 713 NGN/NGS71 CURRENT. | 3 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 225 | P | 225 | P | 225 | P | 225 | P | 225 | P | 225 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | NGS 701 NGN71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | 220 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | NOR 811 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 441 | L | 441 | L | 441 | L | 441 | L | 441 | L | 441 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NT 803 NOR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 441 | L | 441 | L | 441 | L | 441 | L | 441 | L | 441 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NOR 807 SVY81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SVY 802 NOR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | 607 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NOR 710 WUN71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 287 | L | 287 | L | 287 | L | 287 | L | 287 | L | 287 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | NP 801 SRD81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 171 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
#N/A | SRD 813 NP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 250 | L | 250 | L | 250 | L | 250 | L | 250 | L | 250 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 1 | SCADA Point Name is not available in SALM Register for the line NP-SRD81 at line end SRD
FALSE | NT 802 PJR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1580 | C | 1580 | C | 1580 | C | 1580 | C | 1580 | C | 1580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | PJR 844 NT81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1580 | C | 1580 | C | 1580 | C | 1580 | C | 1580 | C | 1580 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | NT 804 SPK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SPK 808 NT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | OC 702 SF71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 700 | C | 700 | C | 700 | C | 700 | C | 700 | C | 700 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | SF 704 OC71 CURRENT. | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 700 | C | 700 | C | 700 | C | 700 | C | 700 | C | 700 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | OC 712 SF72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 712 | L | 712 | L | 712 | L | 712 | L | 712 | L | 712 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | OLY 901 SHO/ST91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SHO 944 OLY/ST91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 932 OLY/SHO91 CURRENT | 3 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | 1740 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | OP 809 Y81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | Y 810 OP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PCY 807 WKT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WKT 811 PCY81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | 614 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PIC 808 WOR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 995 | L | 995 | L | 995 | L | 995 | L | 995 | L | 995 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WOR 806 PIC81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 995 | L | 995 | L | 995 | L | 995 | L | 995 | L | 995 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PJR 822 RGN81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RGN 802 PJR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | 415 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | PJR 864 YP81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | YP 801 PJR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | RO 802 WAI81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 801 | L | 801 | L | 801 | L | 801 | L | 801 | L | 801 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WAI 801 RO81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 801 | L | 801 | L | 801 | L | 801 | L | 801 | L | 801 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SF 824 ST81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1215 | L | 1215 | L | 1215 | L | 1215 | L | 1215 | L | 1215 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 834 SF81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1215 | L | 1215 | L | 1215 | L | 1215 | L | 1215 | L | 1215 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SHO 942 WLT91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 2034 | L | 2034 | L | 2034 | L | 2034 | L | 2034 | L | 2034 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WLT 901 SHO91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 2034 | L | 2034 | L | 2034 | L | 2034 | L | 2034 | L | 2034 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SPK 805 WT81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WT 854 SPK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | ST 894 WLN81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WLN 809 ST81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | 1053 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | SX 709 YER/CAR/MER71 CURRENT. | 4 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 352 | L | 352 | L | 352 | L | 352 | L | 352 | L | 352 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | TS 820 TST81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 678 | L | 678 | L | 678 | L | 678 | L | 678 | L | 678 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | TST 841 TS81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 678 | L | 678 | L | 678 | L | 678 | L | 678 | L | 678 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WCL 801 WOR81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WOR 801 WCL81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | 741 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WD 709 WT71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WT 703 WD71 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | 894 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WD 701 WT72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WT 713 WD72 CURRENT | 2 | 41 | AMP | LINE | Y | 66 | 15 | 41 | AMP | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | 683 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WGP 808 WOR81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WOR 809 WGP81 CURRENT. | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 796 | L | 796 | L | 796 |  | 796 | L | 796 | L | 796 | L | AmpTx 41 Degree Rating | 28/03/2023 | N039716 | 0
FALSE | WKT X42 CGT/YLN X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 442 | P | 442 | P | 442 | P | 442 | P | 442 | P | 442 | P | 90% TPES POL | 28/03/2023 | N039716 | 0
FALSE | YLN X05 WKT X1 CURRENT | 2 | 41 | AMP | LINE | Y | 220 | 15 | 41 | AMP | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | 620 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0
FALSE | WMS 801 WMK81 CURRENT | 2 | 41 | AMP | LINE | Y | 132 | 15 | 41 | AMP | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | 480 | C | Hard Limit: AmpTx minus 20A | 28/03/2023 | N039716 | 0
FALSE | YDT 944 YDW91 CURRENT | 2 | 41 | AMP | LINE | Y | 330 | 15 | 41 | AMP | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | 1995 | O | Reasonability Limit minus 5A | 28/03/2023 | N039716 | 0

## Change Log
Date | Update By | Update Description
2023-03-30 | N039716 | A 801 NT81 CURRENT no change in rating
2023-03-30 | N039716 | NT 833 A81 CURRENT no change in rating
2023-03-30 | N039716 | A 809 OP81 CURRENT no change in rating
2023-03-30 | N039716 | OP 802 A81 CURRENT no change in rating
2023-03-30 | N039716 | AFM 801 RO/WM81 CURRENT no change in rating
2023-03-30 | N039716 | RO 809 AFM/WM81 CURRENT no change in rating
2023-03-30 | N039716 | WM 806 RO/AFM81 CURRENT no change in rating
2023-03-30 | N039716 | KW 812 AKW81 CURRENT. no change in rating
2023-03-30 | N039716 | ALB 810 KOJ81 CURRENT no change in rating
2023-03-30 | N039716 | KOJ 802 ALB81 CURRENT no change in rating
2023-03-30 | N039716 | ALB 804 MBR81 CURRENT no change in rating
2023-03-30 | N039716 | MBR 802 ALB81 CURRENT no change in rating
2023-03-30 | N039716 | AMT 801 CTE81 CURRENT no change in rating
2023-03-30 | N039716 | CTE 811 AMT81 CURRENT no change in rating
2023-03-30 | N039716 | AMT 808 SF81 CURRENT no change in rating
2023-03-30 | N039716 | SF 814 AMT81 CURRENT no change in rating
2023-03-30 | N039716 | APJ OLY91 CURRENT no change in rating
2023-03-30 | N039716 | OLY 903 APJ91 CURRENT no change in rating
2023-03-30 | N039716 | APJ 810 PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | PNJ 801 APJ81 CURRENT no change in rating
2023-03-30 | N039716 | APJ 804 SNR/WGP81 CURRENT no change in rating
2023-03-30 | N039716 | BEL 810 RVE/WE81 CURRENT no change in rating
2023-03-30 | N039716 | BGA 802 CTB/EMD81 CURRENT no change in rating
2023-03-30 | N039716 | CTB 806 EMD/BGA81 CURRENT no change in rating
2023-03-30 | N039716 | BP 705 KW/BHK71 CURRENT no change in rating
2023-03-30 | N039716 | KW 722 BHK/BP71 CURRENT no change in rating
2023-03-30 | N039716 | KEM 844 BSN/PIC/PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | PIC 803 BSN/PNJ/KEM81 CURRENT no change in rating
2023-03-30 | N039716 | PNJ 804 PIC/BSN/KEM81 CURRENT no change in rating
2023-03-30 | N039716 | BTN 802 MU/MJP81 CURRENT no change in rating
2023-03-30 | N039716 | BTN 807 MU/MJP82 CURRENT no change in rating
2023-03-30 | N039716 | MU 813 MJP/BTN82 CURRENT no change in rating
2023-03-30 | N039716 | SNR 802 BYF/ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 812 BYF/SNR81 CURRENT no change in rating
2023-03-30 | N039716 | PIC 704 CAP/WSD71 CURRENT no change in rating
2023-03-30 | N039716 | KW 844 CC/MED81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 802 CT/PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | PNJ 809 CT/MSS81 CURRENT no change in rating
2023-03-30 | N039716 | CT 713 TT/VP72 CURRENT no change in rating
2023-03-30 | N039716 | TT 701 CT/VP72 CURRENT no change in rating
2023-03-30 | N039716 | PJR 814 ENB/EMD81 CURRENT no change in rating
2023-03-30 | N039716 | KDP 801 KW/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | KW 814 KDP/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 826 KW/KDP81 CURRENT.no change in rating
2023-03-30 | N039716 | KW 934 KEM/OLY91 CURRENT no change in rating
2023-03-30 | N039716 | OLY 905 KEM/KW91 CURRENT no change in rating
2023-03-30 | N039716 | KND 801 MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 828 KND81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 816 KPP81 CURRENT no change in rating
2023-03-30 | N039716 | KW 834 ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 832 KW81 CURRENT no change in rating
2023-03-30 | N039716 | MDP 801 MRT81 CURRENT no change in rating
2023-03-30 | N039716 | MRT 807 MDP81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 805 MH/WAI81 CURRENT no change in rating
2023-03-30 | N039716 | MH 802 PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | OLY 901 SHO/ST91 CURRENT no change in rating
2023-03-30 | N039716 | SX 709 YER/CAR/MER71 CURRENT.no change in rating
2023-03-30 | N039716 | BIB 802 SF81 CURRENT no change in rating
2023-03-30 | N039716 | SF 844 BIB81 CURRENT no change in rating
2023-03-30 | N039716 | WKT 812 BKF81 CURRENT no change in rating
2023-03-30 | N039716 | BLD 812 PCY/PKS81 CURRENT no change in rating
2023-03-30 | N039716 | PCY 801 PKS/BLD81 CURRENT no change in rating
2023-03-30 | N039716 | PKS 801 SUT1 HV CURRENT no change in rating
2023-03-30 | N039716 | BLD 808 WKT81 CURRENT no change in rating
2023-03-30 | N039716 | WKT 805 BLD81 CURRENT. no change in rating
2023-03-30 | N039716 | BLD 802 WMS81 CURRENT no change in rating
2023-03-30 | N039716 | WMS 805 BLD81 CURRENT no change in rating
2023-03-30 | N039716 | BLW 903 BWP 91 CURRENT no change in rating
2023-03-30 | N039716 | BLW 907 BWP92 CURRENT no change in rating
2023-03-30 | N039716 | BLW 901 MU91 CURRENT no change in rating
2023-03-30 | N039716 | MU 954 BLW91 CURRENT no change in rating
2023-03-30 | N039716 | BLW 905 SHO91 CURRENT no change in rating
2023-03-30 | N039716 | SHO 924 BLW91 CURRENT no change in rating
2023-03-30 | N039716 | MJP 801 BNP81 CURRENT no change in rating
2023-03-30 | N039716 | BNY 801 KDN81 CURRENT no change in rating
2023-03-30 | N039716 | KDN 801 BNY81 CURRENT no change in rating
2023-03-30 | N039716 | BOD 807 WLT81 CURRENT no change in rating
2023-03-30 | N039716 | WLT 807 BOD81 CURRENT no change in rating
2023-03-30 | N039716 | BOD 802 WLT82 CURRENT no change in rating
2023-03-30 | N039716 | WLT 802 BOD82 CURRENT no change in rating
2023-03-30 | N039716 | KW 752 BP72 CURRENT no change in rating
2023-03-30 | N039716 | MRR 811 BSI81 CURRENT no change in rating
2023-03-30 | N039716 | CAP 709 BSN71 CURRENT. no change in rating
2023-03-30 | N039716 | CAP 701 BSN72 CURRENT. no change in rating
2023-03-30 | N039716 | KEM 844 BSN/PIC/PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | PIC 803 BSN/PNJ/KEM81 CURRENT no change in rating
2023-03-30 | N039716 | PNJ 804 PIC/BSN/KEM81 CURRENT no change in rating
2023-03-30 | N039716 | BTN 802 MU/MJP81 CURRENT no change in rating
2023-03-30 | N039716 | BTN 807 MU/MJP82 CURRENT no change in rating
2023-03-30 | N039716 | MU 813 MJP/BTN82 CURRENT no change in rating
2023-03-30 | N039716 | SNR 802 BYF/ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 812 BYF/SNR81 CURRENT no change in rating
2023-03-30 | N039716 | PIC 704 CAP/WSD71 CURRENT no change in rating
2023-03-30 | N039716 | KW 844 CC/MED81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 802 CT/PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | PNJ 809 CT/MSS81 CURRENT no change in rating
2023-03-30 | N039716 | CT 713 TT/VP72 CURRENT no change in rating
2023-03-30 | N039716 | TT 701 CT/VP72 CURRENT no change in rating
2023-03-30 | N039716 | PJR 814 ENB/EMD81 CURRENT no change in rating
2023-03-30 | N039716 | KDP 801 KW/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | KW 814 KDP/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 826 KW/KDP81 CURRENT.no change in rating
2023-03-30 | N039716 | KW 934 KEM/OLY91 CURRENT no change in rating
2023-03-30 | N039716 | OLY 905 KEM/KW91 CURRENT no change in rating
2023-03-30 | N039716 | KND 801 MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 828 KND81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 816 KPP81 CURRENT no change in rating
2023-03-30 | N039716 | KW 834 ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 832 KW81 CURRENT no change in rating
2023-03-30 | N039716 | MDP 801 MRT81 CURRENT no change in rating
2023-03-30 | N039716 | MRT 807 MDP81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 805 MH/WAI81 CURRENT no change in rating
2023-03-30 | N039716 | MH 802 PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | OLY 901 SHO/ST91 CURRENT no change in rating
2023-03-30 | N039716 | SX 709 YER/CAR/MER71 CURRENT.no change in rating
2023-03-30 | N039716 | KW 844 CC/MED81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 802 CT/PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | PNJ 809 CT/MSS81 CURRENT no change in rating
2023-03-30 | N039716 | CT 713 TT/VP72 CURRENT no change in rating
2023-03-30 | N039716 | TT 701 CT/VP72 CURRENT no change in rating
2023-03-30 | N039716 | PJR 814 ENB/EMD81 CURRENT no change in rating
2023-03-30 | N039716 | KDP 801 KW/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | KW 814 KDP/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 826 KW/KDP81 CURRENT.no change in rating
2023-03-30 | N039716 | KW 934 KEM/OLY91 CURRENT no change in rating
2023-03-30 | N039716 | OLY 905 KEM/KW91 CURRENT no change in rating
2023-03-30 | N039716 | KND 801 MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 828 KND81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 816 KPP81 CURRENT no change in rating
2023-03-30 | N039716 | KW 834 ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 832 KW81 CURRENT no change in rating
2023-03-30 | N039716 | MDP 801 MRT81 CURRENT no change in rating
2023-03-30 | N039716 | MRT 807 MDP81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 805 MH/WAI81 CURRENT no change in rating
2023-03-30 | N039716 | MH 802 PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | OLY 901 SHO/ST91 CURRENT no change in rating
2023-03-30 | N039716 | SX 709 YER/CAR/MER71 CURRENT.no change in rating
2023-03-30 | N039716 | COL 703 CL71 CURRENT circuit has been added
2023-03-30 | N039716 | CL 701 VP71 CURRENT no change in rating
2023-03-30 | N039716 | VP 708 CL71 CURRENT. no change in rating
2023-03-30 | N039716 | PIC 702 CLP71 CURRENT no change in rating
2023-03-30 | N039716 | CO 709 MU71 CURRENT. no change in rating
2023-03-30 | N039716 | MU 708 CO71 CURRENT. no change in rating
2023-03-30 | N039716 | CO 701 MU72 CURRENT. no change in rating
2023-03-30 | N039716 | MU 710 CO72 CURRENT. no change in rating
2023-03-30 | N039716 | CT 704 COL71 CURRENT no change in rating
2023-03-30 | N039716 | CPN 805 GTN81 CURRENT no change in rating
2023-03-30 | N039716 | GTN 801 CPN81 CURRENT no change in rating
2023-03-30 | N039716 | CPN 808 RAN81 CURRENT no change in rating
2023-03-30 | N039716 | RAN 802 CPN81 CURRENT no change in rating
2023-03-30 | N039716 | SHO 932 CPS91 CURRENT no change in rating
2023-03-30 | N039716 | CT 819 KDL81 CURRENT no change in rating
2023-03-30 | N039716 | KDL 802 CT81 CURRENT no change in rating
2023-03-30 | N039716 | CT 821 KNL81 CURRENT no change in rating
2023-03-30 | N039716 | KNL 801 CT81 CURRENT no change in rating
2023-03-30 | N039716 | CT 817 MDN81 CURRENT no change in rating
2023-03-30 | N039716 | MDN 809 CT81 CURRENT no change in rating
2023-03-30 | N039716 | CT 812 MSS/PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 802 CT/PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | PNJ 809 CT/MSS81 CURRENT no change in rating
2023-03-30 | N039716 | CT 713 TT/VP72 CURRENT no change in rating
2023-03-30 | N039716 | TT 701 CT/VP72 CURRENT no change in rating
2023-03-30 | N039716 | PJR 814 ENB/EMD81 CURRENT no change in rating
2023-03-30 | N039716 | KDP 801 KW/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | KW 814 KDP/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 826 KW/KDP81 CURRENT.no change in rating
2023-03-30 | N039716 | KW 934 KEM/OLY91 CURRENT no change in rating
2023-03-30 | N039716 | OLY 905 KEM/KW91 CURRENT no change in rating
2023-03-30 | N039716 | KND 801 MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 828 KND81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 816 KPP81 CURRENT no change in rating
2023-03-30 | N039716 | KW 834 ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 832 KW81 CURRENT no change in rating
2023-03-30 | N039716 | MDP 801 MRT81 CURRENT no change in rating
2023-03-30 | N039716 | MRT 807 MDP81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 805 MH/WAI81 CURRENT no change in rating
2023-03-30 | N039716 | MH 802 PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | OLY 901 SHO/ST91 CURRENT no change in rating
2023-03-30 | N039716 | SX 709 YER/CAR/MER71 CURRENT.no change in rating
2023-03-30 | N039716 | CTB 809 RGN81 CURRENT no change in rating
2023-03-30 | N039716 | RGN 808 CTB81 CURRENT no change in rating
2023-03-30 | N039716 | CTE 801 WT81 CURRENT no change in rating
2023-03-30 | N039716 | WT 824 CTE81 CURRENT no change in rating
2023-03-30 | N039716 | CUN 701 KEL71 CURRENT. no change in rating
2023-03-30 | N039716 | CUN 709 NOR71 CURRENT no change in rating
2023-03-30 | N039716 | NOR 701 CUN71 CURRENT no change in rating
2023-03-30 | N039716 | CVE 808 G81 CURRENT. no change in rating
2023-03-30 | N039716 | G 806 CVE81 CURRENT no change in rating
2023-03-30 | N039716 | CVE 801 WLN81 CURRENT no change in rating
2023-03-30 | N039716 | WLN 802 CVE81 CURRENT no change in rating
2023-03-30 | N039716 | D 809 K81 CURRENT no change in rating
2023-03-30 | N039716 | K 810 D81 CURRENT no change in rating
2023-03-30 | N039716 | D 801 MJ81 CURRENT no change in rating
2023-03-30 | N039716 | MJ 802 D81 CURRENT no change in rating
2023-03-30 | N039716 | D 807 SVY81 CURRENT no change in rating
2023-03-30 | N039716 | SVY 809 D81 CURRENT no change in rating
2023-03-30 | N039716 | E 712 SF71 CURRENT circuit has been added
2023-03-30 | N039716 | SF 702 E71 CURRENT circuit has been added
2023-03-30 | N039716 | E 704 SF72 CURRENT circuit has been added
2023-03-30 | N039716 | SF 705 E72 CURRENT circuit has been added
2023-03-30 | N039716 | EMD 801 PJR/ENB81 CURRENT no change in rating
2023-03-30 | N039716 | ENB 802 PJR/EMD81 CURRENT no change in rating
2023-03-30 | N039716 | PJR 814 ENB/EMD81 CURRENT no change in rating
2023-03-30 | N039716 | ENB 801 TS81 CURRENT no change in rating
2023-03-30 | N039716 | TS 804 ENB81 CURRENT no change in rating
2023-03-30 | N039716 | ENT 932 TST91 CURRENT no change in rating
2023-03-30 | N039716 | TST 942 ENT91 CURRENT no change in rating
2023-03-30 | N039716 | ENT 944 WDW91 CURRENT no change in rating
2023-03-30 | N039716 | ENT 934 YDT91 CURRENT no change in rating
2023-03-30 | N039716 | YDT 932 ENT91 CURRENT no change in rating
2023-03-30 | N039716 | EP 814 HAY81 CURRENT no change in rating
2023-03-30 | N039716 | HAY 808 EP81 CURRENT no change in rating
2023-03-30 | N039716 | EP 824 HAY82 CURRENT no change in rating
2023-03-30 | N039716 | HAY 801 EP82 CURRENT no change in rating
2023-03-30 | N039716 | EP 854 JTE81 CURRENT no change in rating
2023-03-30 | N039716 | EP 829 JTE82 CURRENT no change in rating
2023-03-30 | N039716 | EP 852 NP81 CURRENT no change in rating
2023-03-30 | N039716 | NP 804 EP81 CURRENT no change in rating
2023-03-30 | N039716 | EP 822 ST82 CURRENT no change in rating
2023-03-30 | N039716 | ST 844 EP82 CURRENT no change in rating
2023-03-30 | N039716 | EP 839A SUM81 CURRENT no change in rating
2023-03-30 | N039716 | EP 809B SUM82 CURRENT no change in rating
2023-03-30 | N039716 | EP 704 W71 CURRENT no change in rating
2023-03-30 | N039716 | EP 712 W72 CURRENT no change in rating
2023-03-30 | N039716 | FFD 808 GLT81 CURRENT no change in rating
2023-03-30 | N039716 | GLT 805 FFD81 CURRENT no change in rating
2023-03-30 | N039716 | FFD 802 MDY81 CURRENT no change in rating
2023-03-30 | N039716 | MDY 801 FFD81 CURRENT no change in rating
2023-03-30 | N039716 | FFD 801 MVE81 CURRENT no change in rating
2023-03-30 | N039716 | G 808 MDN81 CURRENT no change in rating
2023-03-30 | N039716 | MDN 801 G81 CURRENT no change in rating
2023-03-30 | N039716 | G 801 SNR81 CURRENT. no change in rating
2023-03-30 | N039716 | SNR 808 G81 CURRENT no change in rating
2023-03-30 | N039716 | TS 801 GGV81 CURRENT. no change in rating
2023-03-30 | N039716 | GLT 808 HZM81 CURRENT no change in rating
2023-03-30 | N039716 | HZM 807 GLT81 CURRENT no change in rating
2023-03-30 | N039716 | GLT 802 MJ81 CURRENT no change in rating
2023-03-30 | N039716 | MJ 810 GLT81 CURRENT no change in rating
2023-03-30 | N039716 | GLT 801 MJ82 CURRENT no change in rating
2023-03-30 | N039716 | MJ 801 GLT82 CURRENT no change in rating
2023-03-30 | N039716 | GLT 809 NT82 CURRENT no change in rating
2023-03-30 | N039716 | NT 838 GLT82 CURRENT no change in rating
2023-03-30 | N039716 | GLT 952 NT91 CURRENT no change in rating
2023-03-30 | N039716 | NT 964 GLT91 CURRENT no change in rating
2023-03-30 | N039716 | GLT 944 ST91 CURRENT no change in rating
2023-03-30 | N039716 | ST 972 GLT91 CURRENT no change in rating
2023-03-30 | N039716 | GLT 804 WLT81 CURRENT no change in rating
2023-03-30 | N039716 | WLT 805 GLT81 CURRENT no change in rating
2023-03-30 | N039716 | ST 8104 GNI81 CURRENT no change in rating
2023-03-30 | N039716 | ST 8112 GNI82 CURRENT no change in rating
2023-03-30 | N039716 | NBT 944 GNN91 CURRENT no change in rating
2023-03-30 | N039716 | GTN 803 MGA81 CURRENT no change in rating
2023-03-30 | N039716 | MGA 842 GTN81 CURRENT no change in rating
2023-03-30 | N039716 | GTN 810 RAN81 CURRENT no change in rating
2023-03-30 | N039716 | RAN 809 GTN81 CURRENT no change in rating
2023-03-30 | N039716 | GTN 809 WWF81 CURRENT no change in rating
2023-03-30 | N039716 | WWF 802 GTN81 CURRENT no change in rating
2023-03-30 | N039716 | H 801 MO81 CURRENT no change in rating
2023-03-30 | N039716 | MO 801 H81 CURRENT circuit has been added
2023-03-30 | N039716 | HAY 804 MIL81 CURRENT no change in rating
2023-03-30 | N039716 | MIL 804 HAY81 CURRENT no change in rating
2023-03-30 | N039716 | HBK 807 MUC81 CURRENT no change in rating
2023-03-30 | N039716 | MUC 804 HBK81 CURRENT no change in rating
2023-03-30 | N039716 | HBK 802 NT81 CURRENT no change in rating
2023-03-30 | N039716 | NT 831 HBK81 CURRENT no change in rating
2023-03-30 | N039716 | HZM 802 NT81 CURRENT no change in rating
2023-03-30 | N039716 | NT 805 HZM81 CURRENT no change in rating
2023-03-30 | N039716 | JDP 809 MUL81 CURRENT no change in rating
2023-03-30 | N039716 | MUL 813 JDP81 CURRENT no change in rating
2023-03-30 | N039716 | JDP 801 WNO81 CURRENT no change in rating
2023-03-30 | N039716 | WNO 802 JDP81 CURRENT no change in rating
2023-03-30 | N039716 | K 801 MDY81 CURRENT no change in rating
2023-03-30 | N039716 | MDY 809 K81 CURRENT no change in rating
2023-03-30 | N039716 | KAT 702 KOJ71 CURRENT no change in rating
2023-03-30 | N039716 | KOJ 711 KAT71 CURRENT no change in rating
2023-03-30 | N039716 | KAT 710 WAG71 CURRENT no change in rating
2023-03-30 | N039716 | WAG 704 KAT71 CURRENT circuit has been added
2023-03-30 | N039716 | KDN X35 MRT X1 CURRENT no change in rating
2023-03-30 | N039716 | MRT X35 KDN X1 CURRENT. no change in rating
2023-03-30 | N039716 | KDN X31 MU/NGS X1 CURRENT no change in rating
2023-03-30 | N039716 | NGS X31 KDN X1 CURRENT. no change in rating
2023-03-30 | N039716 | KDP 801 KW/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | KW 814 KDP/MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 826 KW/KDP81 CURRENT.no change in rating
2023-03-30 | N039716 | KEM 964 KMP91 CURRENT no change in rating
2023-03-30 | N039716 | KMP KEM91 CURRENT no change in rating
2023-03-30 | N039716 | KEM 962 KW/OLY91 CURRENT no change in rating
2023-03-30 | N039716 | KW 934 KEM/OLY91 CURRENT no change in rating
2023-03-30 | N039716 | OLY 905 KEM/KW91 CURRENT no change in rating
2023-03-30 | N039716 | KEM 952 SHO/LWT91 CURRENT no change in rating
2023-03-30 | N039716 | LWT 922.0 SHO/KEM91 CURRENT no change in rating
2023-03-30 | N039716 | SHO 934 KEM/LWT91 CURRENT no change in rating
2023-03-30 | N039716 | KEM 824 MRR81 CURRENT no change in rating
2023-03-30 | N039716 | MRR 801 KEM81 CURRENT no change in rating
2023-03-30 | N039716 | KEM 814 MRR82 CURRENT no change in rating
2023-03-30 | N039716 | MRR 807 KEM82 CURRENT no change in rating
2023-03-30 | N039716 | KEM 932 MU91 CURRENT no change in rating
2023-03-30 | N039716 | MU 944 KEM91 CURRENT no change in rating
2023-03-30 | N039716 | KMK 806 MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 813 KMK81 CURRENT no change in rating
2023-03-30 | N039716 | MUC 803 KMM81 CURRENT no change in rating
2023-03-30 | N039716 | KND 801 MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 828 KND81 CURRENT no change in rating
2023-03-30 | N039716 | KNL 901 ST91 CURRENT no change in rating
2023-03-30 | N039716 | ST 924 KNL91 CURRENT no change in rating
2023-03-30 | N039716 | KOJ 812 MBR81 CURRENT no change in rating
2023-03-30 | N039716 | MBR 805 KOJ81 CURRENT no change in rating
2023-03-30 | N039716 | KOJ 801 MU81 CURRENT no change in rating
2023-03-30 | N039716 | MU 812 KOJ81 CURRENT. no change in rating
2023-03-30 | N039716 | KOJ 807 MU82 CURRENT no change in rating
2023-03-30 | N039716 | MU 809 KOJ82 CURRENT no change in rating
2023-03-30 | N039716 | KOJ 702 WAG71 CURRENT no change in rating
2023-03-30 | N039716 | WAG 710 KOJ71 CURRENT no change in rating
2023-03-30 | N039716 | MSR 816 KPP81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 822 KPP82 CURRENT no change in rating
2023-03-30 | N039716 | KRA 901 TST91 CURRENT no change in rating
2023-03-30 | N039716 | TST 934 KRA91 CURRENT no change in rating
2023-03-30 | N039716 | KW 824 MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 817 KW81 CURRENT no change in rating
2023-03-30 | N039716 | KW 942 NGK91 CURRENT no change in rating
2023-03-30 | N039716 | KW 944 NT91 CURRENT no change in rating
2023-03-30 | N039716 | NT 984 KW91 CURRENT no change in rating
2023-03-30 | N039716 | KW 894 SF82 CURRENT no change in rating
2023-03-30 | N039716 | SF 834 KW82 CURRENT no change in rating
2023-03-30 | N039716 | KW 834 ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 832 KW81 CURRENT no change in rating
2023-03-30 | N039716 | KW 954 ST91 CURRENT no change in rating
2023-03-30 | N039716 | ST 952 KW91 CURRENT no change in rating
2023-03-30 | N039716 | KW 964 ST92 CURRENT no change in rating
2023-03-30 | N039716 | ST 922 KW92 CURRENT no change in rating
2023-03-30 | N039716 | LDE 808 NT81 CURRENT no change in rating
2023-03-30 | N039716 | NT 835 LDE81 CURRENT no change in rating
2023-03-30 | N039716 | LDE 802 WGA81 CURRENT no change in rating
2023-03-30 | N039716 | WGA 801 LDE81 CURRENT no change in rating
2023-03-30 | N039716 | LTH 802 MSR81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 825 LTH81 CURRENT no change in rating
2023-03-30 | N039716 | LTH 805 TLA81 CURRENT no change in rating
2023-03-30 | N039716 | TLA 804 LTH81 CURRENT no change in rating
2023-03-30 | N039716 | LWT 942.0 ST91 CURRENT no change in rating
2023-03-30 | N039716 | ST 962 LWT91 CURRENT no change in rating
2023-03-30 | N039716 | MA 801 NB81 CURRENT no change in rating
2023-03-30 | N039716 | NB 802 MA81 CURRENT no change in rating
2023-03-30 | N039716 | MA 807 OP81 CURRENT no change in rating
2023-03-30 | N039716 | OP 801 MA81 CURRENT no change in rating
2023-03-30 | N039716 | MBA 802 MGA81 CURRENT no change in rating
2023-03-30 | N039716 | MGA 834 MBA81 CURRENT no change in rating
2023-03-30 | N039716 | MBA 806 TS81 CURRENT no change in rating
2023-03-30 | N039716 | TS 807 MBA81 CURRENT no change in rating
2023-03-30 | N039716 | MCE 701 N71 CURRENT no change in rating
2023-03-30 | N039716 | N 706 MCE71 CURRENT no change in rating
2023-03-30 | N039716 | MCE 709 WT71 CURRENT no change in rating
2023-03-30 | N039716 | WT 712 MCE71 CURRENT. no change in rating
2023-03-30 | N039716 | KW 834 ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 832 KW81 CURRENT no change in rating
2023-03-30 | N039716 | MED 809 RO81 CURRENT no change in rating
2023-03-30 | N039716 | RO 801 MED81 CURRENT no change in rating
2023-03-30 | N039716 | MRT 801 MER81 CURRENT no change in rating
2023-03-30 | N039716 | MER 800 MRT81 CURRENT circuit has been added
2023-03-30 | N039716 | MGA 844 TS81 CURRENT no change in rating
2023-03-30 | N039716 | TS 808 MGA81 CURRENT. no change in rating
2023-03-30 | N039716 | MGA 824 WWF81 CURRENT no change in rating
2023-03-30 | N039716 | WWF 806 MGA81 CURRENT no change in rating
2023-03-30 | N039716 | MH 809 MSS/WAI81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 805 MH/WAI81 CURRENT no change in rating
2023-03-30 | N039716 | WAI 809 MH/MSS81 CURRENT no change in rating
2023-03-30 | N039716 | MH 802 PNJ81 CURRENT no change in rating
2023-03-30 | N039716 | PNJ 806 MH81 CURRENT no change in rating
2023-03-30 | N039716 | MIL 808 MLA81 CURRENT no change in rating
2023-03-30 | N039716 | MLA 803 MIL81 CURRENT no change in rating
2023-03-30 | N039716 | MIL 801 MLA82 CURRENT no change in rating
2023-03-30 | N039716 | MLA 806 MIL82 CURRENT no change in rating
2023-03-30 | N039716 | MLA 807 MO81 CURRENT no change in rating
2023-03-30 | N039716 | MO 812 MLA81 CURRENT circuit has been added
2023-03-30 | N039716 | MLA 802 NT81 CURRENT no change in rating
2023-03-30 | N039716 | NT 811 MLA81 CURRENT no change in rating
2023-03-30 | N039716 | MLA 805 NT82 CURRENT no change in rating
2023-03-30 | N039716 | NT 813 MLA82 CURRENT no change in rating
2023-03-30 | N039716 | MLA 801 Y81 CURRENT no change in rating
2023-03-30 | N039716 | MOR 801 MUC81 CURRENT no change in rating
2023-03-30 | N039716 | MUC 801 MOR81 CURRENT no change in rating
2023-03-30 | N039716 | MOR 806 TS81 CURRENT no change in rating
2023-03-30 | N039716 | TS 802 MOR81 CURRENT no change in rating
2023-03-30 | N039716 | MRR 810 MRR PIC 81 CURRENT no change in rating
2023-03-30 | N039716 | PIC 806 MRR81 CURRENT no change in rating
2023-03-30 | N039716 | MRT X44 MRS X1 CURRENT no change in rating
2023-03-30 | N039716 | MRT 803 NOR81 CURRENT no change in rating
2023-03-30 | N039716 | NOR 802 MRT81 CURRENT no change in rating
2023-03-30 | N039716 | WM 803 MSR/OFE81 CURRENT no change in rating
2023-03-30 | N039716 | MSR 814 WM/OFE81 CURRENT no change in rating
2023-03-30 | N039716 | MSS 801 PLD81 CURRENT decreased from 610 A to 590 A
2023-03-30 | N039716 | MSS 808 PLD82 CURRENT no change in rating
2023-03-30 | N039716 | MU X24 NGS/KDN X1 CURRENT no change in rating
2023-03-30 | N039716 | NGS X15 KDN/MU X1 CURRENT. no change in rating
2023-03-30 | N039716 | MU 924 NT91 CURRENT no change in rating
2023-03-30 | N039716 | NT 994 MU91 CURRENT no change in rating
2023-03-30 | N039716 | MU 817 WCL81 CURRENT. no change in rating
2023-03-30 | N039716 | WCL 805 MU81 CURRENT no change in rating
2023-03-30 | N039716 | MUC 807 PJR81 CURRENT. no change in rating
2023-03-30 | N039716 | PJR 834 MUC81 CURRENT no change in rating
2023-03-30 | N039716 | MUC 809 PJR82 CURRENT. no change in rating
2023-03-30 | N039716 | PJR 824 MUC82 CURRENT. no change in rating
2023-03-30 | N039716 | MUL 802 PBY81 CURRENT no change in rating
2023-03-30 | N039716 | PBY 807 MUL81 CURRENT no change in rating
2023-03-30 | N039716 | MUL 801 WGA81 CURRENT no change in rating
2023-03-30 | N039716 | WGA 809 MUL81 CURRENT no change in rating
2023-03-30 | N039716 | MUR 809 RTN81 CURRENT no change in rating
2023-03-30 | N039716 | RTN 801 MUR81 CURRENT no change in rating
2023-03-30 | N039716 | MUR 802 ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 822 MUR81 CURRENT no change in rating
2023-03-30 | N039716 | WUN 701 MW71 CURRENT no change in rating
2023-03-30 | N039716 | MYR 708 OC71 CURRENT no change in rating
2023-03-30 | N039716 | OC 704 MYR71 CURRENT no change in rating
2023-03-30 | N039716 | N 701 WT71 CURRENT no change in rating
2023-03-30 | N039716 | WT 709 N71 CURRENT. no change in rating
2023-03-30 | N039716 | N 709 WT72 CURRENT no change in rating
2023-03-30 | N039716 | WT 706 N72 CURRENT no change in rating
2023-03-30 | N039716 | NB 801 PBY81 CURRENT no change in rating
2023-03-30 | N039716 | PBY 802 NB81 CURRENT no change in rating
2023-03-30 | N039716 | NBT 972 NT91 CURRENT no change in rating
2023-03-30 | N039716 | NT 962 NBT91 CURRENT no change in rating
2023-03-30 | N039716 | NBT 864 PJR81 CURRENT no change in rating
2023-03-30 | N039716 | PJR 884 NBT81 CURRENT no change in rating
2023-03-30 | N039716 | NBT 874 WNO81 CURRENT no change in rating
2023-03-30 | N039716 | WNO 810 NBT81 CURRENT no change in rating
2023-03-30 | N039716 | NBT 962 YDT91 CURRENT no change in rating
2023-03-30 | N039716 | YDT 934 NBT91 CURRENT no change in rating
2023-03-30 | N039716 | NGN 702 NGS/WAG71 CURRENT no change in rating
2023-03-30 | N039716 | NGS 703 NGN/WAG71 CURRENT no change in rating
2023-03-30 | N039716 | WAG 713 NGN/NGS71 CURRENT. no change in rating
2023-03-30 | N039716 | NGS 701 NGN71 CURRENT no change in rating
2023-03-30 | N039716 | NOR 811 NT81 CURRENT no change in rating
2023-03-30 | N039716 | NT 803 NOR81 CURRENT no change in rating
2023-03-30 | N039716 | NOR 807 SVY81 CURRENT no change in rating
2023-03-30 | N039716 | SVY 802 NOR81 CURRENT no change in rating
2023-03-30 | N039716 | NOR 710 WUN71 CURRENT no change in rating
2023-03-30 | N039716 | NP 801 SRD81 CURRENT no change in rating
2023-03-30 | N039716 | NP 801 SRD81 CURRENT no change in rating
2023-03-30 | N039716 | NT 802 PJR81 CURRENT no change in rating
2023-03-30 | N039716 | PJR 844 NT81 CURRENT. no change in rating
2023-03-30 | N039716 | NT 804 SPK81 CURRENT no change in rating
2023-03-30 | N039716 | SPK 808 NT81 CURRENT no change in rating
2023-03-30 | N039716 | OC 702 SF71 CURRENT no change in rating
2023-03-30 | N039716 | SF 704 OC71 CURRENT. no change in rating
2023-03-30 | N039716 | OC 712 SF72 CURRENT no change in rating
2023-03-30 | N039716 | OLY 901 SHO/ST91 CURRENT no change in rating
2023-03-30 | N039716 | SHO 944 OLY/ST91 CURRENT no change in rating
2023-03-30 | N039716 | ST 932 OLY/SHO91 CURRENT no change in rating
2023-03-30 | N039716 | OP 809 Y81 CURRENT no change in rating
2023-03-30 | N039716 | Y 810 OP81 CURRENT no change in rating
2023-03-30 | N039716 | PCY 807 WKT81 CURRENT no change in rating
2023-03-30 | N039716 | WKT 811 PCY81 CURRENT. no change in rating
2023-03-30 | N039716 | PIC 808 WOR81 CURRENT no change in rating
2023-03-30 | N039716 | WOR 806 PIC81 CURRENT. no change in rating
2023-03-30 | N039716 | PJR 822 RGN81 CURRENT. no change in rating
2023-03-30 | N039716 | RGN 802 PJR81 CURRENT no change in rating
2023-03-30 | N039716 | PJR 864 YP81 CURRENT no change in rating
2023-03-30 | N039716 | YP 801 PJR81 CURRENT no change in rating
2023-03-30 | N039716 | RO 802 WAI81 CURRENT no change in rating
2023-03-30 | N039716 | WAI 801 RO81 CURRENT no change in rating
2023-03-30 | N039716 | SF 824 ST81 CURRENT no change in rating
2023-03-30 | N039716 | ST 834 SF81 CURRENT no change in rating
2023-03-30 | N039716 | SHO 942 WLT91 CURRENT no change in rating
2023-03-30 | N039716 | WLT 901 SHO91 CURRENT no change in rating
2023-03-30 | N039716 | SPK 805 WT81 CURRENT no change in rating
2023-03-30 | N039716 | WT 854 SPK81 CURRENT no change in rating
2023-03-30 | N039716 | ST 894 WLN81 CURRENT no change in rating
2023-03-30 | N039716 | WLN 809 ST81 CURRENT no change in rating
2023-03-30 | N039716 | SX 709 YER/CAR/MER71 CURRENT.no change in rating
2023-03-30 | N039716 | TS 820 TST81 CURRENT no change in rating
2023-03-30 | N039716 | TST 841 TS81 CURRENT no change in rating
2023-03-30 | N039716 | WCL 801 WOR81 CURRENT no change in rating
2023-03-30 | N039716 | WOR 801 WCL81 CURRENT no change in rating
2023-03-30 | N039716 | WD 709 WT71 CURRENT no change in rating
2023-03-30 | N039716 | WT 703 WD71 CURRENT no change in rating
2023-03-30 | N039716 | WD 701 WT72 CURRENT no change in rating
2023-03-30 | N039716 | WT 713 WD72 CURRENT no change in rating
2023-03-30 | N039716 | WGP 808 WOR81 CURRENT. no change in rating
2023-03-30 | N039716 | WOR 809 WGP81 CURRENT. no change in rating
2023-03-30 | N039716 | WKT X42 CGT/YLN X1 CURRENT no change in rating
2023-03-30 | N039716 | YLN X05 WKT X1 CURRENT no change in rating
2023-03-30 | N039716 | WMS 801 WMK81 CURRENT no change in rating
2023-03-30 | N039716 | YDT 944 YDW91 CURRENT no change in rating
2023-03-30 | N039716 | BSN715T4 LV no change in rating
2023-03-30 | N039716 | CT711T3 LV no change in rating
2023-03-30 | N039716 | CT714T1 LV no change in rating
2023-03-30 | N039716 | CT722T4 LV no change in rating
2023-03-30 | N039716 | CT806T3 HV no change in rating
2023-03-30 | N039716 | CT808T1 HV no change in rating
2023-03-30 | N039716 | CT814T4 HV no change in rating
2023-03-30 | N039716 | EP705T5 LV no change in rating
2023-03-30 | N039716 | EP713T3 LV no change in rating
2023-03-30 | N039716 | EP832T5 HV no change in rating
2023-03-30 | N039716 | EP842T3 HV no change in rating
2023-03-30 | N039716 | GLT807T1 LV no change in rating
2023-03-30 | N039716 | GLT954T1 HV no change in rating
2023-03-30 | N039716 | KDN614T2 TV no change in rating
2023-03-30 | N039716 | KEM812T1 LV no change in rating
2023-03-30 | N039716 | KEM822T2 LV no change in rating
2023-03-30 | N039716 | KEM842T13 LV circuit has been added
2023-03-30 | N039716 | KEM934T13 LV circuit has been added
2023-03-30 | N039716 | KNL801T1 LV circuit has been added
2023-03-30 | N039716 | KNL901T1 HV circuit has been added
2023-03-30 | N039716 | KOJ703T1 LV no change in rating
2023-03-30 | N039716 | KOJ709T2 LV no change in rating
2023-03-30 | N039716 | KW822SDT1 HV no change in rating
2023-03-30 | N039716 | KW852SDT2 HV no change in rating
2023-03-30 | N039716 | KW884BTT1 LV no change in rating
2023-03-30 | N039716 | KW932BTT1 HV no change in rating
2023-03-30 | N039716 | MER701T3(132/66) LV no change in rating
2023-03-30 | N039716 | MER707T1(132/66) LV no change in rating
2023-03-30 | N039716 | MU709SDT2 LV no change in rating
2023-03-30 | N039716 | MU711SDT1 LV no change in rating
2023-03-30 | N039716 | MU801BTT2 LV no change in rating
2023-03-30 | N039716 | MU810SDT2 HV no change in rating
2023-03-30 | N039716 | MU811SDT1 HV no change in rating
2023-03-30 | N039716 | MU824BTT1 LV no change in rating
2023-03-30 | N039716 | MU903BTT3 HV no change in rating
2023-03-30 | N039716 | MU914BTT1 HV no change in rating
2023-03-30 | N039716 | MUX23BTT2 HV no change in rating
2023-03-30 | N039716 | MUX33BTT3 LV no change in rating
2023-03-30 | N039716 | NBT872T2 LV no change in rating
2023-03-30 | N039716 | NBT964T2 HV no change in rating
2023-03-30 | N039716 | NGS704T1 LV no change in rating
2023-03-30 | N039716 | NGSX15T1 HV circuit has been added
2023-03-30 | N039716 | NOR703T2(132/66) LV decreased from 335 A to 332 A
2023-03-30 | N039716 | NOR709T1(132/66) LV decreased from 335 A to 332 A
2023-03-30 | N039716 | NOR804T2(132/66) HV decreased from 167 A to 166 A
2023-03-30 | N039716 | NOR810T1(132/66) HV decreased from 167 A to 166 A
2023-03-30 | N039716 | NT801T1 LV no change in rating
2023-03-30 | N039716 | NT808T2 LV no change in rating
2023-03-30 | N039716 | NT952T1 HV no change in rating
2023-03-30 | N039716 | NT982T2 HV no change in rating
2023-03-30 | N039716 | PIC705T1 LV no change in rating
2023-03-30 | N039716 | PIC710T2 LV no change in rating
2023-03-30 | N039716 | PIC805T1 HV circuit has been added
2023-03-30 | N039716 | PIC809T2 HV circuit has been added
2023-03-30 | N039716 | SF703T4 LV no change in rating
2023-03-30 | N039716 | SF709T3 LV no change in rating
2023-03-30 | N039716 | SF712T5 LV no change in rating
2023-03-30 | N039716 | SF822T3 HV no change in rating
2023-03-30 | N039716 | SF832T4 HV no change in rating
2023-03-30 | N039716 | SF895T5 HV no change in rating
2023-03-30 | N039716 | ST842T1 LV no change in rating
2023-03-30 | N039716 | ST862T2 LV no change in rating
2023-03-30 | N039716 | ST892T3 LV no change in rating
2023-03-30 | N039716 | ST934T1 HV no change in rating
2023-03-30 | N039716 | ST954T2 HV no change in rating
2023-03-30 | N039716 | ST964T3 HV no change in rating
2023-03-30 | N039716 | TST841T1 LV increased from 2143 A to 2231 A
2023-03-30 | N039716 | TST944T1 HV no change in rating
2023-03-30 | N039716 | WKT807T1 LV no change in rating
2023-03-30 | N039716 | WKT810T2 LV no change in rating
2023-03-30 | N039716 | WKT820T17 LV circuit has been added
2023-03-30 | N039716 | WKTX22T1 HV circuit has been added
2023-03-30 | N039716 | WKTX32T2 HV circuit has been added
2023-03-30 | N039716 | WLT801T1 LV no change in rating
2023-03-30 | N039716 | WLT806T2 LV no change in rating
2023-03-30 | N039716 | WT705T1 LV no change in rating
2023-03-30 | N039716 | WT708T2 LV no change in rating
2023-03-30 | N039716 | WT711T3 LV no change in rating
2023-03-30 | N039716 | WT822T1 HV no change in rating
2023-03-30 | N039716 | WT842T2 HV no change in rating
2023-03-30 | N039716 | WT852T3 HV no change in rating