## DCM Example
FacilityCode | DispatchIntervalStart | DispatchIntervalEnd | ProjectedQuantityMw | SnapshotMw | Check Date/Time | Seconds into minute of check Floored to 10 seconds | Response
DCM_EXAMPLE_SF1 | 2024-06-23 17:55:00.0000000 +08:00 | 2024-06-23 18:00:00.0000000 +08:00 | 13.078 | 0.4 | 2024-06-23 17:57 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 5:57:16 PM +08:00 was 0.4, Expected Operating Range: 2.078 - 24.078, DispatchTarget: 27.097
DCM_EXAMPLE_SF1 | 2024-06-23 17:55:00.0000000 +08:00 | 2024-06-23 18:00:00.0000000 +08:00 | 18.026 | 0.4 | 2024-06-23 17:58 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 5:58:16 PM +08:00 was 0.4, Expected Operating Range: 7.026 - 29.026, DispatchTarget: 27.097
DCM_EXAMPLE_SF1 | 2024-06-23 17:55:00.0000000 +08:00 | 2024-06-23 18:00:00.0000000 +08:00 | 22.974 | 0.4 | 2024-06-23 17:59 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 5:59:16 PM +08:00 was 0.4, Expected Operating Range: 11.974 - 33.974, DispatchTarget: 27.097
DCM_EXAMPLE_SF1 | 2024-06-23 18:00:00.0000000 +08:00 | 2024-06-23 18:05:00.0000000 +08:00 | 26.703 | 0.4 | 2024-06-23 18:00 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:00:17 PM +08:00 was 0.4, Expected Operating Range: 15.703 - 37.703, DispatchTarget: 15.272
DCM_EXAMPLE_SF1 | 2024-06-23 18:00:00.0000000 +08:00 | 2024-06-23 18:05:00.0000000 +08:00 | 24.338 | 0.4 | 2024-06-23 18:01 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:01:17 PM +08:00 was 0.4, Expected Operating Range: 13.338 - 35.338, DispatchTarget: 15.272
DCM_EXAMPLE_SF1 | 2024-06-23 18:00:00.0000000 +08:00 | 2024-06-23 18:05:00.0000000 +08:00 | 21.973 | 0.4 | 2024-06-23 18:02 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:02:17 PM +08:00 was 0.4, Expected Operating Range: 10.973 - 32.973, DispatchTarget: 15.272
DCM_EXAMPLE_SF1 | 2024-06-23 18:00:00.0000000 +08:00 | 2024-06-23 18:05:00.0000000 +08:00 | 19.608 | 0.4 | 2024-06-23 18:03 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:03:17 PM +08:00 was 0.4, Expected Operating Range: 8.608 - 30.608, DispatchTarget: 15.272
DCM_EXAMPLE_SF1 | 2024-06-23 18:00:00.0000000 +08:00 | 2024-06-23 18:05:00.0000000 +08:00 | 17.243 | 0.4 | 2024-06-23 18:04 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:04:17 PM +08:00 was 0.4, Expected Operating Range: 6.243 - 28.243, DispatchTarget: 15.272
DCM_EXAMPLE_SF1 | 2024-06-23 18:05:00.0000000 +08:00 | 2024-06-23 18:10:00.0000000 +08:00 | 16.176 | 0.2 | 2024-06-23 18:05 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:05:17 PM +08:00 was 0.2, Expected Operating Range: 5.176 - 27.176, DispatchTarget: 42.392
DCM_EXAMPLE_SF1 | 2024-06-23 18:05:00.0000000 +08:00 | 2024-06-23 18:10:00.0000000 +08:00 | 21.6 | 0.2 | 2024-06-23 18:06 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:06:17 PM +08:00 was 0.2, Expected Operating Range: 10.6 - 32.6, DispatchTarget: 42.392
DCM_EXAMPLE_SF1 | 2024-06-23 18:05:00.0000000 +08:00 | 2024-06-23 18:10:00.0000000 +08:00 | 27.024 | 0.2 | 2024-06-23 18:07 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:07:16 PM +08:00 was 0.2, Expected Operating Range: 16.024 - 38.024, DispatchTarget: 42.392
DCM_EXAMPLE_SF1 | 2024-06-23 18:05:00.0000000 +08:00 | 2024-06-23 18:10:00.0000000 +08:00 | 32.448 | 0.4 | 2024-06-23 18:08 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:08:17 PM +08:00 was 0.4, Expected Operating Range: 21.448 - 43.448, DispatchTarget: 42.392
DCM_EXAMPLE_SF1 | 2024-06-23 18:05:00.0000000 +08:00 | 2024-06-23 18:10:00.0000000 +08:00 | 37.872 | 0.4 | 2024-06-23 18:09 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:09:17 PM +08:00 was 0.4, Expected Operating Range: 26.872 - 48.872, DispatchTarget: 42.392
DCM_EXAMPLE_SF1 | 2024-06-23 18:10:00.0000000 +08:00 | 2024-06-23 18:15:00.0000000 +08:00 | 41.764 | 0.4 | 2024-06-23 18:10 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:10:17 PM +08:00 was 0.4, Expected Operating Range: 30.764 - 52.764, DispatchTarget: 23.563
DCM_EXAMPLE_SF1 | 2024-06-23 18:10:00.0000000 +08:00 | 2024-06-23 18:15:00.0000000 +08:00 | 37.999 | 0.4 | 2024-06-23 18:11 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:11:17 PM +08:00 was 0.4, Expected Operating Range: 26.999 - 48.999, DispatchTarget: 23.563
DCM_EXAMPLE_SF1 | 2024-06-23 18:10:00.0000000 +08:00 | 2024-06-23 18:15:00.0000000 +08:00 | 34.233 | 0.4 | 2024-06-23 18:12 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:12:17 PM +08:00 was 0.4, Expected Operating Range: 23.233 - 45.233, DispatchTarget: 23.563
DCM_EXAMPLE_SF1 | 2024-06-23 18:10:00.0000000 +08:00 | 2024-06-23 18:15:00.0000000 +08:00 | 30.467 | 0.4 | 2024-06-23 18:13 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:13:17 PM +08:00 was 0.4, Expected Operating Range: 19.467 - 41.467, DispatchTarget: 23.563
DCM_EXAMPLE_SF1 | 2024-06-23 18:10:00.0000000 +08:00 | 2024-06-23 18:15:00.0000000 +08:00 | 26.701 | 0.4 | 2024-06-23 18:14 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:14:17 PM +08:00 was 0.4, Expected Operating Range: 15.701 - 37.701, DispatchTarget: 23.563
DCM_EXAMPLE_SF1 | 2024-06-23 18:15:00.0000000 +08:00 | 2024-06-23 18:20:00.0000000 +08:00 | 23.271 | 0.4 | 2024-06-23 18:15 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:15:17 PM +08:00 was 0.4, Expected Operating Range: 12.271 - 34.271, DispatchTarget: 14.796
DCM_EXAMPLE_SF1 | 2024-06-23 18:15:00.0000000 +08:00 | 2024-06-23 18:20:00.0000000 +08:00 | 21.517 | 0.4 | 2024-06-23 18:16 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:16:16 PM +08:00 was 0.4, Expected Operating Range: 10.517 - 32.517, DispatchTarget: 14.796
DCM_EXAMPLE_SF1 | 2024-06-23 18:15:00.0000000 +08:00 | 2024-06-23 18:20:00.0000000 +08:00 | 19.764 | 0.4 | 2024-06-23 18:17 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:17:16 PM +08:00 was 0.4, Expected Operating Range: 8.764 - 30.764, DispatchTarget: 14.796
DCM_EXAMPLE_SF1 | 2024-06-23 18:15:00.0000000 +08:00 | 2024-06-23 18:20:00.0000000 +08:00 | 18.011 | 0.4 | 2024-06-23 18:18 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:18:16 PM +08:00 was 0.4, Expected Operating Range: 7.011 - 29.011, DispatchTarget: 14.796
DCM_EXAMPLE_SF1 | 2024-06-23 18:15:00.0000000 +08:00 | 2024-06-23 18:20:00.0000000 +08:00 | 16.257 | 0.4 | 2024-06-23 18:19 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:19:16 PM +08:00 was 0.4, Expected Operating Range: 5.257 - 27.257, DispatchTarget: 14.796
DCM_EXAMPLE_SF1 | 2024-06-23 18:20:00.0000000 +08:00 | 2024-06-23 18:25:00.0000000 +08:00 | 14.897 | 0.4 | 2024-06-23 18:20 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:20:16 PM +08:00 was 0.4, Expected Operating Range: 3.897 - 25.897, DispatchTarget: 17.824
DCM_EXAMPLE_SF1 | 2024-06-23 18:20:00.0000000 +08:00 | 2024-06-23 18:25:00.0000000 +08:00 | 15.503 | 0.4 | 2024-06-23 18:21 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:21:16 PM +08:00 was 0.4, Expected Operating Range: 4.503 - 26.503, DispatchTarget: 17.824
DCM_EXAMPLE_SF1 | 2024-06-23 18:20:00.0000000 +08:00 | 2024-06-23 18:25:00.0000000 +08:00 | 16.108 | 0.4 | 2024-06-23 18:22 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:22:16 PM +08:00 was 0.4, Expected Operating Range: 5.108 - 27.108, DispatchTarget: 17.824
DCM_EXAMPLE_SF1 | 2024-06-23 18:20:00.0000000 +08:00 | 2024-06-23 18:25:00.0000000 +08:00 | 16.714 | 0.4 | 2024-06-23 18:23 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:23:16 PM +08:00 was 0.4, Expected Operating Range: 5.714 - 27.714, DispatchTarget: 17.824
DCM_EXAMPLE_SF1 | 2024-06-23 18:20:00.0000000 +08:00 | 2024-06-23 18:25:00.0000000 +08:00 | 17.319 | 0.4 | 2024-06-23 18:24 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:24:16 PM +08:00 was 0.4, Expected Operating Range: 6.319 - 28.319, DispatchTarget: 17.824
DCM_EXAMPLE_SF1 | 2024-06-23 18:25:00.0000000 +08:00 | 2024-06-23 18:30:00.0000000 +08:00 | 17.23 | 0.4 | 2024-06-23 18:25 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:25:17 PM +08:00 was 0.4, Expected Operating Range: 6.23 - 28.23, DispatchTarget: 0
DCM_EXAMPLE_SF1 | 2024-06-23 18:25:00.0000000 +08:00 | 2024-06-23 18:30:00.0000000 +08:00 | 13.665 | 0.4 | 2024-06-23 18:26 | 10 | DCM_EXAMPLE_SF1 Sent-Out MW at 23/06/2024 6:26:17 PM +08:00 was 0.4, Expected Operating Range: 2.665 - 24.665, DispatchTarget: 0

## DCM Logic
DCM Logic | [9 empty] | Dispatch Instructions |  | Tolerance Range
Time | NETT SCADA MW Output | Seconds since Start of Dispatch Interval | Seconds into minute the check occurred floored to 10 seconds | DCM Projected Quantity MW | Regulation Lower | Regulation Raise | Tolerance Down | Tolerance Up | Non-Compliant | Time | Dispatch Target (MW) | 11
17:50 | 0.4 | 0 | 10 | 0.079 | 0 | 0 | -10.921 | 11.079 | FALSE | 17:45 | 0
17:51 | 0.4 | 60 | 10 | 0.55 | 0 | 0 | -10.45 | 11.55 | FALSE | 17:50 | 2.358
17:52 | 0.4 | 120 | 10 | 1.022 | 0 | 0 | -9.978 | 12.022 | FALSE | 17:55 | 27.097
17:53 | 0.4 | 180 | 10 | 1.493 | 0 | 0 | -9.507 | 12.493 | FALSE | 18:00 | 15.272
17:54 | 0.4 | 240 | 10 | 1.965 | 0 | 0 | -9.035 | 12.965 | FALSE | 18:05 | 42.392
17:55 | 0.4 | 0 | 10 | 3.183 | 0 | 0 | -7.817 | 14.183 | FALSE | 18:10 | 23.563
17:56 | 0.4 | 60 | 10 | 8.13 | 0 | 0 | -2.87 | 19.13 | FALSE | 18:15 | 14.796
17:57 | 0.4 | 120 | 10 | 13.078 | 0 | 0 | 2.078 | 24.078 | TRUE | 18:20 | 17.824
17:58 | 0.4 | 180 | 10 | 18.026 | 0 | 0 | 7.026 | 29.026 | TRUE | 18:25 | 0
17:59 | 0.4 | 240 | 10 | 22.974 | 0 | 0 | 11.974 | 33.974 | TRUE | 18:30 | 0
18:00 | 0.4 | 0 | 10 | 26.703 | 0 | 0 | 15.703 | 37.703 | TRUE
18:01 | 0.4 | 60 | 10 | 24.338 | 0 | 0 | 13.338 | 35.338 | TRUE
18:02 | 0.4 | 120 | 10 | 21.973 | 0 | 0 | 10.973 | 32.973 | TRUE
18:03 | 0.4 | 180 | 10 | 19.608 | 0 | 0 | 8.608 | 30.608 | TRUE
18:04 | 0.4 | 240 | 10 | 17.243 | 0 | 0 | 6.243 | 28.243 | TRUE
18:05 | 0.4 | 0 | 10 | 16.176 | 0 | 0 | 5.176 | 27.176 | TRUE
18:06 | 0.4 | 60 | 10 | 21.6 | 0 | 0 | 10.6 | 32.6 | TRUE
18:07 | 0.4 | 120 | 10 | 27.024 | 0 | 0 | 16.024 | 38.024 | TRUE
18:08 | 0.4 | 180 | 10 | 32.448 | 0 | 0 | 21.448 | 43.448 | TRUE
18:09 | 0.4 | 240 | 10 | 37.872 | 0 | 0 | 26.872 | 48.872 | TRUE
18:10 | 0.4 | 0 | 10 | 41.764 | 0 | 0 | 30.764 | 52.764 | TRUE
18:11 | 0.4 | 60 | 10 | 37.999 | 0 | 0 | 26.999 | 48.999 | TRUE
18:12 | 0.4 | 120 | 10 | 34.233 | 0 | 0 | 23.233 | 45.233 | TRUE
18:13 | 0.4 | 180 | 10 | 30.467 | 0 | 0 | 19.467 | 41.467 | TRUE
18:14 | 0.4 | 240 | 10 | 26.701 | 0 | 0 | 15.701 | 37.701 | TRUE
18:15 | 0.4 | 0 | 10 | 23.271 | 0 | 0 | 12.271 | 34.271 | TRUE
18:16 | 0.4 | 60 | 10 | 21.517 | 0 | 0 | 10.517 | 32.517 | TRUE
18:17 | 0.4 | 120 | 10 | 19.764 | 0 | 0 | 8.764 | 30.764 | TRUE
18:18 | 0.4 | 180 | 10 | 18.011 | 0 | 0 | 7.011 | 29.011 | TRUE
18:19 | 0.4 | 240 | 10 | 16.257 | 0 | 0 | 5.257 | 27.257 | TRUE
18:20 | 0.4 | 0 | 10 | 14.897 | 0 | 0 | 3.897 | 25.897 | TRUE
18:21 | 0.4 | 60 | 10 | 15.503 | 0 | 0 | 4.503 | 26.503 | TRUE
18:22 | 0.4 | 120 | 10 | 16.108 | 0 | 0 | 5.108 | 27.108 | TRUE
18:23 | 0.4 | 180 | 10 | 16.714 | 0 | 0 | 5.714 | 27.714 | TRUE
18:24 | 0.4 | 240 | 10 | 17.319 | 0 | 0 | 6.319 | 28.319 | TRUE
18:25 | 0.4 | 0 | 10 | 17.23 | 0 | 0 | 6.23 | 28.23 | TRUE
18:26 | 0.4 | 60 | 10 | 13.665 | 0 | 0 | 2.665 | 24.665 | TRUE
18:27 | 0.4 | 120 | 10 | 10.1 | 0 | 0 | -0.9 | 21.1 | FALSE
18:28 | 0.4 | 180 | 10 | 6.535 | 0 | 0 | -4.465 | 17.535 | FALSE
18:29 | 0.4 | 240 | 10 | 2.971 | 0 | 0 | -8.029 | 13.971 | FALSE
18:30 | 0.4 | 0 | 10 | 0 | 0 | 0 | -11 | 11 | FALSE