## AEMO-use Only
AEMO-approved fields
DUID:
Solar Farm Maximum Capacity (MW):
Cluster ID(s):
Cluster Maximum Capacity (MW):

## Submission Guideline
ECM data template submission guideline:
This guideline for the Energy Conversion Model (ECM) data for registering Semi-Scheduled Generators has been published as prescribed in the Central Dispatch and Integration of Wind and Other Intermittent Generation Rule 2008 under clause 2.2.7(d).
How to use this document
Parameters that need to be supplied by the solar farm to AEMO are listed and marked as 'Mandatory'.
Sampling rates for dynamic parameters are specified. These denote the sampling intervals for data. Aggregation of this data will be done within MMS or the ECM.
Italicised terms are defined in 'Chapter 10: Glossary' of the National Electricity Rules (NER).
Who needs to submit an ECM
A generator intending to register as semi-scheduled must submit an ECM under the National Electricity Rules (NER) clause 2.2.7(c)(2).
Some Non-Scheduled generators may be required to submit an ECM under NER clause 2.2.3(c).
To avoid delays, AEMO recommends that the first draft of the ECM be submitted to AEMO at least three months before applying for Registration.
Document structure
The document is divided by technology types. To this end:
- the 'ECM PV' worksheet contains parameters for solar PV farms with and without tracking technology, fields relating to solar farm level
- the 'ECM PV Cluster' worksheet contains contains fields relating to cluster level operation for solar PV farms. Additional Cluster tabs should be created if more than one cluster exists for the solar farm.
- the 'ECM CPV' worksheet contains parameters for concentrating solar PV technologies, fields relating to solar farm level
- the 'ECM PV Cluster' worksheet contains contains fields relating to cluster level operation for concentrating solar PV farms. Additional Cluster tabs should be created if more than one cluster exists for the solar farm.
- the 'ECM CST' worksheet contains parameters for concentrating solar thermal technologies, fields relating to solar farm level
- the 'ECM PV Cluster' worksheet contains contains fields relating to cluster level operation for concentrating solar thermal farms. Additional Cluster tabs should be created if more than one cluster exists for the solar farm.
Facility hierarchy
There is an assumed hierarchy of sub-components that constitute a solar farm. These are illustrated in the diagram below
In the event that multiple sub-components are available, parameters applicable to these sub-components will need to be provided for each sub-component.
E.g. There are multiple clusters in a facility. Parameters that are applicable to every cluster in the 'ECM PV Cluster' tab will need to be provided
Note that one ECM is required to be submitted for every dispatchable unit within a facility.
Additional Information
In the interest of maintaining accuracy of the solar generation forecasts, any material changes to the ECM data must be re-submitted to AEMO and at any other time on AEMO request.
Where relevant, the data entered into the ECM data template needs to be consistent with, or derived from, data in the Power System Design Data Sheets and Generating System Setting Data Sheets, or as otherwise agreed with AEMO.
Modules/concentrators
Inverter/turbine
Facility
An inverter is fed by multiple modules or concentrators
A cluster is potentially comprised of multiple inverters
A facility is potentially comprised of multiple dispatchable units
Cluster
Dispatchable Unit
A dispatchable unit is potentially comprised of multiple clusters

## Cluster Definition Guideline
Terms and definitions
Term | Definition
Cluster (PV technology) | A cluster is defined as a subset of the Facility with: - the same inverter type (manufacturer, model and rating) - the same module material (PolySi or CdTd or ...) - the same total module DC power connected to each inverter. Tolerance: +/- 2.5% from average. - the same fixed slope and azimuth angles of modules, if fixed - the same tracking algorithm and ranges, if tracking - geographically close location of all modules (within an area up to 5km x 5km)
Cluster (CPV technology) | A cluster is defined as a subset of the Facility with: - the same module type (manufacturer, model and material) - the same inverter type (manufacturer, model and rating) - the same number of modules connected to each inverter - the same tracking algorithm and ranges - the same concentrator attributes - geographically close location of all modules (within an area up to 5km x 5km)
Cluster (CST technology) | A cluster is defined as a subset of the facility with: - the same actual turbine(s) - the same tracking algorithm and ranges - the same concentrator attributes - geographically close location of all modules (within an area up to 5km x 5km)
Dispatchable Unit | The solar farm component enabled for dispatch
Module | For PV farms, is the individual solar panel
Slope angle | The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
Azimuth angle | The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc.)
Tracking slope angle | The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and -90°/90° for a vertical plane. East-West tracking: Morning eastwards angles positive, afternoon westwards angles negative. Azimuth angle to be specified as 90° for East for farms with East-West tracking (or if not exactly East-West accordingly near 90°).
Cluster definition examples
Example 1 | Solar PV without tracking, one module type and one inverter type for the entire facility, same number of modules connected to each inverter
In this case, the cluster definition is straightforward. There would only need to be one cluster with all the inverters contained in that cluster.
Example 2 | Solar PV with three module types, all with same PV material, and one inverter type for the entire facility, all modules with same tracking angle range and algorithms
The DC power of modules connected to each inverter in a cluster must be the same with +/- 2.5% tolerance compared to the average. All parameters related to modules must be specified for each module type. E.g. One inverter having both 1,000 x 102 W poly-Si and 2,000 x 97 W poly-Si panels connected would result in 296 kW DC per inverter, and then another inverter having 3,000 x 97 W poly-Si panels would result in 291 kW DC per inverter; this arrangement could still be in one cluster, as the average of all inverters is 293.5 kW and the deviation from the average is approx +0.84% and -0.86%; both <2.5%. However, having one inverter with both 1000 x 102 W poly-Si and 2000 x 97 W poly-Si panels connected would result in 296 kW DC per inverter, and then another inverter having 2500 x 97 W poly-Si panels connected would result in 242.5 kW DC per inverter; this arrangement requires more than one cluster as the average of all inverters is 269.25 kW; the individual kW DC per inverter deviates more than 2.5% from the average.
Example 3 | Solar PV without tracking, one module type and two inverter types for the entire facility
Two clusters would be specified. The first cluster would relate to the first inverter type, the second cluster would relate to the second inverter type.

## ECM PV
Energy Conversion Model for non-concentrating PV farms | [7 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
Data Parameter | Data type | Valid range | Mandatory | Interval | Value | Units | Comments | Description
Farm Level | Parameters that apply to the solar farm. |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value.
Solar farm identification
Power Station name | Descriptive string | n/a | Yes | n/a |  | n/a |  | Name of the Solar farm. To be same as specified in the 'Application for Registration as a Generator in the NEM' document, section C.
Region | Descriptive string | n/a | Yes | n/a |  | n/a |  | Name of NEM region of the facility. To be same as specified in the 'Application for Registration as a Generator in the NEM' document.
Solar farm nominal data
Nameplate Rating | Scalar decimal number | >0 | Yes | n/a |  | MW |  | The total installed capacity of the Solar Farm (MW) as outlined in the Performance Standard. This equals the sum of the AC power rating of all inverters. This Item corresponds to "Nameplate Rating of Generating System" in section C of the "Application for Registration as a Generator in the NEM" document.
Maximum Capacity | Scalar integer number | >0 | Yes | n/a |  | MW |  | Maximum generation to which the semi-scheduled generating unit may be dispatched as outlined in the Performance Standard, rounded down to the nearest whole MW. This definition can be found in section C of the "Application for Registration as a Generator in the NEM" document. The Maximum Capacity value must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Solar farm location and terrain data
Facility latitude | Scalar decimal number | (-90,90) | Yes | n/a |  | Decimal degrees |  | Defined at the centre of the collector area
Facility longitude | Scalar decimal number | (-180,180) | Yes | n/a |  | Decimal degrees |  | Defined at the centre of the collector area
Facility altitude | Scalar decimal number | (-15,2228) | Yes | n/a |  | metres ASL |  | Defined at the centre of the collector area
Facility map | PDF / high resolution image | n/a | Yes | n/a |  | pdf file |  | Terrain map file with positions of receivers, strings, measuring devices marked. Please submit as separate pdf.
Solar farm other
Number of clusters | Scalar positive integer | >0 | Yes | n/a |  | n/a |  | Number of clusters of the facility, for cross-checking
List of measurement devices (Device ID) | Descriptive string, e.g. a device type and model number e.g. "TSP-700 Pyranometer" | n/a | Yes | n/a |  | n/a |  | Provide list of measurement devices.
NSP MW Control Schemes in operation | String | n/a | n/a | Yes |  | n/a |  | Provide details of NSP MW Control Schemes used to down regulate the solar farm at solar farm and/or cluster level.
Any other restrictions | String | n/a | n/a | Yes |  | n/a |  | Provide details of any other limitations imposed on the Solar Farm. This should be consistent with information provided in Power System Design Data Sheets section 6.1.2 (tab S-6), and Data Sheets section 7.1.2 (tab S-7).
Solar farm SCADA to AEMO: |  |  |  |  | Provision |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated at least every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, maximum 15-second average update is required
Data Parameter | Data type | Valid range | Mandatory | Interval | Yes/No | Units | Comments | Description
Solar Farm Active Power | Scalar decimal number | (<0, >=0) | Yes | 4-10 secs |  | MW |  | Total solar farm active power. The SCADA Solar Farm Active Power measurement must reference the agreed point of dispatch.
Control System Set-Point | Scalar non-negative decimal number | (0, 2.5 x Nameplate Rating) | Yes | 4-10 secs |  | MW |  | MW Set-Point applied in the solar farm's control system to limit (down regulate) its output. At other times when no limit applies, the set-point to be set to above the solar farm's Nameplate Rating, but below 250% of it. SCADA MW Set-Point must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Local Limit | Scalar non-negative decimal number | (0, Max Capacity) | Yes | 4-10 secs |  | MW |  | In MW, the SCADA Local Limit for a solar farm is the lower of its plant availability and all technical limits on the capacity of its connection assets to export energy. When implemented in AWEFS, the SCADA Local Limit is used to cap the UIGF for the solar farm in the dispatch timeframe. The SCADA Local Limit excludes limits on a transmission network and distribution network (to ensure AEMO’s compliance with clause 3.7B(c)(6) of the Rules), and may exclude other limits managed by AEMO through the central dispatch process. Limits already communicated in the SCADA Cluster Inverters Available signal may be excluded from the SCADA Local Limit. Manually-applied transient limits not intended to apply at the end of the next dispatch interval may be excluded from the SCADA Local Limit. The SCADA Local Limit should not exceed the higher of the nameplate ratingand the Maximum Capacity of the solar farm. SCADA Local Limit must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Possible Power | Scalar non-negative decimal number | (0, Max Capacity) | No | 4-10 secs |  | MW |  | SCADA Possible Power is the Generator’s estimate in MW of current unconstrained intermittent generation, subject only to technical factors affecting operation of its generation and connection assets. SCADA Possible Power is used to assess the performance of unconstrained intermittent generation forecasts. SCADA Possible Power must be calculated assuming that no transmission or distribution network constraints currently apply, and may assume that other limits managed by AEMO through the central dispatch process do not apply. SCADA Possible Power must reflect any Local Limits at the solar farm, unless agreed with AEMO. The SCADA Possible Power must not exceed the Maximum Capacity of the solar farm. SCADA Possible Power must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Wind Speed | Scalar decimal number | >=0 | Yes | 4-10 secs |  | m/s |  | To be representative of the facility.
Wind Direction | Scalar decimal number (bearing) | (0,360) | Yes | 4-10 secs |  | º |  | To be representative of the facility.
Ambient Temperature | Scalar decimal number | (-50,100) | Yes | 4-10 secs |  | ºC |  | To be representative of the facility.
Relative Humidity | Scalar non-negative decimal number | (0,100) | Yes | 4-10 secs |  | % |  | To be representative of the facility.
Ends
A cluster is defined as a subset of the Facility with:
- the same inverter type (manufacturer, model and rating)
- the same combination and number of modules connected to each inverter
- the same fixed slope and azimuth angles of modules, if fixed
- the same tracking algorithm and ranges, if tracking
- geographically close location of all modules

## ECM PV Cluster
Energy Conversion Model for non-concentrating PV farms | [7 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
Data Parameter | Data type | Valid range | Mandatory | Interval | Value | Units | Comments | Description
Cluster Level | Parameters that apply to a cluster Please copy this sheet into a separate tab for each additional cluster. |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value. |  |  | A cluster is defined as a subset of the Facility with: - the same inverter type (manufacturer, model and rating) - the same module material (PolySi or CdTd or ...) - the same total module DC power connected to each inverter. Tolerance: +/- 2.5% from average - the same fixed slope and azimuth angles of modules, if fixed - the same tracking algorithm and ranges, if tracking - geographically close location of all modules (within an area up to 5km x 5km)
Cluster identification
Cluster Reference | Descriptive String | n/a | Yes | n/a |  | n/a |  | Unique reference for this cluster. Note, following ECM submission, AEMO will allocate a unique cluster identification to each of your clusters.
Cluster Characteristics
Technology type and Tracking | Descriptive string. E.g. {PV static, PV single axis azimuth tracking, PV single axis slope tracking, PV dual axis tracking} | n/a | Yes | n/a |  | n/a |  | The type of technology used in the cluster including information on tracking.
Cluster centre latitude | Scalar decimal number | (-90,90) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module area of the cluster
Cluster centre longitude | Scalar decimal number | (-180,180) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module area of the cluster
Cluster centre altitude | Scalar decimal number | (-15,2228) | Yes |  |  | meters ASL |  | Defined at the centre of the module area of the cluster
Number of modules in cluster (grand total) | Scalar number | >0 | Yes |  |  | n/a |  | The total number of modules in this cluster, used for cross-checking
Number of inverters | Scalar number | >0 | Yes |  |  | n/a |  | The number of inverters in this cluster
Inverter manufacturer | String | n/a | Yes |  |  | n/a |  | Name of manufacturer of inverters in this cluster
Inverter type reference | String | n/a | Yes |  |  | n/a |  | Manufacturer inverter type reference/model name for inverters in this cluster
Inverter DC power rating | Scalar non-negative decimal number | >0 | Yes |  |  | kW DC |  | DC power rating for inverters in this cluster. Please specify the DC power rating from the datasheet of the inverter manufacturer (max DC rating), not the DC power of the modules attached to the inverter.
Inverter AC power rating | Scalar non-negative decimal number | >0 | Yes |  |  | kW AC |  | AC power rating for inverters in this cluster
Inverter temperature rating | 2-vector (min, max) | n/a | Yes |  |  | min ºC |  | Operating temperature range of inverter as specified by manufacturer
max ºC
Inverter response | 2-vector (power, efficiency) | >=0 | Yes |  |  | power: kW |  | See the inverter response example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted. Please only provide a single curve.
|  | (0,1) |  |  |  | efficiency: n/a |  | Alternatively, 0-100%
Total DC power of modules in cluster | Scalar decimal number | >0 | Yes |  |  | MW |  | The total sum DC nameplate rating of all modules in this cluster, used for cross-checking and documenting overprovisioning ratio
Total DC power of inverters in cluster | Scalar decimal number | >0 | Yes |  |  | MW |  | The total sum DC nameplate rating of all inverters in this cluster, used for cross-checking and documenting overprovisioning ratio
Total AC power of inverters in cluster | Scalar decimal number | >0 | Yes |  |  | MW |  | The total sum AC nameplate rating of all inverters in this cluster, used for cross-checking and documenting overprovisioning ratio
DC power of modules connected to each inverter (min, avg, max) | Scalar decimal number (min, avg, max) | >0 | Yes |  |  | min MW |  | The combined module DC power rating for all modules connected to a single inverter in this cluster, minimum of all inverters in this cluster. Note: Must not be more than 2.5% below average.
[6 empty] | avg MW |  | The combined module DC power rating for all modules connected to a single inverter in this cluster, average of all inverters in this cluster.
[6 empty] | max MW |  | The combined module DC power rating for all modules connected to a single inverter in this cluster, maximum of all inverters in this cluster. Note: Must not be more than 2.5% above average.
Module material | String E.g. {"poly-Si", "mono-Si", "multi-Si", "CdTe", …} | n/a | Yes |  |  | n/a |  | PV material used for all modules in this cluster. Material of interest is the substance that is used to convert sunlight to electricity (e.g. monocrystalline silicon, cadmium telluride).
Tracking slope angle range | 2-vector (min, max) | (-90,90) | Required for slope tracking systems only |  |  | min degrees (º) |  | Minimum slope angle for clusters with slope tracking of the modules. The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and -90°/90° for a vertical plane.
[6 empty] | max degrees (º) |  | Maximum slope angle for clusters with slope tracking of the modules.
Slope tracking direction | String, E.g. {"East-West", "North-South", ...} | n/a | Required for slope tracking systems only |  |  | n/a |  | Direction in which slope tracking is done. Specify "north-south" if panels are tilted in the north/south direction over an east-west axis. Specify "east-west" if panels are tilted from east to west over a north-south axis. For any other angles/cases, specify the compass orientation of the tracking (see "azimuth", perpendicular to axis' compass orientation) and attach additional information on the tracking
Tracking azimuth angle range | 2-vector (min, max) | (0,360) | Required for azimuth tracking systems only |  |  | min degrees (º) |  | Minimum azimuth angle for clusters with azimuth tracking of the modules. The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc.)
[6 empty] | max degrees (º) |  | Maximum azimuth angle for clusters with azimuth tracking of the modules.
Fixed slope angle | Scalar decimal number | (0,90) | Required for non-slope-tracking systems |  |  | º |  | Fixed slope angle of the modules for clusters without slope tracking. The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
Fixed azimuth angle | Scalar decimal number | (0,360) | Required for non-azimuth- tracking systems |  |  | º |  | Fixed azimuth angle of the modules for clusters without azimuth tracking of the modules. The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc.)
Cluster SCADA |  |  |  |  | Provision |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated at least every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, maximum 15-second average update is required
Data Parameter | Data type | Valid range | Mandatory | Interval | Yes/No | Units | Comments | Description
Global horizontal irradiance | Scalar non-negative decimal number | (0,1415) | Yes | 4-10 secs |  | W/m2 |  | Per cluster Measured using a ISO First class pyranometer
Global inclined irradiance | Scalar non-negative decimal number | (0,1415) | Yes | 4-10 secs |  | W/m2 |  | Per cluster Same orientation of the panel Measured using a ISO First class pyranometer
Module surface temperature | Scalar decimal number | (-50,100) | Yes | 4-10 secs |  | ºC |  | Per cluster Averaged across all modules in a cluster
Number of inverters available | Scalar non-negative decimal number | >=0 | Yes | 4-10 secs |  | n/a |  | Per cluster The number of inverters that are available to deliver active power if sufficient sunlight is available
Reduction through soiling | Scalar non-negative decimal number | (0,100) | No | 4-10 secs |  | % |  | Per cluster The percentage reduction of module production caused by soiling. If this parameter is measured at the facility, then it will be requested by AEMO to be provided but is optional.
Actual tracking slope angle | Scalar non-negative decimal number | (-90,90) | Required for slope tracking systems. | 4-10 secs |  | º |  | Per cluster For sign convention, refer to 'tracking slope angle' term in Cluster Definition Guideline tab.
Actual tracking azimuth angle | Scalar non-negative decimal number | (0,360) | Required for azimuth tracking systems. | 4-10 secs |  | º |  | Per cluster
Tracking share of modules not on track | Scalar non-negative decimal number | (0,100) | Required for tracking systems only | 4-10 secs |  | % |  | Per cluster
Trackers online | Scalar non-negative integer | >=0 | Optional, for tracking systems only | 4-10 secs |  | n/a |  | Per Cluster
Module Type 1 used in this Cluster | Parameters that apply to a module type used within a cluster (part of cluster definition) |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value.
Data Parameter | Data type | Valid range | Mandatory | Interval | Value | Units | Comments | Description
Module manufacturer | String | n/a | Yes | n/a |  | n/a |  | Manufacturer of PV modules in this cluster
Module type reference | String | n/a | Yes |  |  | n/a |  | Manufacturer module/panel type reference/model name for modules in this cluster
Module DC power rating | Scalar decimal number | n/a | Yes |  |  | W DC |  | The power rating for each single module in this cluster at standard test conditions. Standard test conditions are defined as irradiance of 1000 W/m2 at AM 1.5 solar spectrum and temperature 25 ± 2 °C
Module surface area | Scalar number | >0 | Yes |  |  | m2 |  | Surface area of a single module
Module temperature response | Scalar number | (0,100) | No |  |  | %/K |  | % decrease of efficiency per degree.
Module normalised spectral response | 2-vector (wavelength, response) | (200,4000) | No |  |  | wavelength: nm |  | See the spectral response worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | response: n/a |  | Alternatively, 0-100%
Module degradation curve | 2-vector (year since installation, degradation) | >=0 | No |  |  | year since installation: n/a |  | See the degradation curve example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | degradation: n/a |  | Alternatively, 0-100%
Module annual degradation rate | Scalar number | (0,100) | No |  |  | %/year |  | Fallback if degradation curve is not supplied
Module Type 2 used in this Cluster | Parameters that apply to a module type used within a cluster (part of cluster definition). ONLY COMPLETE IF THIS CLUSTER HAS MORE THAN 1 MODULE TYPE.
Module manufacturer | String | n/a | Yes | n/a |  | n/a |  | Manufacturer of PV modules in this cluster
Module type reference | String | n/a | Yes |  |  | n/a |  | Manufacturer module/panel type reference/model name for modules in this cluster
Module DC power rating | Scalar decimal number | n/a | Yes |  |  | W DC |  | The power rating for each single module in this cluster at standard test conditions. Standard test conditions are defined as irradiance of 1000 W/m2 at AM 1.5 solar spectrum and temperature 25 ± 2 °C
Module surface area | Scalar number | >0 | Yes |  |  | m2 |  | Surface area of a single module
Module temperature response | Scalar number | (0,100) | No |  |  | %/K |  | % decrease of efficiency per degree.
Module normalised spectral response | 2-vector (wavelength, response) | (200,4000) | No |  |  | wavelength: nm |  | See the spectral response worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | response: n/a |  | Alternatively, 0-100%
Module degradation curve | 2-vector (year since installation, degradation) | >=0 | No |  |  | year since installation: n/a |  | See the degradation curve example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | degradation: n/a |  | Alternatively, 0-100%
Module annual degradation rate | Scalar number | (0,100) | No |  |  | %/year |  | Fallback if degradation curve is not supplied
Module Type 3 used in this Cluster | Parameters that apply to a module type used within a cluster (part of cluster definition). ONLY COMPLETE IF THIS CLUSTER HAS MORE THAN 2 MODULE TYPES. ADD MORE MODULE TYPE SECTIONS IF REQUIRED.
Module manufacturer | String | n/a | Yes | n/a |  | n/a |  | Manufacturer of PV modules in this cluster
Module type reference | String | n/a | Yes |  |  | n/a |  | Manufacturer module/panel type reference/model name for modules in this cluster
Module DC power rating | Scalar decimal number | n/a | Yes |  |  | W DC |  | The power rating for each single module in this cluster at standard test conditions. Standard test conditions are defined as irradiance of 1000 W/m2 at AM 1.5 solar spectrum and temperature 25 ± 2 °C
Module surface area | Scalar number | >0 | Yes |  |  | m2 |  | Surface area of a single module
Module temperature response | Scalar number | (0,100) | No |  |  | %/K |  | % decrease of efficiency per degree.
Module normalised spectral response | 2-vector (wavelength, response) | (200,4000) | No |  |  | wavelength: nm |  | See the spectral response worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | response: n/a |  | Alternatively, 0-100%
Module degradation curve | 2-vector (year since installation, degradation) | >=0 | No |  |  | year since installation: n/a |  | See the degradation curve example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | degradation: n/a |  | Alternatively, 0-100%
Module annual degradation rate | Scalar number | (0,100) | No |  |  | %/year |  | Fallback if degradation curve is not supplied
Inverter | Parameters that apply to an individual inverter. COPY THIS SECTION OF THE SHEET FOR EACH INVERTER IN THE CLUSTER.
Inverter ID | Descriptive string, e.g. INV_1045 | n/a | Yes | n/a |  | n/a |  | Unique ID for this inverter (may be built of cluster ID plus count).
Centre latitude of modules connected to inverter | Scalar decimal number | (-90,90) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module area of modules connected to this inverter.
Centre longitude of modules connected to inverter | Scalar decimal number | (-180,180) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module area of modules connected to this inverter.
Centre altitude of modules connected to inverter | Scalar decimal number | (-15,2228) | Yes |  |  | m ASL |  | Defined at the centre of the module area of modules connected to this inverter.
Number of modules of Module Type 1 connected to this inverter | integer number | >=0 | Yes |  |  | n/a |  | Please specify for each inverter.
Number of modules of Module Type 2 connected to this inverter | integer number | >=0 | Yes |  |  | n/a |  | Please specify for each inverter, only used if more than one module type.
Number of modules of Module Type 3 connected to this inverter | integer number | >=0 | Yes |  |  | n/a |  | Please specify for each inverter, only used if more than two module types, add more if more than three module types.
DC power of modules connected to this inverter | Scalar decimal number | >0 | Yes |  |  | MW |  | The combined module DC power rating for all modules connected to this inverter.
Ends

## ECM CPV
Energy Conversion Model for concentrating PV farms | [7 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
Data Parameter | Data type | Valid range | Mandatory | Interval | Value | Units | Comments | Description
Farm Level | Parameters that apply to the solar farm. |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value.
Solar farm identification
Power Station name | Descriptive string | n/a | Yes | n/a |  | n/a |  | Name of the Solar farm. To be same as specified in the 'Application for Registration as a Generator in the NEM' document, section C.
Region | Descriptive string | n/a | Yes | n/a |  | n/a |  | Name of NEM region of the facility. To be same as specified in the 'Application for Registration as a Generator in the NEM' document.
Solar farm nominal data
Nameplate Rating | Scalar decimal number | >0 | Yes | n/a |  | MW |  | The total installed capacity of the Solar Farm (MW) as outlined in the Performance Standard. This equals the sum of the AC power rating of all inverters. This Item corresponds to "Nameplate Rating of Generating System" in section C of the "Application for Registration as a Generator in the NEM" document.
Maximum Capacity | Scalar integer number | >0 | Yes | n/a |  | MW |  | Maximum generation to which the semi-scheduled generating unit may be dispatched as outlined in the Performance Standard, rounded down to the nearest whole MW. This definition can be found in section C of "Application for Registration as a Generator in the NEM" document. The Maximum Capacity value must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Solar farm location and terrain data
Facility Latitude | Scalar decimal number | (-90,90) | Yes | n/a |  | Decimal degrees |  | Defined at the centre of the collector area
Facility Longitude | Scalar decimal number | (-180,180) | Yes | n/a |  | Decimal degrees |  | Defined at the centre of the collector area
Facility Altitude | Scalar decimal number | (-15,2228) | Yes | n/a |  | metres ASL |  | Defined at the centre of the collector area
Facility Map | PDF / high resolution image | n/a | Yes | n/a |  | n/a |  | Terrain map file with positions of receivers, strings, measuring devices marked. Please submit as separate pdf.
Solar farm other
Number of Clusters | Scalar positive integer | >0 | Yes | n/a |  | n/a |  | Number of clusters of the facility, for cross-checking
List of measurement devices (Device ID) | Descriptive string, e.g. a device type and model number e.g. "TSP-700 Pyranometer" | n/a | Yes | n/a |  | n/a |  | Please complete the measurement devices worksheet.
NSP MW Control Schemes in operation | String | n/a | Yes | n/a |  | n/a |  | Provide details of NSP MW Control Schemes used to down regulate the solar farm at solar farm and/or cluster level.
Any other restrictions | String | n/a | Yes | n/a |  | n/a |  | Provide details of any other limitations imposed on the Solar Farm. This should be consistent with information provided in Power System Design Data Sheets section 6.1.2 (tab S-6), and Data Sheets section 7.1.2 (tab S-7).
Solar farm SCADA to AEMO: |  |  |  |  | Provision |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated at least every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, maximum 15-second average update is required.
Data Parameter | Data type | Valid range | Mandatory | Interval | Yes/No | Units | Comments | Description
Solar Farm Active Power | Scalar decimal number | (<0, >=0) | Yes | 4-10 secs |  | MW |  | Total solar farm active power. The SCADA Solar Farm Active Power measurement must reference the agreed point of dispatch.
Control System Set-Point | Scalar non-negative decimal number | (0, 2.5 x Nameplate Rating) | Yes | 4-10 secs |  | MW |  | MW Set-Point applied in the solar farm's control system to limit (down regulate) its output. At other times when no limit applies, the set-point to be set to above the solar farm's Nameplate Rating, but below 250% of it. SCADA MW Set-Point must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Local Limit | Scalar non-negative decimal number | (0, Max Capacity) | Yes | 4-10 secs |  | MW |  | In MW, the SCADA Local Limit for a solar farm is the lower of its plant availability and all technical limits on the capacity of its connection assets to export energy. When implemented in AWEFS, the SCADA Local Limit is used to cap the UIGF for the solar farm in the dispatch timeframe. The SCADA Local Limit excludes limits on a transmission network and distribution network (to ensure AEMO’s compliance with clause 3.7B(c)(6) of the Rules), and may exclude other limits managed by AEMO through the central dispatch process. Limits already communicated in the SCADA Cluster Inverters Available signal may be excluded from the SCADA Local Limit. Manually-applied transient limits not intended to apply at the end of the next dispatch interval may be excluded from the SCADA Local Limit. The SCADA Local Limit should not exceed the higher of the nameplate ratingand the Maximum Capacity of the solar farm. SCADA Local Limit must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Possible Power | Scalar non-negative decimal number | (0, Max Capacity) | No | 4-10 secs |  | MW |  | SCADA Possible Power is the Generator’s estimate in MW of current unconstrained intermittent generation, subject only to technical factors affecting operation of its generation and connection assets. SCADA Possible Power is used to assess the performance of unconstrained intermittent generation forecasts. SCADA Possible Power must be calculated assuming that no transmission or distribution network constraints currently apply, and may assume that other limits managed by AEMO through the central dispatch process do not apply. SCADA Possible Power must reflect any Local Limits at the solar farm, unless agreed with AEMO. The SCADA Possible Power must not exceed the Maximum Capacity of the solar farm. SCADA Possible Power must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Wind Speed | Scalar decimal number | >=0 | Yes | 4-10 secs |  | m/s |  | To be representative of the facility.
Wind Direction | Scalar decimal number (bearing) | (0,360) | Yes | 4-10 secs |  | º |  | To be representative of the facility.
Ambient Temperature | Scalar decimal number | (-50,100) | Yes | 4-10 secs |  | ºC |  | To be representative of the facility.
Relative Humidity | Scalar non-negative decimal number | (0,100) | Yes | 4-10 secs |  | % |  | To be representative of the facility.
Ends

## ECM CPV Cluster
Energy Conversion Model for concentrating PV farms | [7 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
Data Parameter | Data type | Valid range | Mandatory | Interval | Value | Units | Comments | Description
Cluster | Parameters that apply to a cluster Please copy this sheet into a separate tab for each additional cluster. |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value. |  |  | A cluster is defined as a subset of the Facility with: - the same module type (manufacturer, model and material) - the same inverter type (manufacturer, model and rating) - the same number of modules connected to each inverter - the same tracking algorithm and ranges - the same concentrator attributes - geographically close location of all modules (within an area up to 5km x 5km)
Cluster identification
Cluster Reference | Descriptive String | n/a | Yes | n/a |  | n/a |  | Unique reference for this cluster. Note, following ECM submission, AEMO will allocate a unique cluster identification to each of your clusters.
Cluster Characteristics
Technology type and Tracking | Descriptive string | n/a | Yes | n/a |  | n/a |  | The type of technology used in the cluster including information on tracking.
Cluster centre latitude | Scalar decimal number | (-90,90) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module/concentrator area of the cluster
Cluster centre longitude | Scalar decimal number | (-180,180) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module/concentrator area of the cluster
Cluster centre altitude | Scalar decimal number | (-15,2228) | Yes |  |  | meters |  | Defined at the centre of the module/concentrator area of the cluster
Number of modules in cluster | Scalar number | >0 | Yes |  |  | n/a |  | Total number of modules in this cluster
Total DC power of modules in cluster | Scalar decimal number | >0 | Yes |  |  | MW |  | The total sum DC nameplate rating of all modules in this cluster, used for cross-checking and documenting overprovisioning ratio
Number of inverters in cluster | Scalar | >0 | Yes |  |  | n/a |  | The number of inverters in this cluster
Inverter manufacturer | String | n/a | Yes |  |  | n/a |  | Manufacturer of inverters in this cluster
Inverter type reference | String | n/a | Yes |  |  | n/a |  | Manufacturer inverter type reference/model name for inverters in this cluster
Inverter DC power rating | Scalar non-negative decimal number | >0 | Yes |  |  | kW DC |  | DC power rating for inverters in this cluster. Please specify the DC power rating from the datasheet of the inverter manufacturer (max DC rating), not the DC power of the modules attached to the inverter.
Total DC power of inverters in cluster | Scalar decimal number | >0 | Yes |  |  | MW |  | The total sum DC nameplate rating of all inverters in this cluster, used for cross-checking and documenting overprovisioning ratio
Inverter AC power rating | Scalar non-negative decimal number | >0 | Yes |  |  | kW AC |  | AC power rating for inverters in this cluster
Total AC power of inverters in cluster | Scalar decimal number | >0 | Yes |  |  | MW |  | The total sum AC nameplate rating of all inverters in this cluster, used for cross-checking and documenting overprovisioning ratio
Inverter temperature rating | 2-vector (min, max) | n/a | Yes |  |  | min ºC |  | Operating temperature range of inverter as specified by manufacturer
|  | n/a | Yes |  |  | max ºC
Inverter response | 2-vector (power, efficiency) | >=0 | Yes |  |  | power: kW |  | See inverter response example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted. Please only provide a single curve.
|  | (0,1) | Yes |  |  | efficiency: n/a |  | Alternatively, 0-100%
Number of concentrators per inverter | Scalar number | >0 | Yes |  |  | n/a |  | The number of concentrators attached to each inverter
Number of concentrators in cluster | Scalar number | >0 | Yes |  |  | n/a |  | Total number of concentrators in this cluster
Module material | String | n/a | Yes |  |  | n/a |  | PV material used for all modules in this cluster Material of interest is the substance that is used to convert sunlight to electricity (e.g. monocrystalline silicon, cadmium telluride)
Concentrator manufacturer | String | n/a | Yes |  |  | n/a |  | Manufacturer of concentrators in this cluster
Concentrator model ID | String | n/a | Yes |  |  | n/a |  | Model ID for concentrators in this cluster
Concentrator technology | Descriptive string. E.g. {dish, trough, fresnel} | n/a | Yes |  |  | n/a |  | Technology of the concentrator
Concentrator concentrating factor | Scalar decimal number | n/a | Yes |  |  | n/a |  | Concentrating factor of concentrator
Concentrator aperture width | Scalar decimal number | >0 | Yes |  |  | meters |  | Aperture width of concentrator
Concentrator receiver length | Scalar decimal number | >0 | Yes |  |  | meters |  | Receiver length of concentrator
Concentrator aperture area | Scalar decimal number | >0 | Yes |  |  | m2 |  | Aperture area of concentrator
Tracking slope angle range | 2-vector (min, max) | (-90,90) | Required for tracking systems only |  |  | min degrees (º) |  | Minimum slope angle The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
|  | (-90,90) | Required for tracking systems only |  |  | max degrees (º) |  | Maximum slope angle.
Slope tracking direction | String | n/a | Required for tracking systems only |  |  | n/a |  | Direction in which slope tracking is done. Specify "north-south" if panels are tilted in the north/south direction over an east-west axis. Specify "east-west" if panels are tilted from east to west over a north-south axis. For any other angles/cases, specify the compass orientation of the tracking (see "azimuth", perpendicular to axis' compass orientation) and attach additional information on the tracking
Tracking azimuth angle range | 2-vector (min, max) | (0,360) | Required for tracking systems only |  |  | min degrees (º) |  | Minimum azimuth angle. The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc.)
|  | (0,360) | Required for tracking systems only |  |  | max degrees (º) |  | Maximum azimuth angle.
Cluster SCADA |  |  |  |  | Provision |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, maximum 15-second average update is required.
Data Parameter | Data type | Valid range | Mandatory | Inverval | Yes/No | Units | Comments | Description
Global horizontal irradiance | Scalar non-negative decimal number | (0,1415) | Yes | 4-10 secs |  | W/m2 |  | Per cluster Measured using a ISO First class pyranometer
Global inclined irradiance | Scalar non-negative decimal number | (0,1415) | Yes | 4-10 secs |  | W/m2 |  | Per cluster Same orientation of the panel Measured using a ISO First class pyranometer
Direct normal irradiance | Scalar non-negative decimal number | (0,1415) | Yes | 4-10 secs |  | W/m2 |  | Same orientation as the modules Per cluster Measured using a ISO First class pyrheliometer
Module surface temperature | Scalar decimal number | (-50,100) | Yes | 4-10 secs |  | ºC |  | Per cluster Averaged across all modules in a cluster
Number of inverters available | Scalar non-negative decimal number | >=0 | Yes | 4-10 secs |  | n/a |  | Per cluster The number of inverters that are available to deliver active power if sufficient sunlight is available
Reduction through soiling | Scalar non-negative decimal number | (0,100) | No | 4-10 secs |  | % |  | Per cluster The percentage reduction of module production caused by soiling If this parameter is measured at the facility, then it will be requested by AEMO to be provided but is optional.
Actual tracking slope angle | Scalar non-negative decimal number | (-90,90) | Required for tracking systems only | 4-10 secs |  | º |  | Per cluster For sign convention, refer to 'tracking slope angle' term in Cluster Definition Guideline tab.
Actual tracking azimuth angle | Scalar non-negative decimal number | (0,360) | Required for tracking systems only | 4-10 secs |  | º |  | Per cluster
Tracking share of modules not on track | Scalar non-negative decimal number | (0,100) | Required for tracking systems only | 4-10 secs |  | % |  | Per cluster
Trackers online | Scalar non-negative integer | >=0 | Optional for tracking systems only | 4-10 secs |  | n/a |  | Per Cluster
Module Type 1 Used In This Cluster | Parameters that apply to a module type used within a cluster (part of cluster definition) |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value.
| Data type | Valid range | Mandatory | Inverval | Value | Units | Comments | Description
Module manufacturer | String | n/a | Yes | n/a |  | n/a |  | Manufacturer of PV modules in this cluster
Module type reference | String | n/a | Yes |  |  | n/a |  | Model ID for PV modules in this cluster
Module DC power rating | Scalar decimal number | n/a | Yes |  |  | W DC |  | The power rating for each single module in this cluster at standard test conditions. Standard test conditions are defined as irradiance of 1000 W/m2 at AM 1.5 solar spectrum and temperature 25 ± 2 °C
Module surface area | Scalar number | >0 | Yes |  |  | m2 |  | Surface area of a single module
Module temperature response | 2-vector (temperature, response) | (-50,100) | No |  |  | temperature: ºC |  | See temperature response example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | response: n/a |  | Alternatively, 0-100%
Module normalised spectral response | 2-vector (wavelength, response) | (200,4000) | No |  |  | wavelength: nm |  | See the spectral response worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | response: n/a |  | Alternatively, 0-100%
Module degradation curve | 2-vector (year since installation, degradation) | >=0 | No |  |  | year since installation: n/a |  | See the degradation curve example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | degradation: n/a |  | Alternatively, 0-100%
Module annual degradation rate | Scalar number | (0,100) | No |  |  | %/year |  | Fallback if degradation curve is not supplied
Module Type 2 Used In This Cluster | Parameters that apply to a module type used within a cluster (part of cluster definition) ONLY COMPLETE IF THIS CLUSTER HAS MORE THAN 1 MODULE TYPE
Module manufacturer | String | n/a | Yes | n/a |  | n/a |  | Manufacturer of PV modules in this cluster
Module type reference | String | n/a | Yes |  |  | n/a |  | Model ID for PV modules in this cluster
Module DC power rating | Scalar decimal number | n/a | Yes |  |  | W DC |  | The power rating for each single module in this cluster at standard test conditions. Standard test conditions are defined as irradiance of 1000 W/m2 at AM 1.5 solar spectrum and temperature 25 ± 2 °C
Module surface area | Scalar number | >0 | Yes |  |  | m2 |  | Surface area of a single module
Module temperature response | 2-vector (temperature, response) | (-50,100) | No |  |  | temperature: ºC |  | See temperature response example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | response: n/a |  | Alternatively, 0-100%
Module normalised spectral response | 2-vector (wavelength, response) | (200,4000) | No |  |  | wavelength: nm |  | See the spectral response worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | response: n/a |  | Alternatively, 0-100%
Module degradation curve | 2-vector (year since installation, degradation) | >=0 | No |  |  | year since installation: n/a |  | See the degradation curve example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | degradation: n/a |  | Alternatively, 0-100%
Module annual degradation rate | Scalar number | (0,100) | No |  |  | %/year |  | Fallback if degradation curve is not supplied
Module Type 3 Used In This Cluster | Parameters that apply to a module type used within a cluster (part of cluster definition) ONLY COMPLETE IF THIS CLUSTER HAS MORE THAN 2 MODULE TYPES. ADD MORE MODULE TYPE SECTIONS IF REQUIRED.
Module manufacturer | String | n/a | Yes | n/a |  | n/a |  | Manufacturer of PV modules in this cluster
Module type reference | String | n/a | Yes |  |  | n/a |  | Manufacturer module/panel type reference/model name for modules in this cluster
Module DC power rating | Scalar decimal number | n/a | Yes |  |  | W DC |  | The power rating for each single module in this cluster at standard test conditions. Standard test conditions are defined as irradiance of 1000 W/m2 at AM 1.5 solar spectrum and temperature 25 ± 2 °C
Module surface area | Scalar number | >0 | Yes |  |  | m2 |  | Surface area of a single module
Module temperature response | Scalar number | (0,100) | No |  |  | %/K |  | % decrease of efficiency per degree.
Module normalised spectral response | 2-vector (wavelength, response) | (200,4000) | No |  |  | wavelength: nm |  | See the spectral response worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | response: n/a |  | Alternatively, 0-100%
Module degradation curve | 2-vector (year since installation, degradation) | >=0 | No |  |  | year since installation: n/a |  | See the degradation curve example worksheet. Please provide a table similar to the example. Pictures or pdf files will not be accepted.
|  | (0,1) | No |  |  | degradation: n/a |  | Alternatively, 0-100%
Module annual degradation rate | Scalar number | (0,100) | No |  |  | %/year |  | Fallback if degradation curve is not supplied
Inverter | Parameters that apply to an individual inverter COPY THIS SECTION OF THE SHEET FOR EACH INVERTER IN THE CLUSTER
Inverter ID | Descriptive string, e.g. INV_1045 | n/a | Yes | n/a |  | n/a |  | Unique ID for this inverter (may be built of cluster ID plus count)
Centre latitude of modules connected to inverter | Scalar decimal number | (-90,90) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module / concentrator area of modules connected to this inverter
Centre longitude of modules connected to inverter | Scalar decimal number | (-180,180) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module / concentrator area of modules connected to this inverter
Centre altitude of modules connected to inverter | Scalar decimal number | (-15,2228) | Yes |  |  | m ASL |  | Defined at the centre of the module / concentrator area of modules connected to this inverter
Number of modules of module type 1 connected to this inverter | integer number | >=0 | Yes |  |  | n/a |  | Please specify for each inverter
Number of modules of module type 2 connected to this inverter | integer number | >=0 | Yes |  |  | n/a |  | Please specify for each inverter, only used if more than one module type
Number of modules of module type 3 connected to this inverter | integer number | >=0 | Yes |  |  | n/a |  | Please specify for each inverter, only used if more than two module types, add more if more than three module types
DC power of modules connected to this inverter | Scalar decimal number | >0 | Yes |  |  | MW |  | The combined module DC power rating for all modules connected to this inverter
Ends

## ECM CST
Energy Conversion Model for concentrating solar-thermal farms | [7 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
Data Parameter | Data type | Valid range | Mandatory | Interval | Value | Units | Comments | Description
Farm Level | Parameters that apply to the solar farm. |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value.
Solar farm identification
Power Station name | Descriptive string | n/a | Yes | n/a |  | n/a |  | Name of the Solar farm. To be same as specified in the 'Application for Registration as a Generator in the NEM', section C.
Region | Descriptive string | n/a | Yes | n/a |  | n/a |  | Name of NEM region of the facility. To be same as specified in the 'Application for Registration as a Generator in the NEM'.
Solar farm nominal data
Nameplate Rating | Scalar decimal number | >0 | Yes | n/a |  | MW |  | The total installed capacity of the Solar Farm (MW) as outlined in the Performance Standard. This Item corresponds to "Nameplate Rating of Generating System" in section C of the "Application for Registration as a Generator in the NEM" document.
Maximum Capacity | Scalar integer number | >0 | Yes | n/a |  | MW |  | Maximum generation to which the semi-scheduled generating unit may be dispatched as outlined in the Performance Standard, rounded down to the nearest whole MW. This definition can be found in section C of the "Application for Registration as a Generator in the NEM" document. The Maximum Capacity value must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Solar farm location and terrain data
Facility latitude | Scalar decimal number | (-90,90) | Yes | n/a |  | Decimal degrees |  | Defined at the centre of the collector area
Facility longitude | Scalar decimal number | (-180,180) | Yes | n/a |  | Decimal degrees |  | Defined at the centre of the collector area
Facility altitude | Scalar decimal number | (-15,2228) | Yes | n/a |  | metres ASL |  | Defined at the centre of the collector area
Facility map | PDF / high resolution image | n/a | Yes | n/a |  | n/a |  | Terrain map file with positions of receivers, strings, measuring devices marked. Please submit as separate pdf.
Solar farm other
Number of clusters | Scalar positive integer | >0 | Yes | n/a |  | n/a |  | Number of clusters of the facility, for cross-checking
List of measurement devices (Device ID) | Descriptive string, e.g. a device type and model number e.g. "TSP-700 Pyranometer" | n/a | Yes | n/a |  | n/a |  | Please complete the measurement devices worksheet.
NSP MW Control Schemes in operation | String | n/a | n/a | Yes |  | n/a |  | Provide details of NSP MW Control Schemes used to down regulate the solar farm at solar farm and/or cluster level.
Any other restrictions | String | n/a | n/a | Yes |  | n/a |  | Provide details of any other limitations imposed on the Solar Farm. This should be consistent with information provided in Power System Design Data Sheets section 6.1.2 (tab S-6), and Data Sheets section 7.1.2 (tab S-7).
Solar farm SCADA to AEMO |  |  |  |  | Provision |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated at least every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, maximum 15-second average update is required
Data Parameter | Data type | Valid range | Mandatory | Interval | Yes/No | Units | Comments | Description
Solar Farm Active Power | Scalar decimal number | (<0, >=0) | Yes | 4-10 secs |  | MW |  | Total solar farm active power. The SCADA Solar Farm Active Power measurement must reference the agreed point of dispatch.
Control System Set-Point | Scalar non-negative decimal number | (0, 2.5 x Nameplate Rating) | Yes | 4-10 secs |  | MW |  | MW Set-Point applied in the solar farm's control system to limit (down regulate) its output. At other times when no limit applies, the set-point to be set to above the solar farm's Nameplate Rating, but below 250% of it. SCADA MW Set-Point must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Local Limit | Scalar non-negative decimal number | (0, Max Capacity) | Yes | 4-10 secs |  | MW |  | In MW, the SCADA Local Limit for a solar farm is the lower of its plant availability and all technical limits on the capacity of its connection assets to export energy. When implemented in AWEFS, the SCADA Local Limit is used to cap the UIGF for the solar farm in the dispatch timeframe. The SCADA Local Limit excludes limits on a transmission network and distribution network (to ensure AEMO’s compliance with clause 3.7B(c)(6) of the Rules), and may exclude other limits managed by AEMO through the central dispatch process. Limits already communicated in the SCADA Cluster Inverters Available signal may be excluded from the SCADA Local Limit. Manually-applied transient limits not intended to apply at the end of the next dispatch interval may be excluded from the SCADA Local Limit. The SCADA Local Limit should not exceed the higher of the nameplate ratingand the Maximum Capacity of the solar farm. SCADA Local Limit must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Possible Power | Scalar non-negative decimal number | (0, Max Capacity) | No | 4-10 secs |  | MW |  | SCADA Possible Power is the Generator’s estimate in MW of current unconstrained intermittent generation, subject only to technical factors affecting operation of its generation and connection assets. SCADA Possible Power is used to assess the performance of unconstrained intermittent generation forecasts. SCADA Possible Power must be calculated assuming that no transmission or distribution network constraints currently apply, and may assume that other limits managed by AEMO through the central dispatch process do not apply. SCADA Possible Power must reflect any Local Limits at the solar farm, unless agreed with AEMO. The SCADA Possible Power must not exceed the Maximum Capacity of the solar farm. SCADA Possible Power must reference the same measurement point as the SCADA Solar Farm Active Power signal.
Wind Speed | Scalar decimal number | >=0 | Yes | 4-10 secs |  | m/s |  | To be representative of the facility.
Wind Direction | Scalar decimal number (bearing) | (0,360) | Yes | 4-10 secs |  | º |  | To be representative of the facility.
Ambient Temperature | Scalar decimal number | (-50,100) | Yes | 4-10 secs |  | ºC |  | To be representative of the facility.
Relative Humidity | Scalar non-negative decimal number | (0,100) | Yes | 4-10 secs |  | % |  | To be representative of the facility.
Ends

## ECM CST Cluster
Energy Conversion Model for concentrating solar-thermal farms | [7 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
Data Parameter | Data type | Valid range | Mandatory | Interval | Value | Units | Comments | Description
Cluster | Parameters that apply to a cluster Please copy this sheet into a separate tab for each additional cluster. |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value. |  |  | A cluster is defined as a subset of the facility with: - the same actual turbine(s) - the same tracking algorithm and ranges - the same concentrator attributes - geographically close location of all modules (within an area up to 5km x 5km)
Cluster identification
Cluster Reference | Descriptive String | n/a | Yes | n/a |  | n/a |  | Unique reference for this cluster. Note, following ECM submission, AEMO will allocate a unique cluster identification to each of your clusters.
Cluster Characteristics
Technology type | Data type: Descriptive string | n/a | Yes | n/a |  | n/a |  | The type of solar-thermal technology used in the cluster
Cluster centre latitude | Scalar decimal number | (-90,90) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module/concentrator area of the cluster
Cluster centre longitude | Scalar decimal number | (-180,180) | Yes |  |  | Decimal degrees |  | Defined at the centre of the module/concentrator area of the cluster
Cluster centre altitude | Scalar decimal number | (-15,2228) | Yes |  |  | meters |  | Defined at the centre of the module/concentrator area of the cluster
Turbine manufacturer | String | n/a | Yes |  |  | n/a |  | Manufacturer of turbine(s) in this cluster
Turbine model ID | String | n/a | Yes |  |  | n/a |  | Model ID for turbine(s) in this cluster
Turbine AC power rating | Scalar decimal number | >0 | Yes |  |  | W AC |  | The power rating for each single turbine in this cluster
Turbine response | 2-vector (irradiance, power) | >=0 | Yes |  |  | irradiance: W/m2 |  | Concentrator and turbine response to irradiation (provide in extra sheet)
|  | (0,100) | Yes |  |  | power: kW |  | Alternatively, 0-100%
Number of steam turbines in cluster | Scalar | >0 | Yes |  |  | n/a |  | Total number of turbines in this cluster
Concentrator manufacturer | String | n/a | Yes |  |  | n/a |  | Manufacturer of concentrators in this cluster
Concentrator model ID | String | n/a | Yes |  |  | n/a |  | Model ID for concentrators in this cluster
Concentrator technology | Descriptive string. E.g. {dish, trough, fresnel} | n/a | Yes |  |  | n/a |  | Technology of the concentrator
Concentrator concentrating factor | Scalar decimal number | >0 | Yes |  |  | n/a |  | Concentrating factor of concentrator
Concentrator aperture width | Scalar decimal number | >0 | Yes |  |  | meters |  | Aperture width of concentrator
Concentrator receiver length | Scalar decimal number | >0 | Yes |  |  | meters |  | Receiver length of concentrator
Concentrator aperture area | Scalar decimal number | >0 | Yes |  |  | m2 |  | Aperture area of concentrator
Concentrating factor | Scalar decimal number | >0 | Yes |  |  | n/a
Operating temperature | 2-vector (min, max) | n/a | Yes |  |  | min ºC |  | Operational temperature range
|  | n/a | Yes |  |  | max ºC
Receiver diameter | Scalar decimal number | >0 | Yes |  |  | millimetres |  | Receiver diameter
Number of concentrators per turbine | Scalar number | >0 | Yes |  |  | n/a |  | Number of concentrators per turbine
Receiver rows distance | Scalar decimal number | >0 | Yes |  |  | meters
Optical efficiency of mirror without soiling | Scalar decimal number |  | Yes |  |  | n/a
Absorbance of receiver | Scalar decimal number |  | Yes |  |  | n/a
Emissivity of receiver | Scalar decimal number |  | Yes |  |  | n/a
Heat transfer coefficient of receiver | Scalar decimal number |  | Yes |  |  | W/m2/K
Heat transfer collection pipes | Scalar decimal number |  | Yes |  |  | W/m2/K
Rated power steam turbine | Scalar decimal number | >0 | Yes |  |  | kW
Steam turbine efficiency | 2-vector (efficiency, power) | (0,1) | Yes |  |  | Efficiency: near |  | Alternatively, 0-100%
|  | >0 | Yes |  |  | power: kW
Tracking slope angle range | 2-vector (min, max) | (-90,90) | Required for tracking systems only |  |  | min degrees |  | Minimum slope angle. The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
|  | (-90,90) | Required for tracking systems only |  |  | max degrees |  | Maximum slope angle
Slope tracking direction | String |  | Required for tracking systems only |  |  | n/a |  | Direction in which slope tracking is done. Specify "north-south" if panels are tilted in the north/south direction over an east-west axis. Specify "east-west" if panels are tilted from east to west over a north-south axis. For any other angles/cases, specify the compass orientation of the tracking (see "azimuth", perpendicular to axis' compass orientation) and attach additional information on the tracking
Tracking azimuth angle range | 2-vector (min, max) | (0,360) | Required for tracking systems only |  |  | min degrees |  | Minimum azimuth angle. The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc.)
|  | (0,360) | Required for tracking systems only |  |  | max degrees |  | Maximum azimuth angle.
Cluster SCADA |  |  |  |  | Provision |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, maximum 15-second average update is required.
Data Parameter | Data type | Valid range | Mandatory | Interval | Yes/No | Units | Comments | Description
Global horizontal irradiance | Scalar non-negative decimal number | (0,1415) | Yes | 4-10 secs |  | W/m2 |  | Per cluster Measured using a ISO First class pyranometer
Global inclined irradiance | Scalar non-negative decimal number | (0,1415) | Yes | 4-10 secs |  | W/m2 |  | Per cluster Same orientation of the panel Measured using a ISO First class pyranometer
Direct normal irradiance | Scalar non-negative decimal number | (0,1415) | Yes | 4-10 secs |  | W/m2 |  | Same orientation as the modules Per cluster Measured using a ISO First class pyrheliometer
Module receiver surface temperature | Scalar decimal number | (-50,100) | Yes | 4-10 secs |  | ºC |  | Per cluster Averaged across all modules in a cluster
Number of inverters available | Scalar non-negative decimal number | >=0 | Yes | 4-10 secs |  | n/a |  | Per cluster The number of inverters that are available to deliver active power if sufficient sunlight is available
Reduction through soiling | Scalar non-negative decimal number | (0,100) | Yes | 4-10 secs |  | % |  | Per cluster The percentage reduction of module production caused by soiling If this parameter is measured at the facility, then it will be requested by AEMO to be provided but is optional.
Actual tracking slope angle | Scalar non-negative decimal number | (-90,90) | Required for tracking systems only | 4-10 secs |  | º |  | Per cluster For sign convention, refer to 'tracking slope angle' term in Cluster Definition Guideline tab.
Actual tracking azimuth angle | Scalar non-negative decimal number | (0,360) | Required for azimuth tracking systems. | 4-10 secs |  | º |  | Per cluster
Tracking share of modules not on track | Scalar non-negative decimal number | (0,100) | Required for tracking systems only | 4-10 secs |  | % |  | Per cluster
Trackers online | Scalar non-negative integer | >=0 | Optional for tracking systems only | 4-10 secs |  | n/a |  | Per Cluster
Ends

## Spectral Response example
Spectral response (Optional) | Values outside the provided range are assumed to be zero
Module manufacturer | example
Module type reference | example module xyz-200
Wavelength (nm) | Response
300 | 0
320 | 0
340 | 0
360 | 0
380 | 0.02
400 | 0.1
420 | 0.18
440 | 0.25
460 | 0.32
480 | 0.38
500 | 0.44
520 | 0.5
540 | 0.55
560 | 0.59
580 | 0.63
600 | 0.67
620 | 0.71
640 | 0.74
660 | 0.77
680 | 0.79
700 | 0.81
720 | 0.83
740 | 0.85
760 | 0.87
780 | 0.89
800 | 0.9
820 | 0.91
840 | 0.92
860 | 0.93
880 | 0.94
900 | 0.95
920 | 0.95
940 | 0.95
960 | 0.945
980 | 0.94
1000 | 0.92
1020 | 0.88
1040 | 0.8
1060 | 0.6
1080 | 0.4
1100 | 0.255
1120 | 0.2
1140 | 0.15
1160 | 0.1
1180 | 0.05
1200 | 0.025
1220 | 0
1240 | 0
1260 | 0
1280 | 0
1300 | 0
1320 | 0

## Inverter Response example
Inverter efficiency response |  | Values outside the provided range are assumed to be zero
Inverter manufacturer | example
Inverter type reference | example inverter SB-3500LAX
Power (kW) | Response
10 | 0.3
20 | 0.5
30 | 0.8
40 | 0.95
50 | 0.979
60 | 0.9795
70 | 0.98
80 | 0.9805
90 | 0.981
100 | 0.9815
110 | 0.982
120 | 0.9825
130 | 0.983
140 | 0.9835
150 | 0.984
160 | 0.9845
170 | 0.985
180 | 0.9855
190 | 0.986
200 | 0.9865
210 | 0.986
220 | 0.9855
230 | 0.985
240 | 0.9845
250 | 0.984
260 | 0.9835
270 | 0.983
280 | 0.9825
290 | 0.982
300 | 0.9815
310 | 0.981
320 | 0.9805
330 | 0.98
340 | 0.979
350 | 0.978
360 | 0.977
370 | 0.976
380 | 0.975
390 | 0.974
400 | 0.973
410 | 0.972
420 | 0.971
430 | 0.97
440 | 0.969
450 | 0.968
460 | 0.967
470 | 0.966
480 | 0.965
490 | 0.964
500 | 0.963
510 | 0.962
520 | 0.961
530 | 0.959
540 | 0.957
550 | 0.955
560 | 0.953
570 | 0.951
580 | 0.949
590 | 0.947
600 | 0.945
610 | 0.943
620 | 0.941
630 | 0.939
640 | 0.937
650 | 0.935
660 | 0.933

## Temperature Response example
Module Temperature Response (Optional) |  | Values outside the provided range are assumed to be zero
Module manufacturer | example
Module type reference | example module xyz-200
Temperature (◦C) | DC power at STC (%)
20 | 1.02
30 | 0.98
40 | 0.94
50 | 0.9
60 | 0.86
70 | 0.82
80 | 0.78