## Capacity_Factors
Technology | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
Data type | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float
Solar PV - Single axis tracking | 29.8 | 29.9 | 30.1 | 30.2 | 30.4 | 30.5 | 30.7 | 30.8 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
Wind - onshore | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
Wind - offshore | 50.2 | 50.8 | 51.4 | 52 | 52.6 | 53.2 | 53.8 | 54.4 | 55 | 55.6 | 56.2 | 56.8 | 57.4 | 58 | 58.6 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2
Wave | 35.2 | 35.3 | 35.4 | 35.5 | 35.6 | 35.7 | 35.8 | 35.9 | 36 | 36.1 | 36.2 | 36.3 | 36.4 | 36.5 | 36.6 | 36.7 | 36.8 | 36.9 | 37 | 37.1 | 37.2 | 37.3 | 37.4 | 37.5 | 37.6 | 37.7
Tidal stream | 34.2 | 34.3 | 34.4 | 34.5 | 34.6 | 34.7 | 34.8 | 34.9 | 35 | 35.1 | 35.2 | 35.3 | 35.4 | 35.5 | 35.6 | 35.7 | 35.8 | 35.9 | 36 | 36.1 | 36.2 | 36.3 | 36.4 | 36.5 | 36.6 | 36.7

## Generation_Storages_Electrolyse
General Details | [8 empty] | Technical Parameter | [46 empty] | Economic Parameter
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Assumed unit size | Plant net power output | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical (Net) | Seasonal ratings: not summer (Net) | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation (HHV Net) | Heat rate at maximum operation (HHV Net) | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs $ | Carbon storage costs | Carbon transportation costs | Disposal costs | Recycling cost | Fixed operating cost | Extended warranties | Variable operating cost
|  |  |  | MW | MW | MW | MW | MW | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/h | MW/h | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | tpd |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km |  |  | $/MW Net/year | $/MW Net/year | $/MWh Net
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float
CCGT - With CCS (90%) | Thermal | Natural Gas | 2024 | 351.5 | 319.3 |  | 301.5 | 334.5 | 40 | 25 | 3 | 1.75 | 104 | 46% | 9.2% | [8 empty] | 3.5% |  | 12.8 |  | 1320 | 1320 | 9.177 | 8.208 |  | 43.9% | [11 empty] | 0.02 | [10 empty] | 5576 |  |  | 1699623133 | 1852589215 | 585009652 | 21200000 | 1600000 | 152966082 | 250718422 | 863895058 | 18.5 | 0.11 |  |  | 22542 |  | 8
CCGT - With CCS (50%) | Thermal | Natural Gas | 2024 | 364.7 | 338.1 |  | 318.8 | 354 | 40 | 25 | 3 | 1.75 | 104 | 46% | 7.3% | [8 empty] | 3.5% |  | 12.8 |  | 1320 | 1320 | 8.595 | 7.753 |  | 46.4% | [22 empty] | 4756 |  |  | 1534788803 | 1672919795 | 585009652 | 21200000 | 1600000 | 138130992 | 250718422 | 699060729 | 18.5 | 0.1075 |  |  | 19955 |  | 6.7
CCGT - Without CCS | Thermal | Natural Gas | 2024 | 380 | 371 |  | 348 | 389 | 40 | 25 | 2.5 | 1.75 | 78 | 46% | 2.5% | [8 empty] | 3.5% |  | 12.8 |  | 1320 | 1320 | 8.271 | 7.068 |  | 50.9% | [22 empty] | 2360 |  |  | 835728075 | 910943602 | 585009652 | 21200000 | 1600000 | 75215527 | 250718422 | [5 empty] | 15028 |  | 4.1
OCGT - Without CCS, Small unit size, hydrogen ready (35%) | Thermal | Natural Gas/Diesel | 2024 | 196.5 | 193.6 |  | 188.1 | 199 | 40 | 25 | 2 | 2 | 78 | 50% | 1.5% | [8 empty] | 2% |  | 5 |  | 5220 | 5220 | 14.629 | 10.489 |  | 34.3% |  |  | 2048 | [19 empty] | 2193 |  |  | 430943200 | 469728088 | 301660240 | 21200000 | 1600000 | 38784888 | 129282960 | [5 empty] | 17368 |  | 16.1
OCGT - Without CCS, Large unit size, hydrogen ready (5%) | Thermal | Natural Gas/Diesel | 2024 | 244.3 | 241.7 |  | 226.4 | 258.2 | 40 | 25 | 2 | 2 | 58 | 50% | 1.1% | [8 empty] | 2% |  | 5 |  | 1320 | 1320 | 16.312 | 10.811 |  | 33.3% |  |  | 276 | [19 empty] | 1189 |  |  | 290479200 | 316622328 | 203335440 | 21200000 | 1600000 | 26143128 | 87143760 | [5 empty] | 14066 |  | 8.1
Reciprocating Internal Combustion Engines, hydrogen ready (25%) | Thermal | Natural Gas/Diesel | 2024 | 211.2 | 209.1 |  | 209.1 | 209.1 | 40 | 25 | 2 | 1.25 | 52 | 40% | 1% | [8 empty] | 2% |  | 2.7 |  | 2160 | 2160 | 11.356 | 8.79 |  | 40.9% |  |  | 1237 | [19 empty] | 1900 |  |  | 397290000 | 433046100 | 238374000 | 21200000 | 1600000 | 35756100 | 158916000 | [5 empty] | 29383 |  | 8.51
Advanced Ultra Supercritical PC - Black coal with CCS (90% capture) | Thermal | Black Coal | 2024 | 700 | 577.3 |  | 566.7 | 581.7 | 50 | 30 | 4 | 2 | 104 | 30% | 17.5% | [8 empty] | 4% |  | 10.5 |  | 1200 | 1200 | 11.644 | 11.986 |  | 30.03% | [22 empty] | 10219 |  |  | 5899518000 | 7079421000 | 1350924000 |  | 2279000 | 1179903000 | 2026386000 | 2522208000 | 18.5 | 0.1075 |  |  | 94838 |  | 8.85
Advanced Ultra Supercritical PC - Black coal with CCS (50% capture) | Thermal | Black Coal | 2024 | 700 | 612.3 |  | 599.9 | 616.3 | 50 | 30 | 4 | 2 | 104 | 30% | 12.5% | [8 empty] | 4% |  | 10.5 |  | 1200 | 1200 | 10.108 | 9.891 |  | 36.39% | [22 empty] | 8211 |  |  | 5027478000 | 6032973000 | 1350924000 |  | 2279000 | 1005495000 | 2026386000 | 1650168000 | 18.5 | 0.1075 |  |  | 84720 |  | 7.43
Advanced Ultra Supercritical PC - Black coal without CCS | Thermal | Black Coal | 2024 | 700 | 671.3 |  | 658.6 | 673.8 | 50 | 30 | 4 | 2 | 104 | 30% | 4.1% | [8 empty] | 4% |  | 10.5 |  | 1200 | 1200 | 10.172 | 8.548 |  | 42.12% | [22 empty] | 5031 |  |  | 3377310000 | 4052772000 | 1350924000 |  | 2279000 | 675462000 | 2026386000 | [5 empty] | 64851 |  | 4.68
Conventional hydro | Conventional hydro | N/A | 2024 | 100 | 99 |  | 99 | 99 | 90 | 40 | 3 | 1.5 | 125 | 40% | 1% | [8 empty] | 1.5% |  | 7 |  | 10000 | 10000 |  |  |  | 90% | [23 empty] | 5250 |  | 525000000 | 577500000 | 105000000 |  |  | 52500000 | 420000000 | [5 empty] | 105000
Pumped hydroelectric storage (10 hr) | Storage | N/A | 2024 | 500 | 495 |  | 495 | 495 | 90 | 40 | 4 | 2 | 125 | 40% | 1% | [8 empty] | 1.5% |  | 11 |  | 10000 | 10000 |  |  |  | 77.5% | [12 empty] | 550 | 77.5 | [9 empty] | 7000 |  | 3500000000 | 3800000000 | 525000000 |  |  | 300000000 | 2975000000 | [5 empty] | 95000
Pumped hydroelectric storage (24 hr) | Storage | N/A | 2024 | 2000 | 1980 |  | 1980 | 1980 | 90 | 40 | 4 | 2 | 200 | 40% | 1% | [8 empty] | 1.5% |  | 11 |  | 10000 | 10000 |  |  |  | 77.5% | [12 empty] | 2200 | 77.5 | [9 empty] | 5775 |  | 11550000000 | 12862500000 | 1837500000 |  |  | 1312500000 | 9712500000 | [5 empty] | 73500
Pumped hydroelectric storage (48 hr) | Storage | N/A | 2024 | 2000 | 1980 |  | 1980 | 1980 | 90 | 40 | 4 | 2 | 200 | 40% | 1% | [8 empty] | 1.5% |  | 11 |  | 10000 | 10000 |  |  |  | 77.5% | [12 empty] | 2200 | 77.5 | [9 empty] | 6825 |  | 13650000000 | 15487500000 | 2100000000 |  |  | 1837500000 | 11550000000 | [5 empty] | 84000
Large Scale Li-ion Battery Storage (1hr) | Storage | N/A | 2024 | 200 | 198.3 |  | 198.3 | 198.3 | 20 | 20 | 1.5 | 1 | 44 |  | 0.85% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 84% | [14 empty] | 92% | 92% | 100% | 0% | 7300 | 100% |  |  | 526 |  | 326 | 170500000 | 180500000 | 141300000 |  |  | 10000000 | 29200000 | [5 empty] | 5400 | 3600
Large Scale Li-ion Battery Storage (2hr) | Storage | N/A | 2024 | 200 | 198.1 |  | 198.1 | 198.1 | 20 | 20 | 1.5 | 1.2 | 52 |  | 0.95% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 84% | [14 empty] | 92% | 92% | 100% | 0% | 7300 | 100% |  |  | 526 |  | 314 | 230800000 | 240800000 | 191300000 |  |  | 10000000 | 39500000 | [5 empty] | 8000 | 5300
Large Scale Li ion Battery Storage (4hr) | Storage | N/A | 2024 | 200 | 197.6 |  | 197.6 | 197.6 | 20 | 20 | 1.5 | 1.4 | 60 |  | 1.2% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 85% | [14 empty] | 92.5% | 92.5% | 100% | 0% | 7300 | 100% |  |  | 525 |  | 274 | 324100000 | 334100000 | 268600000 |  |  | 10000000 | 55500000 | [5 empty] | 12800 | 8400
Large Scale Li ion Battery Storage (8hr) | Storage | N/A | 2024 | 200 | 196.5 |  | 196.5 | 196.5 | 20 | 20 | 1.5 | 1.6 | 68 |  | 1.75% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 85% | [14 empty] | 93% | 93% | 100% | 0% | 7300 | 100% |  |  | 522 |  | 266 | 530000000 | 540000000 | 439300000 |  |  | 10000000 | 90700000 | [5 empty] | 22500 | 14800
Large Scale Flow Battery Storage (24hr) | Storage | N/A | 2024 | 200 | 188 |  | 188 | 188 | 25 | 25 | 2 | 1.5 | 78 |  | 6% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 62% | [14 empty] | 81% | 81% | 100% | 0% | 13500 |  |  |  | 2936 |  | 290 | 1981000000 | 1996000000 | 1624000000 |  |  | 15000000 | 357000000 | [5 empty] | 510000
Large Scale Flow Battery Storage (48hr) | Storage | N/A | 2024 | 200 | 188 |  | 188 | 188 | 25 | 25 | 2 | 2 | 104 |  | 6% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 62% | [14 empty] | 81% | 81% | 100% | 0% |  |  |  |  | 2936 |  | 290 | 3375000000 | 3390000000 | 2767000000 |  |  | 15000000 | 608000000 | [5 empty] | 79000
Large Scale Battery Storage (1hr) for hybrid generation | Storage | N/A | 2024 | 200 | 198.3 |  | 198.3 | 198.3 | 20 | 20 | 2 | 1 | 44 |  | 0.85% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 84% | [14 empty] | 92% | 92% | 100% | 0% | 7300 | 100% |  |  | 471 |  | 326 | 159300000 | 169300000 | 13200000 |  |  | 10000000 | 27300000 | [5 empty] | 5400 | 3600
Large Scale Battery Storage (2hr) for hybrid generation | Storage | N/A | 2024 | 200 | 198.1 |  | 198.1 | 198.1 | 20 | 20 | 2 | 1.2 | 52 |  | 0.95% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 84% | [14 empty] | 92% | 92% | 100% | 0% | 7300 | 100% |  |  | 471 |  | 314 | 219700000 | 229700000 | 182100000 |  |  | 10000000 | 37600000 | [5 empty] | 8000 | 5300
Large Scale Battery Storage (4hr) for hybrid generation | Storage | N/A | 2024 | 200 | 197.6 |  | 197.6 | 197.6 | 20 | 20 | 2 | 1.4 | 60 |  | 1.2% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 85% | [14 empty] | 92.5% | 92.5% | 100% | 0% | 7300 | 100% |  |  | 471 |  | 274 | 313300000 | 323300000 | 259700000 |  |  | 10000000 | 53600000 | [5 empty] | 12800 | 8400
Large Scale Battery Storage (8hr) for hybrid generation | Storage | N/A | 2024 | 200 | 196.5 |  | 196.5 | 196.5 | 20 | 20 | 2 | 1.6 | 68 |  | 1.75% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 85% | [14 empty] | 93% | 93% | 100% | 0% | 7300 | 100% |  |  | 471 |  | 266 | 519700000 | 529700000 | 430800000 |  |  | 10000000 | 88900000 | [5 empty] | 22500 | 14800
Large Scale Battery Storage (24hr) for hybrid generation (VRB) | Storage | N/A | 2024 | 200 | 188 |  | 188 | 188 | 25 | 25 | 2 | 1.5 | 78 |  | 6% | [8 empty] | 2.25% |  |  |  | 600000 | 600000 |  |  |  | 62% | [14 empty] | 81% | 81% | 100% | 0% | 18000 | 100% |  |  | 2876 |  | 290 | 1969000000 | 1984000000 | 1615000000 |  |  | 15000000 | 354000000 | [5 empty] | 51000
Large Scale Battery Storage (48hr) for hybrid generation (VRB) | Storage | N/A | 2024 | 200 | 188 |  | 188 | 188 | 25 | 25 | 2 | 2 | 104 |  | 6% | [8 empty] | 2.25% |  |  |  | 600000 | 600000 |  |  |  | 62% | [14 empty] | 81% | 81% | 100% | 0% | 18000 | 100% |  |  | 2876 |  | 290 | 3363000000 | 3378000000 | 2757000000 |  |  | 15000000 | 6706000000 | [5 empty] | 79000
Residential Battery Storage (2hr) | Storage | N/A | 2024 | 0.005 | 0.00495 |  | 0.00495 | 0.00495 | 10 | 10 | 0.24641 |  |  |  | 1% | [8 empty] | 4.3% |  |  |  | 600000 | 600000 |  |  |  | 90% | [14 empty] | 95% | 95% | 100% | 0% | 3653 | 100% | [5 empty] | 13500 |  | 10800 |  |  |  | 2700
Compressed Air Energy Storage (24 hr cavern storage) | Storage | N/A | 2024 | 200 | 200 |  | 200 | 200 | 40 | 30 | 2.5 | 1 | 104 |  | 0% | [8 empty] | 2% |  |  |  | 3000 | 3000 |  |  |  | 62.5% | [16 empty] | 100% | 0% | 20000 |  |  |  | 1935 |  | 228 | 1480000000 | 1517023000 | 1037000000 |  |  | 37023000 | 444300000 | [5 empty] | 36570 |  | 4.45
Compressed Air Energy Storage (12 hr vessel storage) | Storage | N/A | 2024 | 50 | 50 |  | 50 | 50 | 40 | 30 | 2.5 | 1 | 104 |  | 0% | [8 empty] | 2% |  |  |  | 3000 | 3000 |  |  |  | 62.5% | [16 empty] | 100% | 0% | 20000 |  |  |  | 1935 |  | 740 | 541000000 | 554528000 | 378800000 |  |  | 13528000 | 162300000 | [5 empty] | 36570 |  | 4.45
Wave | Renewable | N/A | 2024 | 2 | 1.94 |  | 1.94 | 1.94 | 20 | 20 | 5 | 1 | 52 | 0% | 3% | [8 empty] | 20% | [32 empty] | 14670 |  | 29340000 | 30161520 | 23472000 |  |  | 821520 | 5868000 | [5 empty] | 520000 |  | -
Tidal Stream | Renewable | N/A | 2024 | 2 | 1.94 |  | 1.94 | 1.94 | 20 | 20 | 4.5 | 1 | 52 | 0% | 3% | [8 empty] | 5% | [32 empty] | 12190 |  | 24380000 | 25180000 | 19504000 |  |  | 800000 | 4876000 | [5 empty] | 487600 |  | -
Solar PV - Single axis tracking | Renewable | N/A | 2024 | 200 | 200 |  | 200 | 140 | 30 | 30 | 2.5 | 1 | 26 | 0% | 2.9% | [8 empty] | 1.5% | 52 | [30 empty] | 1150 |  |  | 276000000 | 292560000 | 165600000 |  |  | 16560000 | 110400000 | [5 empty] | 12000
Solar Thermal Central Receiver with storage (16hr) | Renewable | N/A | 2024 | 150 | 140 |  | 140 | 140 | 40 | 30 | 2.5 | 1.75 | 91 | 20% | 6.7% | [8 empty] | 3% |  | 7 |  | 360 | 360 | [27 empty] | 6104 |  | 915655000 | 947655000 | 686742000 |  |  | 32000000 | 228914000 | [5 empty] | 122087
Wind - onshore | Renewable | N/A | 2024 | 620 | 601.4 |  | 601.4 | 601.4 | 30 | 25 | 4 | 1 | 90 | 0% | 3% | [8 empty] | 2.5% | [29 empty] | 6.2 | 100 |  | 3170 |  | 1966000000 | 2015150000 | 1418250000 |  |  | 49150000 | 547750000 | [5 empty] | 28000 |  | -
Wind - offshore (Fixed) | Renewable | N/A | 2024 | 1200 | 1152 |  | 1152 | 1152 | 30 | 25 | 7 | 3 | 156 | 0% | 4% | [8 empty] | 5% | [29 empty] | 12 | 100 |  | 4306 |  | 5167680000 | 5426064000 | 3514022400 |  |  | 258384000 | 1395273600 | [5 empty] | 174573 |  | -
Wind - offshore (Floating) | Renewable | N/A | 2024 | 432 | 415 |  | 415 | 415 | 30 | 25 | 7 | 3 | 156 | 0% | 4% | [8 empty] | 5% | [29 empty] | 12 | 36 |  | 7724 |  | 3336681600 | 3470148864 | 2836179360 |  |  | 133467264 | 367034976 | [5 empty] | 247297
Waste to Energy | Waste to Energy | Municipal waste | 2024 | 30 | 26.4 |  | 25.7 | 26.8 | 50 | 30 | 3.5 | 1.75 | 65 | 40% | 12% | [8 empty] | 4% |  | 22.8 |  | 72 | 72 | 19.94 | 15.388 |  | 23.4% | [22 empty] | 25512 |  |  | 673542000 | 734160000 | 404125000 |  |  | 60618000 | 269417000 | [5 empty] | 235556 |  | 13.79
Fuel cells - small | Renewable | Renewable Hydrogen | 2024 | 0.108 | 0.108 |  | 0.108 | 0.108 | 20 | 8 | 1 | 0.75 | 13 | 10% | 10% | [8 empty] | 2% |  |  |  | 55.56 | 55.56 | 7.1 | 11.36 |  | 31.6% |  |  | 8.64 | [20 empty] | 14300 |  | 1716000 | 2060000 | 1372800 |  |  | 344000 | 343200 | [5 empty] | 572000 |  | -
Fuel cells - large | Renewable | Renewable Hydrogen | 2024 | 1.08 | 1.08 |  | 1.08 | 1.08 | 20 | 8 | 1 | 0.75 | 20 | 10% | 10% | [8 empty] | 2% |  |  |  | 555 | 555 | 7.1 | 11.36 |  | 31.6% |  |  | 86.4 | [20 empty] | 6600 |  | 7920000 | 8712000 | 6336000 |  |  | 792000 | 1584000 | [5 empty] | 264000 |  | -
Electrolysers - Proton Exchange Membrane | Storage | Renewable Hydrogen | 2024 | 500 | 500 |  | 500 | 500 | 25 | 10 | 2.5 | 2 | 26 | 10% | 5% | [8 empty] | 3% |  | 15 |  | 180000 | 180000 |  |  |  | 65.7% |  | 8350 | [21 empty] | 2630 |  | 1315000000 | 1420200000 | 531000000 |  |  | 105200000 | 784000000 | [5 empty] | 52600 |  | -
Electrolysers - Alkaline | Storage | Renewable Hydrogen | 2024 | 500 | 500 |  | 500 | 500 | 25 | 10 | 2.5 | 2 | 26 | 10% | 5% | [8 empty] | 3% |  | 15 |  | 6000 | 6000 | N/A | N/A |  | 71.7% |  | 9100 | [21 empty] | 2460 |  | 1230000000 | 1353000000 | 455000000 |  |  | 123000000 | 775000000 | [5 empty] | 49200 |  | -
List to be continued by Consultant

## SMR_&_Liquefaction_Plant
Technology | Description | Plant capacity | Water consumption | Capex rate: kW | Capex rate: kg | Capex | Development cost | Construction cost | Opex - power cost | Opex - operation and maintenance cost | Hydrogen source | Co2 emissions | Gas consumption | Electric power consumption | Opex incl natural gas cost | Storage temperature | Boil off losses /day
|  | T-H2/d | kg/kg H2 | $/kW-H2 | $/kg H2/yr | $ | % | % | $/year | $/kg H2 |  | kg-CO2/kg-H2 | GJ/d | kWh/kg-H2 | $/year | degC | Losses/day (%)
str | str | int | float | float | float | float | float | float | float | float | str | float | float | float | float | float | float
SMR | Hydrogen generation by Steam Methane Reforming | 900 | 6.3 | 1459.5 |  | 2100000000 |  |  | 793346400 |  | Natural Gas (biogas possible) | 8.5
SMR with CCS | Hydrogen generation by SMR with Carbon Capture and Storage | 900 | 6.3 | 2667 |  | 2835000000 |  |  | 901530000 |  | Natural Gas (biogas possible) | 2
Liquefaction Plant & Storage | Hydrogen Liquefaction by cooling to cryogenic temperatures | 27 |  |  | 20.58 | 203700000 |  |  | 23373000 | 2.142 | SMR / Electrolysis |  |  | 12 |  | -252 | 0.1%

## Ammonia_Facility
Technology | Description | Daily ammonia production (tpd) | Energy consumption | Hydrogen consumption | Water consumption | Annual ammonia output | Stream days | Capex | Opex
|  | tpd | MWh/t(ammonia) | kg (H2)/t(NH3) | m3/t(NH3) | tpa |  | $M | $M/year
str | str | float | float | float | float | float | int | float | float
Ammonia Facility | Haber-Bosch process, with air separation unit for nitrogen supply, cooling tower, and steam turbine generator for waste heat recovery | 1000 | 1.15 | 180 | 0.6 | 350000 | 350 | 800 | 12

## Water_Treatment
Technology | Description | Source water | Plant capacity | Demineralised water produced | Potable water produced | Wastewater - membrane backwash and cleaning | Wastewater - brine production | Recovery ratio | Power consumption: with energy recovery | Power consumption: without energy recovery | Capex rate | Capex | Development cost | Construction cost | Opex - chemical cost | Opex - labour cost | Opex - power cost | Opex - operation and maintenance cost
|  |  | m3/d | m3/d | m3/d | m3/d | m3/d | % | kWh/m3 feed water | kWh/m3 feed water | $/ML/year feed water | $ | % | % | $/year | $/year | $/year | $/year
str | str | str | int | int | int | int | int | float | int | int | float | float | float | float | float | float | float | float
Demineralisation plant | Using potable water to produce highly purified water for hydrogen production for a 10 MW electrolyser | Potable water | 70 | 60.5 |  | 0 | 9.5 | 86 |  | 22.5 | 52837.5734 | 1450000 | 10 | 90 | 1950 | 35000 | 8250 | 21750
Desalination plant (large scale) | Full-scale desalination for 100,000 ML/year plant to produce potable water with a recovery ratio of 0.4 | Seawater | 273972.6027 |  | 109589.0411 | 0 | 164383.5616 | 40 | 3.75 | 10.5 | 22000 | 2200000000 | 20 | 80 | 8800000 | 8800000 | 22000000 | 13000000

## Hydrogen_Storage
Technology | Description | Cavern volume | Maximum storage capacity | Mean depth | Working capacity | Gas cycling requirements | Operating pressure | Operating temperature | Energy consumption | Capex, engineering | Capex, below ground | Capex, leaching and brine disposal | Capex, above ground | Opex
|  | m3 | tonne | m | m3 | cycles/year | bar | deg C | MWh/tonne | $M | $M | $M | $M | $M/year
str | str | int | int | int | int | int | int | float | float | float | float | float | float | float
Hydrogen storage (geological) | Salt cavern that reflects operating conditions of existing projects in the UK and USA | 300000 | 2200 | 1000 | 210000 | 10 | 100 | 35 | 1.2 | 8.5 | 46.5 | 8 | 26 | 1.6

## Biogas Digestors
General Details | [8 empty] | Technical Parameter | [46 empty] | Economic Parameter
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Assumed unit size | Plant net power output | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical | Seasonal ratings: not summer | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation | Heat rate at maximum operation | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs | Carbon storage costs | Carbon transportation costs | Disposal costs | Recycling cost | Fixed operating cost | Extended warranties | Variable operating cost
|  |  |  | NmÂ³/h | MW | MW | MW | MW | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/h | MW/h | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | NmÂ³/year |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km |  |  | $/MW Net/year | $/MW Net/year | $/MWh Net
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float
Biogas digestors | Anaerobic digestion of organic feedstocks | Agricultural residues, energy crops, food waste, manures, sewage, MSW | 2024 | 900 | 2 |  | 2 | 2 | 30 | 25 | 2 | 1 | 52 | 20% | 10% | [10 empty] | 15 | [16 empty] | 7560000 | [12 empty] | 14560 | 16000 |  | 29120000 | 32032000 | 11648000 |  |  | 2912000 | 17472000 | [5 empty] | 416000 |  | 72.8

## Biodiesel Production
General Details | [8 empty] | Technical Parameter | [46 empty] | Economic Parameter
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Assumed unit size | Plant net power output | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical | Seasonal ratings: not summer | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation | Heat rate at maximum operation | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs | Carbon storage costs | Carbon transportation costs | Disposal costs | Recycling cost | Fixed operating cost | Extended warranties | Variable operating cost
|  |  |  | ML/year | ML/year | ML/year | ML/year | ML/year | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/h | MW/h | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | tpd |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km |  |  | $/ML/year | $/MW Net/year | $/ML/year
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float
Biodiesel production | Renewable Biofuel Production | Vegetable Oils from soybean, sunflower or safflower, Used Cooking Oil (UCO), Tallow, etc | 2024 | 50 | 50 |  | 50 | 50 | 30 | 25 | 2 | 2 | 52 | 20% | 5% | [10 empty] | 65 | [32 empty] | 60000000 | 66000000 | 24000000 |  |  | 6000000 | 36000000 | [5 empty] | 312000 |  | 832000

## Biomass Generation
General Details | [12 empty] | Technical Parameter | [46 empty] | Economic Parameter
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Assumed unit size (Electrical) | Assumed unit size (thermal) | Plant net power output (Electrical) | Plant net power output (thermal) | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical (Electrical) | Seasonal ratings: summer typical (thermal) | Seasonal ratings: not summer (Electrical) | Seasonal ratings: not summer (thermal) | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation | Heat rate at maximum operation | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net (Electrical) | Total capex: net (Electrical plus thermal0) | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs | Carbon storage costs | Carbon transportation costs | Disposal costs | Recycling cost | Fixed operating cost | Extended warranties | Variable operating cost
|  |  |  | MW | MW | MW | MW | MW | MW | MW | MW | MW | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/h | MW/h | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | tpd |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km |  |  | $/MW Net/year | $/MW Net/year | $/MWh Net
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float
Biomass Generation - Electricity and steam | Thermal (renewable) | Woodchip | 2024 | 30 | 44.2 | 27.8 | 44.2 |  | 27.4 | 44.2 | 28 | 44.2 | 50 | 30 | 3 | 1.75 | 65 | 40% | 7.3% | [8 empty] | 4% |  | 22.8 |  | 72 | 72 | 18.092 | 16.255 |  | 22.15% | 57.4% | [21 empty] | 8180 | 3156 |  |  | 227404000 | 247870378 | 136442000 |  |  | 20466378 | 90961000 | [5 empty] | 184085 |  | 10.74