## Mid Size PV BESS
General Details | [8 empty] | Technical Parameter | [46 empty] | Economic Parameter
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Assumed unit size | Plant net power output | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical (Net) | Seasonal ratings: not summer (Net) | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation (HHV Net) | Heat rate at maximum operation (HHV Net) | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs $ | Carbon storage costs | Carbon transportation costs | Disposal costs | Recycling cost | Fixed operating cost | Extended warranties | Variable operating cost
|  |  |  | MW | MW | MW | MW | MW | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/h | MW/h | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | tpd |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km |  |  | $/MW Net/year | $/MW Net/year | $/MWh Net
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float
Mid Size BESS 40 MW (2hr) | Storage | N/A | 2024 | 40 | 39.62 |  | 39.62 | 39.62 | 20 | 20 | 1.5 | 0.5 | 52 |  | 0.95% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 84% | [14 empty] | 92% | 92% | 100% | 0% | 7300 | 100% |  |  | 516 |  | 344 | 48200000 | 50200000 | 40000000 |  |  | 2000000 | 8100000 | [5 empty] | 8500 | 2570
Mid Size BESS 20 MW (2hr) | Storage | N/A | 2024 | 20 | 19.72 |  | 19.72 | 19.72 | 20 | 20 | 1.5 | 0.5 | 52 |  | 0.95% | [8 empty] | 1.5% |  |  |  | 600000 | 600000 |  |  |  | 84% | [14 empty] | 92% | 92% | 100% | 0% | 7300 | 100% |  |  | 567 |  | 378 | 26400000 | 27500000 | 22000000 |  |  | 1100000 | 4400000 | [5 empty] | 8800 | 2840
Mid Size BESS 4.99 MW (2hr) | Storage | N/A | 2024 | 4.99 | 4.94 |  | 4.94 | 4.94 | 20 | 20 | 0.5 | 0.5 | 52 |  | 0.95% | [8 empty] | 2% |  |  |  | 600000 | 600000 |  |  |  | 84% | [14 empty] | 92% | 92% | 100% | 0% | 7300 | 100% |  |  | 588 |  | 392 | 6900000 | 7150000 | 5100000 |  |  | 250000 | 1800000 | [5 empty] | 9400 | 6500
Community BESS (250kW) | Storage | N/A | 2024 | 0.25 | 0.25 |  | 0.25 | 0.25 | 15 | 15 | 0.5 | 0.25 | 26 |  | 0.94% | [8 empty] | 4% |  |  |  | 600000 | 600000 |  |  |  | 84% | [14 empty] | 92% | 92% | 100% | 0% | 7300 | 100% |  |  | 1319 |  | 879 | 770000 |  | 530000 |  |  |  | 240000 | [5 empty] | 47000 | 40000
Solar PV 40MW Ground-mount | Renewable | N/A | 2024 | 40 | 40 |  | 40 | 30 | 30 | 30 | 1.5 | 0.5 | 26 | 0% | 2.9% | [8 empty] | 1.5% | 52 | [30 empty] | 1300 |  |  | 67600000 | 71656000 | 40560000 |  |  | 4056000 | 27040000 | [5 empty] | 12000
Solar PV 20MW Ground-mount | Renewable | N/A | 2024 | 20 | 20 |  | 20 | 15 | 30 | 30 | 1.5 | 0.5 | 26 |  | 2.9% | [8 empty] | 1.5% | 52 | [30 empty] | 1450 |  |  | 37700000 | 39962000 | 22620000 |  |  | 2262000 | 15080000 | [5 empty] | 12000
Solar PV 4.99MW Ground-mount | Renewable | N/A | 2024 | 4.99 | 4.99 |  | 4.99 | 3.49 | 30 | 30 | 1 | 0.25 | 12 |  | 2.9% | [8 empty] | 1.5% | 52 | [30 empty] | 1600 |  |  | 11976000 | 12694560 | 7185600 |  |  | 718560 | 4790400 | [5 empty] | 13360
Solar PV 1MW rooftop | Renewable | N/A | 2024 | 1 | 1 |  | 1 | 0.75 | 25 | 25 | 0.5 | 0.25 | 12 |  | 2.9% | [8 empty] | 1.5% | 52 | [30 empty] | 1300 |  |  | 1560000 |  | 936000 |  |  |  | 624000 | [5 empty] | 15000
List to be continued by Consultant