## Data_BuildingBlock
Release Date | Version Number
2025-05-14 | 1 | [6 empty] | FOR NATUAL GAS ONLY | FOR NATUAL GAS ONLY | FOR NATUAL GAS ONLY | FOR NATUAL GAS ONLY
Building Block ID | Category | Subcategory | Detail | Description | Notes | Unit | Initial Capital Cost | Yearly Operating Cost | Cost of Capacity Upgrade | Cost of Refurbishment | Decommissioning Cost | calculated increase - 83% across AC lines | calculated increase - 83% across all AC cables
1 | Natural gas | Gas pipelines | Buried pipeline |  |  |  | $3,000/mm km ($75,000/inch km) this is for typical gas pipelines greater than 100km. Sizing basis provided in report | Percentage of capex (net of compression) $9,000/km to $29,000/km | Partially looped pipelines are 17% higher than a new pipeline construction ($3,627/mm km) Capacity increase assumed as = (loop length/oringal pipeline length) x orignal pipeline length Pipeline change of service to natural gas is 10% to 30% of cost of new equivalent pipeline system | $250,000/km for recoating of pipelines | $197/mm km ($5000/inch km)
2 | Natural gas | Gas pipelines | Pipeline stations |  | Excludes compression |  | $5,600,000 for a 100TJ/d flow. For facilities of different sizes use a 0.6 scaling factor using the scaling relationship | Not applicable as pipeline cost is all inclusive | Proportion of flow increase multiplied by the cost base from Initial Capital Cost | 10% of capital cost of new facility. $560,000 for a 100TJ/d flow | Covered in cost for pipeline
3 | Natural gas | Production plant - Conventional gas | Key elements: gas liquids separation, gas stripping (contaminants), gas fractionation (LPGs), gas dehydration, gas compression |  | Covers "tight gas" as well, such as Beetaloo sub-basin |  | $235,000,000 for a 200TJ/d facility. For facilities of different sizes use a 0.6 scaling factor using the scaling relationship | 12% of CAPEX which includes sustaining capital costs. $2,820,000 per year for a 200TJ/d facility | Proportion of flow increase multiplied by the cost base from Initial Capital Cost, plus a 30% increase applied to additional capacity. | 10% of capital cost of new facility | $16,000,000 for a 50TJ facility
4 | Natural gas | Production plant - Coal Seam Gas | Key elements: gas liquids separation, gas dehydration, gas compression |  |  |  | $38,000,000 for a 32 TJ/d facility. For facilities of different sizes use a 0.5 scaling factor using the scaling relationship | 8% of CAPEX which includes sustaining capital costs. $1,880,000 per year for a 32 TJ/d facility | Proportion of flow increase multiplied by the cost base from Initial Capital Cost, plus a 30% increase applied to additional capacity. | 5% of capital cost of new facility | $8,000,000 for a 50TJ facility
5 | Natural gas | Compression facility |  |  | Assumed as pipeline compression only, not for gas process or gas storage facilities |  | CAPEX cost for a compressor station ranges from $3,000,000/MW to $6,400,000/MW of compressor power. Nominal compressor station cost $24,000,000 for a 1.85 MW comporessor unit station on a DN250 pipeline $45,000,000 for a 3.5 MW comporessor unit station on a DN300 to DN400 pipeline $73,000,000 for a 5.7 MW comporessor unit station on a DN450 to DN600 pipeline Compressor station flow reversal 10% of the cost of a new facility of the same capacity | New facility - 4% of capital costs plus 9% of capital cost every 10 years for sustaining capital. Existing facility - $37,000/MW to $45,000/MW of compression power. | $3,000,000/MW | 7.5% of capital cost of new facility | $3,000,000 to $4,000,000 per facility
6 | Natural gas | Storage - Underground (depleted reservoir) | Key elements: gas liquids separation, gas stripping (contaminants), gas fractionation (LPGs), gas dehydration, gas compression |  |  |  | Storage well: $5,000,000. Gathering Line: $1,000,000. Compression and Conditioning Facilities: $1,000,000/TJ to $1,250,000/TJ, for a 100-150TJ/d facility. $600,000/TJ to $800,000/TJ, for a 200-250TJ/d facility. Metering Station: $5,000,000 to $7,500,000. Pipelines: $600,000/km to $900,000/km for typical class 600 pipeline $210,000,000 for a 100 TJ/d withdrawl facility, assuming 10 wells, injection rate of 50 TJ/d, and a 30 km connecting pipeline For facilities of different sizes use a 0.6 scaling factor using the scaling relationship | $4,000,000 to $8,000,000 per annum, depending on utilisation of facility | For all brownfields conventional gas plant upgrades an estimated 20% of the upgrade cost, representing the labour cost, should have a 30% increase applied to this portion to allow for lower labour productivity at an operating facility. | 10% of capital cost of new facility | $12,000,000 for a 50 TJ/d facility. For facilities of different sizes use a 0.8 scaling factor using the scaling relationship
7 | Natural gas | Storage - Aboveground (LNG) | Liquefaction, tanks, regassification |  |  |  | $250,000,000 - $275,000,000 per PJ of storage | $5,500,000 to $7,500,000 per annum for a 120MTPD facility $8,100,000 to $11,100,000 per annum for a 250MTPD | $250,000,000 - $275,000,000 per PJ of additional storage | Liquification equipment 5% of capital of new facility. Regassification equipment 3% of capital of new facility. | 12000000
8 | Natural gas | Storage - Linepack Lateral | Power station storage pipeline |  |  |  | 20 TJ total volume of natural gas $61,900,000 for a DN500 pipeline, 32.3 km long $41,300,000 for a DN750 pipeline, 13.9 km long $33,800,000 for a DN900 pipeline, 9.4 km long $19,200,000 for a compressor station to pressurise the linepack lateral | Percentage of capex (net of compression) $9,000/km to $29,000/km | N/A | $250,000/km for recoating of pipelines | $197/mm km ($5000/inch km)
9 | Natural gas | LNG import facilities | Wharf/jetty, topsides, nitrogen balancing |  | FSRU is assumed excluded from capital cost as typically leased |  | Based on developed and proposed LNG import terminals in Australia, these facilities costs between $500,000/TJ to $650,000/TJ | Not in scope | Not in scope | Not in scope | Not in scope
10 | Carbon Capture and Storage | Compression |  |  | Cost basis reflective of materially more complex compression plant |  | CO2 compression can range from: $6,008,000/MW to $9,408,000/MW. For CO2 compression its expected to cost an extra $3008/kW when compared to natural gas compression. | Not in scope | Not in scope | Not in scope | Not in scope
11 | Carbon Capture and Storage | Pipelines |  |  | Reflective of increased unit costs for CO2 specific needs |  | 10% increase in comparison to natural gas pipelines 3,300/mm km ($82,500/inch km) | Not in scope | Not in scope | Not in scope | Not in scope
12 | Carbon Capture and Storage | Injection |  |  |  |  | Cost of wellhead metering and control skid: $3,000,000/well Flowlines: $600,000/km Wellhead and wellhead completion: $5,000,000/well Other wellhead facilities: $2,000,000 | Not in scope | Not in scope | Not in scope | Not in scope
13 | Hydrogen | Hydrogen transport | Pipeline |  |  |  | 25% increase overall in natural gas pipeline costs resulting in $3,750/mm km (93,750/inch km) Energy capacity is 15% to 25% less than eqivalent size natural gas pipeline | Not in scope | Not in scope | Not in scope | Not in scope
14 | Hydrogen | Hydrogen transport | Trucking - metal hydride storage |  |  |  | $27.45/kWh, basis from vendor information | Not in scope | Not in scope | Not in scope | Not in scope
15 | Hydrogen | Hydrogen storage | Salt cavern |  |  |  | $599,000,000 based on a facility of 8,000 tonnes storage capacity in two caverns, a withdrawl rate of 750 tonnes/d and injection rate of 375 tonnes/d, and a 3 km interconnecting pipeline Includes storage wells, salt water disposal wells, water supply wells, leach plants, brine disposal operations, hydrogen compression. | Not in scope | Not in scope | Not in scope | Not in scope
16 | Biomethane | Biomethane production |  |  | Delivery and storage of biomethane is the same as for natural gas. It is noted that often biomethane will be injected into gas distribution systems rather than gas transmission systems due to high cost and relatively small volume of production |  | $21,000,000 to $33,000,000 for a small facility (10,000/tpa to 30,000/tpa feedstock capacity) $33,000,000 to $43,000,000 for a medium facility (30,000/tpa to 60,000/tpa feedstock capacity) $43,000,000 to $71,000,000 for a large facility (60,000/tpa to 140,000/tpa feedstock capacity) $85,000,000 plus for a very large facility (200,000/tpa plus feedstock capacity) | Not in scope | Not in scope | Not in scope | Not in scope
17 | Coal Seam Gas | CSG desalination plants |  |  |  |  | Capital costs for water treatment plants are estimated using the equation below: CAPEX ($/M) = 10.3 x (WTP feed capacity ML/d)0.74 Plant sizing water rate/TJ of gas production of 0.07 ML/TJ for Surat Basin, and 0.032 ML/TJ for Bowen Basin | Not in scope | Not in scope | Not in scope | Not in scope
18 | Coal Seam Gas | CSG water pipeline |  |  |  |  | Capital costs for supply, install and indirect costs: 0.5 ML/d = $249/m 1.5 ML/d = $314/m 4.5 ML/d = $528/m 9.2 ML/d = $925/m 18 ML/d = $1708/m | Not in scope | Not in scope | Not in scope | Not in scope